## Structural
Date
19-Apr-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Apparel 21 Ltd., Shirir Chala, Bagher Bazer Gagipur Shadar, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-05-03
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Prop temporary opening in wall of Boiler building | Temporary opening to be propped. This was pointed out to the factory management on site. | Completed | Oct 28 2014 | ON 09/06/2015: Done. On verification we found that the factory management repaired the wall and there was no opening in wall of boiler building. ON 13/03/2016 : It is done. ON 27/04/2016 : Already it is done from previous follow up. ON 04/04/2017: Corrected from previous follow up inspection report. ON 21/12/2017: This issue has been corrected as per 1st follow up inspection. Wall of the boiler building has been repaired. ON 05/06/2018: Corrected as per 1st follow up inspection report. On 17-April-2019: This issue was corrected from previous inspecting. During inspection, wall of the boiler building has been repaired. On 19-Dec-2019: Corrected in previous follow up inspection. On 09-Nov-2020: Corrected from previous follow up inspection of Accord. During inspection, wall of the boiler building was found repaired. On 28-Dec-2021: This issue was corrected in previous follow-up inspection. On 28-Nov-2024: Corrected previously. | (Immediate -Now) | Corrected
Initial Inspection |  | 2 | Lateral stability of Building 1 | Building engineer to check ability of column, wall and foundation structure on each side to resist E-W wind loading | DEA Submitted | Apr 16 2015 | ON 09/06/2015: This issue will be covered under Engineering assessment. The factory management has already submitted Engineering Assessment on 16th April, which is under review. ON 13/03/2016 : The factory management have done assessment on lateral stability issue and that has got approval from accord on 18 January, 2016. ON 27/04/2016 :This issue is covered in DEA. Factory got acceptance on 18/01/2016. ON 04/04/2017: This issue was covered in DEA. Factory completed DEA and submitted to ACCORD which was accepted on 18/01/2016. ON 21/12/2017: This issue has been corrected as per 2nd follow up inspection. DEA of the factory received acceptance from ACCORD on 18/01/2016. ON 05/06/2018: This issue was covered in DEA. Factory got DEA acceptance from Accord on 18/01/2016. On 17-April-2019: This issue was corrected from previous inspecting. Factory has carried out DEA report and accepted from ACCORD on 18th January 2016. On 19-Dec-2019: Corrected in previous follow up inspection. This issue had been covered in DEA report. Factory management got DEA re-acceptance from Accord on 29-September-2019. On 09-Nov-2020: Corrected from previous follow up inspection of Accord. This issue had been covered in DEA report. Factory management had submitted revised retrofitting scheme of dyeing shed (Building-1) along with DEA, which got re-acceptance on 15-March-2020 from Accord. On 28-Dec-2021: This issue was corrected in previous follow-up inspection. DEA was re-accepted from Accord on 15th March 2020. On 28-Nov-2024: Corrected previously. This issue has been covered in the DEA which was re-accepted by ACCORD dated 15-March-2020. | (within 6-weeks) | Corrected
Initial Inspection |  | 3 | Lateral stability of Building 1 | Building engineer to assess N-S stability of portal structure. | DEA Submitted | Apr 16 2015 | ON 09/06/2015:This issue will be covered under Engineering assessment. The factory management has already submitted Engineering Assessment on 16th April, which is under review. ON 13/03/2016 : The factory management have done assessment on lateral stability issue and that has got approval from accord on 18 January ,2016. ON 27/04/2016 : This issue is covered in DEA. Factory got acceptance on 18/01/2016. ON 04/04/2017: This issue was covered in DEA. Factory completed DEA and submitted to ACCORD which was accepted on 18/01/2016. ON 21/12/2017: This issue has been corrected as per 2nd follow up inspection. DEA of the factory received acceptance from ACCORD on 18/01/2016. ON 05/06/2018: This issue was covered in DEA. Factory had submitted DEA report to ACCORD which was accepted on 18/01/2016. On 17-April-2019: This issue was corrected from previous inspecting. Factory has carried out DEA report and accepted from ACCORD on 18th January 2016. On 19-Dec-2019: Corrected in previous follow up inspection. This issue had been covered in DEA report. Factory management got DEA re-acceptance from Accord on 29-September-2019. On 09-Nov-2020: Corrected from previous follow up inspection of Accord. Stability of portal structures had been covered in DEA report. Factory management had submitted revised retrofitting scheme of dyeing shed (Building-1) along with DEA, which got re-acceptance on 15-March-2020 from Accord. On 28-Dec-2021: This issue was corrected in previous follow-up inspection. On 28-Nov-2024: Corrected previously. | (within 6-weeks) | Corrected
Initial Inspection |  | 4 | Lateral stability of Building 1 | Building Engineer to advise on additional measures to provide structural resistance to lateral loads if required. | Corrected ,(Now cylinder and rebar test report is available at factory site. In addition, we submitted cylinder and rebar test report to ACCORD/RSC.) | Jun 30 2016 | ON 09/06/2015: This issue will be covered under Engineering assessment. The factory management has already submitted Engineering Assessment on 16th April, which is under review. ON 13/03/2016: The factory management have done assessment on lateral stability issue and that has got approval from accord on 18 January, 2016. From the assessment it was noticed that they were suggested for retrofitting and retrofitting work was going on. ON 27/04/2016: This issue is covered in DEA. Factory got acceptance on 18/01/2016. During inspection retrofitting work was going on. ON 04/04/2017: This issue was covered in DEA. Factory completed DEA and submitted to ACCORD which was accepted on 18/01/2016. During inspection, Retrofitting work was found on going. ON 21/12/2017: DEA of the factory received acceptance from ACCORD on 18/01/2016. As per accepted DEA building - 1 required retrofitting. Factory has completed all the remediation works. During inspection construction of a mezzanine floor was found ongoing which is structurally connected to the main structure. Factory is required to submit revised DEA for building- 1 as soon as possible. ON 05/06/2018: Factory had submitted the revised DEA to Accord on 30th May 2018 after following verification report. Currently the DEA is under review. This issue will be corrected after re-acceptance of DEA, verification of accepted documents with as built condition and completion of proper retrofitting work. On 17-April-2019: Factory had submitted the revised DEA to ACCORD on 4th April 2019, which is now under review. But during inspection, as per last submission some mismatch was found at mezzanine portion. Factory engineer is required to survey and update documents as per site condition. On 19-Dec-2019: Factory management got DEA re-acceptance from Accord on 29-September-2019. As per DEA recommendation factory management had completed remedial works for steel members but foundation retrofitting was pending. Factory management had faced some difficulties for foundation retrofitting and as a result they had submitted revised retrofitting scheme on 26-December-2019 to Accord which is under review. On 09-Nov-2020: Factory management had submitted revised retrofitting scheme of dyeing shed (Building-1) along with DEA, which got re-acceptance on 15-March-2020 from Accord. During inspection retrofitting works (RC column jacketing, foundation retrofitting & addition of steel plate in rafter) were found completed as required. QC certificate had been provided by factory consultant but cylinder and rebar test report were not found at the time of inspection. On 28-Dec-2021: Retrofitting work was completed as per re-accepted DEA. QC certificate and material test report were found during inspection. On 28-Nov-2024: Corrected previously. | (within 6-Month) | Corrected
Initial Inspection |  | 5 | Wind load on gable walls of Building 1 and Boiler building | Building Engineer to check ability of the Building 1 gable columns and foundations to cantilever from ground to resist N-S wind loading. | DEA Submitted | Apr 16 2015 | ON 09/06/2015: This issue will be covered under Engineering assessment. The factory management has already submitted Engineering Assessment on 16th April, which is under review. ON 13/03/2016 : The factory management have done assessment on lateral stability issue and that has got approval from accord on 18 January, 2016. ON 27/04/2016 : This issue is covered in DEA. Factory got acceptance on 18/01/2016. ON 04/04/2017: This issue was covered in DEA. Factory completed DEA and submitted to ACCORD which was accepted on 18/01/2016. ON 21/12/2017: This issue has been corrected as per 1st follow up inspection. DEA of the factory has been accepted from ACCORD on 18/01/2016. ON 05/06/2018: This issue was covered in DEA. Factory got DEA acceptance from Accord on 18/01/2016. On 17-April-2019: This issue was corrected from previous inspecting. Factory has carried out DEA report and accepted from ACCORD on 18th January 2016. On 19-Dec-2019: Corrected in previous follow up inspection. This issue had been covered in DEA report. Factory management got DEA re-acceptance from Accord on 29-September-2019. On 09-Nov-2020: Corrected from previous follow up inspection of Accord. This issue had been covered in DEA report. Factory management had submitted revised retrofitting scheme of dyeing shed (Building-1) along with DEA, which got re-acceptance on 15-March-2020 from Accord. On 28-Dec-2021: This issue was corrected in previous follow-up inspection. DEA of Building-1 got re-acceptance from Accord on 15th March 2020. On 28-Nov-2024: Corrected previously. | (within 6-weeks) | Corrected
Initial Inspection |  | 6 | Wind load on gable walls of Building 1 and Boiler building | A similar check is to be carried out on the gable walls for the Boiler building. | DEA Submitted | Apr 16 2015 | ON 09/06/2015: This issue will be covered under Engineering assessment. The factory management has already submitted Engineering Assessment on 16th April, which is under review. ON 13/03/2016 : The factory management have done assessment on lateral stability issue and that has got approval from accord on 18 January ,2016. ON 27/04/2016 : This issue is covered in DEA. Factory got acceptance on 18/01/2016. ON 04/04/2017: This issue was covered in DEA. Factory completed DEA and submitted to ACCORD which was accepted on 18/01/2016. ON 21/12/2017: This issue has been corrected as per 1st follow up inspection. DEA of the factory has been accepted from ACCORD on 18/01/2016. ON 05/06/2018: This issue was covered in DEA. Factory got DEA acceptance on 18/01/2016. On 17-April-2019: This issue was corrected from previous inspecting. Factory has carried out DEA report and accepted from ACCORD on 18th January 2016. On 19-Dec-2019: Corrected in previous follow up inspection. This issue had been covered in DEA report. Factory management got DEA re-acceptance from Accord on 29-September-2019. On 09-Nov-2020: Corrected from previous follow up inspection of Accord. This issue had been covered in DEA report. Factory management had submitted revised retrofitting scheme of dyeing shed (Building-1) along with DEA, which got re-acceptance on 15-March-2020 from Accord. On 28-Dec-2021: This issue was corrected in previous follow-up inspection On 28-Nov-2024: Corrected previously. | (within 6-weeks) | Corrected
Initial Inspection |  | 7 | Wind load on gable walls of Building 1 and Boiler building | Building Engineer to advise on measures to stabilise gable columns and walls if required. | Done by Accord | Jun 30 2016 | ON 09/06/2015: This issue will be covered under Engineering assessment. The factory management has already submitted Engineering Assessment on 16th April, which is under review. ON 13/03/2016 : The factory management have done assessment on lateral stability issue and that has got approval from accord on 18 January ,2016.They were proposed for retrofitting work Building 1and Boiler building. But that retrofitting work was going on. ON 27/04/2016 : This issue is covered in DEA. Factory got acceptance on 18/01/2016. During inspection retrofitting work is going on. ON 04/04/2017: This issue was covered in DEA. Factory completed DEA and submitted to ACCORD which was accepted on 18/01/2016. During inspection, Retrofitting work was found on going. ON 21/12/2017: DEA of the factory received acceptance from ACCORD on 18/01/2016. As per accepted DEA building - 1 required retrofitting. Factory has completed all the remediation works. During inspection construction of a mezzanine floor was found ongoing which is structurally connected to the main structure. Factory is required to submit revised DEA for building- 1 as soon as possible. ON 05/06/2018: Factory had submitted the revised DEA to Accord on 30th May 2018 after following verification report. Currently the DEA is under review. This issue will be corrected after re-acceptance of DEA, verification of accepted documents with as built condition and completion of proper retrofitting work. On 17-April-2019: Factory had submitted the revised DEA to ACCORD on 4th April 2019, which is now under review. But during inspection, as per last submission some mismatch was found at mezzanine portion. Factory engineer is required to survey and update documents as per site condition. On 19-Dec-2019: As built drawings were prepared as a part of DEA. Factory management got DEA re-acceptance from Accord on 29-September-2019. As per DEA recommendation factory management had completed remedial works. On 09-Nov-2020: Corrected from previous follow up inspection of Accord. This issue had been covered in DEA report. Factory management had submitted revised retrofitting scheme of dyeing shed (Building-1) along with DEA, which got re-acceptance on 15-March-2020 from Accord. As per DEA recommendation factory management had completed remedial works (RC column jacketing, foundation retrofitting & addition of steel plate in rafter). On 28-Dec-2021: This issue was corrected in previous follow-up inspection. On 28-Nov-2024: Corrected previously. | (within 6-Month) | Corrected
Initial Inspection |  | 8 | Edge cantilever of Generator building | Building Engineer to check ability of facade columns and edge beams to resist bending and torsion from the first floor edge cantilever. | DEA Submitted | Apr 16 2015 | ON 09/06/2015: This issue will be covered under Engineering assessment. The factory management has already submitted Engineering Assessment on 16th April, which is under review. ON 13/03/2016 : They did assessment on this issue and that is approved by accord. ON 27/04/2016 : This issue is covered in DEA. Factory got acceptance on 18/01/2016. ON 04/04/2017: This issue was covered in DEA. Factory completed DEA and submitted to ACCORD which was accepted on 18/01/2016. ON 21/12/2017: This issue has been corrected as per 2nd follow up inspection. DEA of the factory has been accepted from ACCORD on 18/01/2016. ON 05/06/2018: This issue was covered in DEA. Factory got DEA acceptance from Accord on 18/01/2016. On 17-April-2019: This issue was corrected from previous inspecting. Factory has carried out DEA report and accepted from ACCORD on 18th January 2016. On 19-Dec-2019: Corrected in previous follow up inspection. This issue had been covered in DEA report. Factory management got DEA re-acceptance from Accord on 18-January-2016. On 09-Nov-2020: Corrected from previous follow up inspection of Accord. As built drawings were prepared as a part of DEA. Factory got DEA acceptance from Accord on 18-January-2016. Factory management had installed RC column under cantilever portion of generator building as required. On 28-Dec-2021: This issue was corrected in previous follow-up inspection. DEA was accepted from Accord on 18-Jan-2016. On 28-Nov-2024: Corrected previously. This issue has been covered in the DEA which was accepted by ACCORD dated 18-Jan-2016. | (within 6-Weeks) | Corrected
Initial Inspection |  | 9 | Edge cantilever of Generator building | Building Engineer to advise on remedial measures for cantilever slab structure if required. | Completed | Jun 30 2016 | ON 09/06/2015:This issue will be covered under Engineering assessment. The factory management has already submitted Engineering Assessment on 16th April, which is under review. ON 13/03/2016 : They did assessment on this issue and that is approved by accord and they had some recommendations which need to implement. ON 27/04/2016 : This issue is covered in DEA. Factory got acceptance on 18/01/2016. During inspection retrofitting work is going on. ON 04/04/2017: This issue was covered in DEA. Factory completed DEA and submitted to ACCORD which was accepted on 18/01/2016. During inspection, Retrofitting work was found on going. ON 21/12/2017: This issue is required to be covered under DEA. DEA of the factory has been accepted from ACCORD on 18/01/2016. As per accepted DEA, edge cantilever of generator building was required to be supported by columns. Factory has completed the remediation works of generator building. ON 05/06/2018: This issue was covered in DEA. Factory got DEA acceptance from Accord on 18/01/2016. As per recommendation form the accepted DEA report factory has completed the remedial measures for cantilever slab structure. On 17-April-2019: This issue was corrected from previous inspecting. Factory has carried out DEA report and accepted from ACCORD on 18th January 2016. As per recommendation form the accepted DEA report factory has completed the remedial measures for cantilever slab structure. On 19-Dec-2019: As built drawings were prepared as a part of DEA. Factory management got DEA acceptance from Accord on 18-January-2016. As per DEA recommendation factory management had completed remedial works. On 09-Nov-2020: Corrected from previous follow up inspection of Accord. Factory got DEA acceptance from Accord on 18-January-2016. Factory management had installed RC column under cantilever portion of generator building as required. On 28-Dec-2021: This issue was corrected in previous follow-up inspection. As a part of remediation new RC columns were constructed beneath the cantilever part. On 28-Nov-2024: Corrected previously. | (within 6-months) | Corrected
Initial Inspection |  | 10 | Monitor performance of propped beams in Building 2 | Building engineer to monitor behaviourof propped beams in Finish Fabric area (S-E side) of Building 2, and record any settlement of brick props or further deflection of beams. | DEA Submitted | Apr 16 2015 | ON 09/06/2015: This issue will be covered under Engineering assessment. The factory management has already submitted Engineering Assessment on 16th April, which is under review. ON 13/03/2016 : At the time of inspection It was observed that they had some propped beams in building 2.It was suggested them to follow the recommendations from the DEA report and monitor deflection so that it can not take place further. ON 27/04/2016 : During inspection brick props was observed. It was suggested to them to follow the DEA recommendations and record any settlement of brick props. ON 04/04/2017:Corrected from previous follow up inspection report. During inspection, Brick props were observed. Factory was suggested to follow DEA recommendations and record settlement of brick props or further deflection of beams if happens. ON 21/12/2017: This issue has been corrected as per 2nd follow up inspection. Brick props were installed as per recommendation of DEA. Factory is required to monitor the settlements of brick props for further deflection of beams if happens. ON 05/06/2018: This issue was covered in DEA which was accepted on 18/01/2016. During inspection brick column props was observed. Factory is required to monitor the settlements of brick props for further deflection of beams if happens. On 17-April-2019: This issue was corrected from previous inspecting. Factory has carried out DEA report and accepted from ACCORD on 18th January 2016. During inspection brick column props was found. On 19-Dec-2019: Corrected in previous follow up inspection. During inspection brick column props were found. On 09-Nov-2020: Corrected from previous follow up inspection of Accord. During inspection brick columns were found under beam. On 28-Dec-2021: This issue was corrected in previous follow-up inspection. Brick column was found during inspection. On 28-Nov-2024: Corrected previously. | (within 6-Weeks) | Corrected
Initial Inspection |  | 11 | Monitor performance of propped beams in Building 2 | Building Engineer is working for remedial works to ensure effective propping of beams . | DEA Submitted & work is running. | Jun 30 2016 | ON 09/06/2015: This issue will be covered under Engineering assessment. The factory management has already submitted Engineering Assessment on 16th April, which is under review. ON 13/03/2016 : At the time of inspection It was observed that they had some propped beams in building 2.As per assessment report they had some remedial works needed to do and that is on going. ON 27/04/2016 : During inspection brick props was observed. It was suggested to them to follow the DEA recommendations and record any settlement of brick props. ON 04/04/2017:Corrected from previous follow up inspection report. During inspection, Brick props were observed. Factory was suggested to follow DEA recommendations and record settlement of brick props or further deflection of beams if happens. ON 21/12/2017: This issue has been corrected as per 2nd follow up inspection. Brick props were installed as per recommendation of DEA. Factory is required to monitor the settlements of brick props for further deflection of beams if happens. ON 05/06/2018: This issue was covered in DEA which was accepted on 18/01/2016. During inspection brick props was observed. Factory is required to monitor the settlements of brick column props for further deflection of beams if happens. On 17-April-2019: This issue was corrected from previous inspecting. Factory has carried out DEA report and accepted from ACCORD on 18th January 2016. During inspection brick column props was found. On 19-Dec-2019: Corrected in previous follow up inspection. During inspection brick column props were found. On 09-Nov-2020: Corrected from previous follow up inspection of Accord. During inspection brick columns were found under beam. On 28-Dec-2021: This issue was corrected in previous follow-up inspection. Brick column was found during inspection. On 28-Nov-2024: Corrected previously. | (within 6-months) | Corrected
Follow Up Inspection |  | 12 | New Findings: Corrosion in Steel member | Building engineer working to check the corroded steel member and suggest a suitable repair method. | Done | Jun 30 2016 | ON 09/06/2015:On verification we found that there were some corroded steel members in Dyeing & Boiler building. Building engineer did not do anything about it. ON 13/03/2016 : They have not repaired those corrosions in steel members till the time of inspection. ON 27/04/2016 : During inspection remedial work was not done against corrosions. ON 04/04/2017: During inspection, No repairing work against corrosion was observed in dyeing and boiler building. Factory is required to take necessary repairing action as per suggestion of factory engineer. ON 21/12/2017: During inspection, corrosion was found on steel members of different buildings. Factory is required to take necessary remedial measures to remove corrosion as per recommendation of building engineer. ON 05/06/2018: During inspection corrosion protecting paint was observed on the steel member of building-2. But, corrosion was found on steel members of generator and boiler buildings. Factory is required to take necessary remedial measures as per recommendation of factory engineer. On 17-April-2019: During inspection corrosion protecting paint was observed on the steel member of building-2, generator and boiler buildings. On 19-Dec-2019: Corrected in previous follow up inspection. During inspection corrosion was not found. On 09-Nov-2020: Corrected from previous follow up inspection of Accord. During inspection corrosion was not found in steel members. On 28-Dec-2021: This issue was corrected in previous follow-up inspection. Corrosion was not observed during inspection. On 28-Nov-2024: Corrected previously. During the inspection, corrosion was not observed on the Building 1 and Boiler building. | 15 days | Corrected
Follow Up Inspection |  | 13 | New Findings: Dampness was found on several places of Garments Building | Factory Engineer required to investigate the cause of dampness and implement necessary repairing action accordingly | Done | May 16 2017 | ON 04/04/2017: During inspection, Dampness was found at several places(specially toilet block and stair portion) of south east portion of the garments building. Building Engineer is required to take necessary repairing action as per investigation. ON 21/12/2017: During inspection, dampness was found at several places of garments building. Factory is required to take necessary remedial measures for providing protection from dampness as per recommendation of building engineer. ON 05/06/2018: Dampness was found at several places of garments building. Factory is required to take necessary repairing action for providing protection against dampness as per recommendation of factory engineer. On 17-April-2019: During inspection, no dampness was found at garments building. Factory has repaired all dampness portion. On 19-Dec-2019: Corrected in previous follow up inspection. During inspection dampness was not found. On 09-Nov-2020: Corrected from previous follow up inspection of Accord. During inspection dampness was not found. On 28-Dec-2021: This issue was corrected in previous follow-up inspection. Dampness was not observed during inspection. On 28-Nov-2024: Corrected previously. See item no-16. | (within 6-Weeks) | Corrected
Follow Up Inspection |  | 14 | New Findings: Exposed Rebar found most of the RCC column of building-1 | Factory is required to take necessary action to protect rebar from corrosion | Completed | May 16 2017 | ON 04/04/2017: Factory is required to take necessary action regarding this issue. ON 21/12/2017: Building-1 is under construction. Reinforcements were found exposed from beams and columns of building-1 during inspection. Factory is required to take necessary remedial measures to protect exposed reinforcements from corrosion. ON 05/06/2018: During inspection, no exposed rebar was found. Factory already removed the exposed rebar from the RCC column of building 1. On 17-April-2019: This issue was corrected from previous inspecting. On 19-Dec-2019: Corrected in previous follow up inspection. Exposed rebar was not found. On 09-Nov-2020: Corrected from previous follow up inspection of Accord. Exposed rebar was not found. On 28-Dec-2021: This issue was corrected in previous follow-up inspection. On 28-Nov-2024: Corrected previously. During the inspection, exposed re-bar was not observed. | (within 6-Weeks) | Corrected
Follow Up Inspection |  | 15 | New findings 4: Construction of a new mezzanine floor in building-1 | Factory is required to provide adequacy check of building-1 for newly constructed mezzanine floor | Done by Accord | Feb 1 2018 | ON 21/12/2017: During inspection, construction work of a mezzanine floor was found ongoing in building-1. DEA of the factory was previously accepted from ACCORD on 18/01/2016. Factory completed all the remediation works in building-1. Factory is required to revise the DEA for newly constructed mezzanine floor and submit to ACCORD as soon as possible. ON 05/06/2018: Factory had submitted the revised DEA to Accord on 30th May 2018 after following verification report. Currently the DEA is under review. This issue will be corrected after re-acceptance of DEA, verification of accepted documents with as built condition and completion of proper retrofitting work. On 17-April-2019: Factory had submitted the revised DEA to ACCORD on 4th April 2019, which is now under review. But during inspection, as per last submission some mismatch was found at mezzanine portion. Factory engineer is required to survey and update documents as per site condition. On 19-Dec-2019: This issue had been covered in DEA report. Factory management got DEA re-acceptance from Accord on 29-September-2019. On 09-Nov-2020: Corrected from previous follow up inspection of Accord. This issue had been covered in DEA report. Factory management had submitted revised retrofitting scheme of dyeing shed (Building-1) along with DEA, which got re-acceptance on 15-March-2020 from Accord. On 28-Dec-2021: This issue was corrected in previous follow-up inspection. As per re-accepted DEA, retrofitting was completed for Building-1. On 28-Nov-2024: Corrected previously. | (within 6-Weeks) | Corrected
Follow Up Inspection |  | 16 | New Finding-5: Dampness on beam, column and brick wall (Building 1, Building 2, Boiler building) | The building engineer is required to investigate the source of dampness and repair the dampness with proper methodology. | We have completed the plaster work, and the dampness issue has been resolved. Done | Jan 23 2025 | On 28-Nov-2024: During the inspection, dampness was observed on the beam, column and brick wall at several location of Building 1, Building 2, and Boiler building. The building engineer is required to investigate the source of dampness and repair the dampness with proper methodology. RPO Comments: 16-Sep-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 weeks) | Pending Verification

## Fire
Date
19-Apr-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Apparel 21 Ltd., Shirir Chala, Bagher Bazer Gagipur Shadar, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-05-05
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Areas used for combustible storage are not separated by firerated construction. Storage was located in various areas throughout the west wing ground floor. The various storage areas were scattered, around the floor with no dedicated storage rooms or areas. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Completed | Mar 27 2016 | On 30/08/2016: Partially corrected. Still storage areas are not organized as per standard in buidling-1 on ground floor. On 21/11/2016: It has been found same as before. On 29/01/2017: No action taken yet for finished good, bonded ware house, yarn store, etc. On 04/04/2017: No action taken yet for finished good, bonded ware house, yarn store, etc. On 20/07/2017: In progress. On 03/01/2018: Storage area as well as store room without proper separation has been found on ground floor (dyeing shed). But dedicated storage room construction is going on. On 12-07-2018: Partially corrected. Fire rated door is not installed properly. Moreover, storages are found in improper way in dyeing shed. On 27/02/2019: Separated. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 2 | Egress doors / gates with locking features are provided at building exits, exit stairs, along egress routes, and exit discharge. This was reflected throughout the building on all floors. | Remove locking features from all egress doors / gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101 | Completed | Mar 13 2016 | On 30/08/2016: Corrected. Factory has removed non-compliant locking features from egress routes exit doors/gates. On 21/11/2016: Corrected. On 29/01/2017: Corrected. On 04/04/2017: Corrected. On 20/07/2017: Removed On 03/01/2018: Corrected as per previous follow up. On 12-07-2018: Corrected. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Immediately | Corrected
Initial Inspection |  | 3 | Storage areas/ electrical boxes were located in all exit stairwells on the ground floor, underneath the stairs. | Remove all storage from exit stairs and egress paths. | Completed | Mar 13 2016 | On 30/08/2016: Corrected. On 21/11/2016: Corrected. On 29/01/2017: Corrected. On 04/04/2017: Corrected. On 20/07/2017: Removed On 03/01/2018: Corrected as per previous follow up. On 12-07-2018: Corrected. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Immediately | Corrected
Initial Inspection |  | 4 | Storage was located in various areas throughout the west wing ground floor. The various storage areas were scattered, around the floor with no dedicated egress path. | Keep egress paths and stairs clear of storage. | Completed | Mar 27 2016 | On 30/08/2016: Corrected. Storage was not found during follow up inspection. On 21/11/2016: Corrected. On 29/01/2017: Corrected. On 04/04/2017: Corrected. On 20/07/2017: Not found On 03/01/2018: Corrected as per previous follow up. On 12-07-2018: Corrected. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Immediately | Corrected
Initial Inspection |  | 5 | Collapsible gates/ sliding doors are provided at building exits, exit stairs, along egress routes, and exit discharge. This was reflected throughout the building on all floors. | Replace all gates / sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Completed | Mar 27 2016 | On 30/08/2016: Corrected. Factory has removed non-compliant doors/gates from egress routes. On 21/11/2016: Corrected. On 29/01/2017: Corrected. On 04/04/2017: Corrected. On 20/07/2017: Replaced On 03/01/2018: Corrected as per previous follow up. On 12-07-2018: Corrected. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 6 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | As per the reviewed FADS drawing we have completed almost 98% work. Some Beam detector installation work is going on and rest of the work including addressing, programming & troubleshooting work will be done by June 20, 2026. | May 13 2016 | On 30/08/2016: Partially corrected. Reviewed drawing from Accord was available during 4th follow-up inspection. Installation was almost completed. Fire doors, HVAC system, fire pump controls should be interfaced with FACP if applicable. On 21/11/2016: Still installation process is going on. On 29/01/2017: Installation work is going on. On 04/04/2017: Factory has informed they have completed the installation of fire alarm system. On 20/07/2017: Installation almost completed. Needs to perform testing& commissioning by 3rd party in presence of Accord. On 03/01/2018: Installation is almost done and factory is going to apply (as per factory information) with in few days for testing & commissioning to Accord. Factory will ensure all the used products are third party certified including air sampling system. On 12-07-2018: Waiting for T&C verification by ACCORD. On 27/02/2019: Awaiting for T&C. On 02-01-2020: In progress. Modification work in progress. Once installation completed, Factory shall provide adequate documents and designs for T&Cx inspection. On 29/08/2024: Factory has reviewed FADS drawing from RSC on 18-Dec-2023 due to the addition of another structure (RSC ID: 24259) with the fire alarm control panel of this ID. The modification work is on going. After completion of installation work, factory shall submit documents and design for Pre T&C VI. RPO Comments: On 20-Apr-2026, The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Design within 4 months, install within 9 months | In Progress
Initial Inspection |  | 7 | Inspection, testing, and maintenance for the fire alarm system was not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72 | Completed | May 13 2016 | On 30/08/2016: Corrected. Factory management is maintaining and keeping existing fire alarm system maintenance records on site. On 21/11/2016: Corrected. Factory is maintaining as per Accord standard for their existing system. On 29/01/2017: Corrected. On 04/04/2017: Corrected. On 20/07/2017: Integrated part of fire alarm system On 03/01/2018: Corrected as per previous follow up. Moreover it is an integrated part of fire alarm system. On 12-07-2018: Corrected. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected as per previous follow up. Moreover it is an integrated part of fire alarm system. | Within 3 months | Corrected
Initial Inspection |  | 8 | The building is equipped with single -station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Replace the single-station smoke alarms. Provide automatic smoke detection throughout the building in accordance with NFPA 72. | As per the reviewed FADS drawing we have completed almost 98% work. Some Beam detector installation work is going on and rest of the work including addressing, programming & troubleshooting work will be done by June 20, 2026. | May 13 2016 | On 30/08/2016: It is an integrated part of fire alarm system. On 21/11/2016: Still installation work is going on. On 29/01/2017: It is an integrated part of fire alarm system. 13/03/2017: Factory is asking till 20/04/2017,timeline extension is not accepted. 03/04/2017: Factory is asking till 20/04/2017,timeline extension is not accepted. On 04/04/2017: It is an integrated part of fire alarm system. On 20/07/2017: Installed On 03/01/2018: It is an integrated part of fire alarm and detection system. On 12-07-2018: It is an integrated part of fire alarm and detection system. On 27/02/2019: It is an integrated part of fire alarm and detection system. On 02-01-2020: In progress. Integrated part of FA system. On 29/08/2024: In progress. It is an integrated part of fire alarm and detection system. RPO Comments: On 20-Apr-2026, The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 6 months | In Progress
Initial Inspection |  | 9 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. This was reflected throughout the building on all floors. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Completed | Apr 13 2016 | On 30/08/2016: Corrected. During follow up inspection illumination level was found satisfactory. If floor layout will change than factory shall ensure that illumination level on aisles are as per standard. On 21/11/2016: Corrected. On 29/01/2017: Corrected. On 20/07/2017: Completed. Needs to maintain log sheet of illumination level. On 03/01/2018: Corrected as per previous follow up. This issue also reflect by the issue no 24. On 12-07-2018: Corrected as per previous follow up. This issue also reflect by the issue no 24. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 10 | Inspection, testing, and maintenance records for the emergency lighting system were not available. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | Completed | Mar 27 2016 | On 30/08/2016: Corrected. Factory is keeping emergency & exit light maintenance checklist record on-site as per Accord standard. On 21/11/2016: Corrected. Factory is maintaining as per Accord standard for their existing system. On 29/01/2017: Corrected. On 04/04/2017: Corrected. On 20/07/2017: Maintaining. On 03/01/2018: Corrected as per previous follow up. On 12-07-2018: Corrected. On 27/02/2019: Maintaining. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 11 | NEW FINDING (1st follow-up): Chemical area is not separated by fire-rated construction (openings, non-rated doors, penetrations). | Chemical storage room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | Completed | Apr 13 2016 | On 30/08/2016: Corrected. Factory has relocated chemical store to new building. On 21/11/2016: Corrected. On 29/01/2017: Corrected. On 04/04/2017: Corrected. On 20/07/2017: Relocated to another building. On 03/01/2018: Corrected as per previous follow up. On 12-07-2018 : Corrected as per previous follow up. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 12 | NEW FINDING (2nd follow-up): All exit stairs in garments building discharge inside the building. | Factory shall provide either of the following: - Modify stair to discharge directly outside. - Provide 2-hr fire-rated exit passageway leading directly outside (vestibules to separate any storage areas). - Provide sprinkler protection for discharge floor in accordance with NFPA 13. | Completed | Jul 10 2016 | On 30/08/2016: Partially corrected. Still factory didn't install door closer and push bar on east side exit fire rated. On 21/11/2016: Fire door installation has been done. But door closer and door holding device still is missing. On 29/01/2017: Fire door has been installed. Hardware is missing in fire rated door. On 04/04/2017: Factory shall install fire rated door. On 20/07/2017: Sealed at ground level. On 03/01/2018: East middle exit stair discharge is not separated on ground floor due to new building construction. On 12-07-2018: Factory has changed the direction of all (three) the stairs. All stairs discharge directly outside the building. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 13 | NEW FINDING (2nd follow-up): The width of egress aisles is less than 36-in. both in west wing and garments building | Provide minimum aisle widths of 36-in. | Completed | Apr 13 2016 | On 30/08/2016: Corrected. On 21/11/2016: Corrected. On 29/01/2017: Corrected. On 20/07/2017: Provided On 03/01/2018: Corrected as per previous follow up. This issue will also reflect by the issue no 26. On 12-07-2018: Corrected. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 14 | NEW FINDING (2nd follow-up): Occupant load sign is missing | Provide occupant load sign in appropriate places next to exit of each production floor | Completed | Apr 13 2016 | On 30/08/2016: Corrected. On 21/11/2016: Corrected. On 29/01/2017: Corrected. On 04/04/2017: Corrected. On 20/07/2017: Posted On 03/01/2018: Corrected as per previous follow up. On 12-07-2018: Corrected. On 27/02/2019: Posted. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 15 | NEW FINDING (2nd follow-up): Exit capacity is not adequate for the occupant load on 1st floor of garments building. | Factory shall provide either of the following: - Reduce occupant load to not more than available exit capacity. - Provide additional exits in the future to increase exit capacity. | Completed | Apr 13 2016 | On 30/08/2016: Corrected. On 21/11/2016: Corrected. Factory already has made a additional exit stair at east side. On 29/01/2017: Corrected. On 04/04/2017: Corrected. On 20/07/2017: Completed. Reduced On 03/01/2018: Corrected as per previous follow up. Note: factory will ensure safe exit as per Accord recommendation. On 12-07-2018: Corrected. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 16 | NEW FINDING (2nd follow-up): Storage was located on the egress path in 1st floor of garments building | Keep egress paths and stairs clear of storage. | Completed | Apr 13 2016 | On 30/08/2016: Corrected. On 21/11/2016: Corrected. On 29/01/2017: Corrected. On 04/04/2017: Corrected. On 20/07/2017: Found same as before during inspection. On 03/01/2018: Corrected as per previous follow up. On 12-07-2018: Corrected. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 17 | NEW FINDING (2nd follow-up): Areas used for combustible storage are not separated by fire-rated construction in garments building | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Completed | Jul 30 2016 | On 30/08/2016: Corrected. During follow up inspection storage arrangement was found as per standard. On 21/11/2016: Corrected. On 29/01/2017: Corrected. On 04/04/2017: Corrected. On 20/07/2017: In-process areas shall be defined properly. Dedicated stores are not separated yet. On 03/01/2018: It has been found same as the previous follow. On 12-07-2018: Storages have been found in improper manner in garments building, 1st floor. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 18 | NEW FINDING (2nd follow-up): Parapets or guards with a minimum height of 1067mm (42in.). | Provide Parapets or guards with a minimum height of 1067mm (42in.) We will Provide Parapets or guards with a minimum height of 1067mm (42in.) | Completed | Apr 13 2016 | On 30/08/2016: Corrected. Factory has permanently closed balcony. On 21/11/2016: Corrected. On 29/01/2017: Corrected. On 04/04/2017: Corrected. On 20/07/2017: Completed On 03/01/2018: Corrected as per previous follow up. On 12-07-2018: Corrected as per previous follow up. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 19 | NEW FINDING (2nd follow-up): A single means of egress is provided from cutting section in south east corner of new floor where the occupant load exceeds 49 persons. | Provide either of the following:- Reduce occupant load to not more than 49 persons.- Provide additional means of egress. | Completed | Apr 13 2016 | On 30/08/2016: Corrected. Factory has created new exit. On 21/11/2016: Corrected. On 29/01/2017: Corrected. On 04/04/2017: Corrected. On 20/07/2017: Provided On 03/01/2018: Corrected as per previous follow up. On 12-07-2018: Corrected. On 27/02/2019: Provided. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1month | Corrected
Follow Up Inspection |  | 20 | NEW FINDING (2nd follow-up): The exit discharge path serving boiler room is less than 10 ft. wide and is not separated from the building interior of boiler and generator storage room | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft., to provide a minimum 1-hr fire separation. Alternatively, provide a second remote discharge path to the public way | Completed | Apr 13 2016 | On 30/08/2016: Corrected. On 21/11/2016: Corrected. On 29/01/2017: Corrected. On 04/04/2017: Corrected. On 20/07/2017: Completed On 03/01/2018: Corrected as per previous follow up. On 12-07-2018: Corrected as per previous follow up.. On 27/02/2019: Completed. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 21 | NEW FINDING (2nd follow-up): The exit stairs are not separated from work areas & other spaces on each floor by fire-rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. | Completed The management has completed the issue in a timely manner | Jul 30 2016 | On 30/08/2016: Partially corrected. Still factory didn't install door closer and push bar on east side exit fire rated. On 21/11/2016: Corrected. Fire door installation has been done. On 29/01/2017: Corrected as per last follow-up inspection. On 04/04/2017: Corrected. On 20/07/2017: Not separated, stairs of garments building yet. On 03/01/2018: Separation has been completed yet. Moreover east-middle discharge from 1st floor at garments building is interior discharge due to new building construction. On 12-07-2018: In progress. Stairs in garments building are not separated. On 27/02/2019: Comment is same as last follow up. On 02-01-2020: In progress. Exit from ground floor in garments building is not separated from adjacent store shed. On 29/08/2024: Progress found since last follow-up inspection. The exit has been removed from ground floor in garments building and has been separated from adjacent store shed by fire rated door. Moreover, The exit stairs has not been separated from work areas due to non-functionality of the fire doors. Fire doors were randomly checked and some of the fire doors did not latch properly and door coordinator was found non-functional. RPO Comments: 26-May-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 22 | New finding (6th follow-up): Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10 | Inspect, test and maintain the portable fire extinguishers and keep written records on-site, in accordance with NFPA 10. | Completed | Feb 2 2017 | On 29/01/2017: New finding. On 04/04/2017: Corrected. On 20/07/2017: Maintaining On 03/01/2018: Corrected as per previous follow up. On 12-07-2018: Corrected. On 27/02/2019: Corrected. On 29/08/2024: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 23 | New finding (6th follow-up): Compressor room or furnace room is not properly separated by fire rated construction with other Occupancies/Are as (specify the occupancy/area, location and construction materials of room). | Compressor room or other heat producing equipment shall be separated from other occupancies by a minimum 1-hr (2-hr for highrise building) fire rated construction (wall, floor, slab etc). Seal all penetrations and openings (door, window etc.) should be protected by 0.75-hr (45 min) fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. Or Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building | Completed | Mar 1 2017 | On 29/01/2017: New finding. On 04/04/2017: Corrected. On 20/07/2017: Needs to separated them from generator rooms. On 03/01/2018: Not separated from production floor. On 12-07-2018: Not corrected yet. Compressor has been found in generator room without separation. On 27/02/2019: Separated. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 24 | New finding (7th follow-up): Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. Location- Dying Shed | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Completed | May 4 2017 | On 04/04/2017:New finding. On 20/07/2017: In-progress On 03/01/2018: Adequate illumination has been observed on several places including printing section and 1st floor of garments building. On 12-07-2018: All emergency light in one aisles in dyeing shed have been found inactive. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 25 | New finding (7th follow-up): Dining area is not separated from other occupancies with fire rated assemblies. | Re-locate the dining area or separate the dining area from other occupancies with fire rated construction | Completed | May 4 2017 | On 04/04/2017:New finding. On 20/07/2017: In-progress On 03/01/2018: Dining area has been already replaced from the left over or jhut storage room but female prayer has not been separated from this storage room. On 12-07-2018: Comment is same as last follow up. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 26 | New finding (7th follow-up): Width of aisles is less than 0.9m (36-in.). Location- Cutting and washing section. | Aisles shall be provided with a minimum unobstructed clear-width of 0.9 m (36 in.). | Completed | May 4 2017 | On 04/04/2017:New finding. On 20/07/2017: Provided On 03/01/2018: Proper aisles has not been provided on 1st floor at garments building and proper aisles as well as safe exit discharge has not been provided from printing section. On 12-07-2018: Factory has changed the machine layout to provide recommended aisles. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 27 | New finding (7th follow-up): Unsealed penetrations and openings are located in exit stair enclosures. | Seal all penetrations and openings in the wall of exit enclosure walls (full thickness of the wall) by fire rated materials to maintain the fire resistance rating. | Completed | May 4 2017 | On 04/04/2017:New finding. On 20/07/2017: Sealed On 03/01/2018: Corrected as per previous follow up. On 12-07-2018: No unsealed penetration has been found during inspection. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 28 | New finding (7th follow-up): Diesel Fuel Storage was found in the Generator room of the Building( Utility Building) | Remove the diesel fuel storage from the generator room or provide minimum 2 hour Fire rated separation | Completed | May 4 2017 | On 04/04/2017:New finding. On 20/07/2017: Removed On 03/01/2018: Corrected as per previous follow up. On 12-07-2018: Corrected as per previous follow. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 29 | New finding (9th follow-up): Manual on-off switch is provided for emergency lighting / exit signage units at several places. | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. | Completed | Jan 31 2018 | New finding (9th follow-up) On 12-07-2018: Corrected. On 27/02/2019: Corrected. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 30 | New finding (10th follow-up): The boiler room is not properly separated by fire-rated construction from dyeing section.During inspection, no listed mark/documents have been found on fire door.Moreover vision glass was not installed in tha fire door though there is a provision of it. | Separate the boiler room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | Completed | Aug 30 2018 | NEW FINDING On 27/02/2019: Separated. On 02-01-2020: Corrected on previous follow-ups. On 29/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 31 | New Finding (12th FU): Rooms used for storage of combustible materials are not separated from the surrounding occupancy/areas. Location: Dyeing Shed, Garments Building | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour construction. | Completed | Mar 3 2020 | On 02-01-2020: New Finding On 29/08/2024: Corrected. Storage room has been separated by fire rated construction and opening is protected by fire rated door from the surroundings occupancy/areas. | Within 2 months | Corrected

## Electrical
Date
19-Apr-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Apparel 21 Ltd., Shirir Chala, Bagher Bazer Gagipur Shadar, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-05-05
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Service line between pole mounted transformer and building, not supported. | Service cables/lines from the transformer till it enters the building must be supported and protected. | Completed | Nov 10 2014 | On 08/06/2016: Already verified in Accord first follow up inspection. Also found same during current inspection. | Within 3 Month | Corrected
Initial Inspection |  | 2 | Unprotected cable trenches. | Cable trench should be covered with concrete slab or checkered plates. | Completed | Oct 30 2014 | On 08/06/2016: Already verified in Accord first follow up inspection. Also found same during current inspection. | Within 1 Month | Corrected
Initial Inspection |  | 3 | Cables terminating at panel, not supported. | Cables behind panel must be supported and arranged on cable trays or ladder. | Completed | Oct 30 2014 | On 08/06/2016: Already verified in Accord first follow up inspection. Also found same during current inspection. | Within 1 Month | Corrected
Initial Inspection |  | 4 | Wirings in flexible PVC conduit entering panels are not firmly fixed. | Wiring in PVC flexible conduit entering panels must be firmly fixed at the panel (base / Top) using socket and check nuts. | Completed | Oct 30 2014 | On 08/06/2016: Already verified in Accord first follow up inspection. Also found same during current inspection. | Within 1 Month | Corrected
Initial Inspection |  | 5 | Panel base plates removed to allow cable entry. | Panel base plates must be installed, at all time and cable(s) entering panel must be firmly fixed with cable gland. | Completed | Jul 30 2015 | On 08/06/2016: Already verified in Accord second follow up inspection. Also found same during current inspection. | Within 1 Month | Corrected
Initial Inspection |  | 6 | Panel doors not connected with earth bond. | Panel door(s) must be connected with earth bond connecting frame and door. | Completed | Jul 30 2015 | On 08/06/2016: Already verified in Accord second follow up inspection. Also found same during current inspection. | Within 1 Month | Corrected
Initial Inspection |  | 7 | Wiring and cables installed in boiler room are not protected. | All electrical installations, including wiring and cable works must be protected against heat from the boiler by supporting and separating at safe distance. | Completed | Jul 30 2015 | On 08/06/2016: Already verified in Accord second follow up inspection. Also found same during current inspection. | Within 3 Months | Corrected
Initial Inspection |  | 8 | MCBs and contactors are not fixed firmly on the panel board, inside boiler control panel. | MCB, contactor and other devises used in panel must be firmly fixed and protected from touching unintentionally to other live parts. | Completed | Oct 30 2014 | On 08/06/2016: Already verified in Accord first follow up inspection. Also found same during current inspection. | Within 1 Month | Corrected
Initial Inspection |  | 9 | Storage in generator room. | Remove diesel and other oil barrels from generator room. | Completed | Jul 30 2015 | On 08/06/2016: Already verified in Accord second follow up inspection. Also found same during current inspection. | Within 1 Month | Corrected
Follow Up Inspection |  | 10 | New Finding: Lightning Protection System(LPS) has not installed yet | Design and Install LPS for your factory; Factory have to submit LPS design to Accord before starting installation. | Completed | May 31 2016 | On 29/01/2017: Not Corrected. On 13/03/2017: Factory is asking till 30/05/2017, timeline extension is not accepted. On 04/04/2017: Not corrected. On 20/07/2017: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 11 | New Finding: Electrical Single Line Diagram (SLD) has inadequate information which has no effectiveness. | Prepare SLD more informative thus anyone can understand it. | Completed | Apr 30 2016 | On 13/03/2016: This issue is not corrected yet. New timeline is till 30/04/16 On 08/06/2016: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 12 | New Finding: Insulation resistance test of electrical cables is not performed | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off) | Completed | Apr 30 2016 | On 13/03/2016: This issue is not corrected yet. New timeline is till 31/04/16 On 08/06/2016: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 13 | New Finding: Earth Pit resistance record is unavailable | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. | Completed | Apr 30 2016 | On 13/03/2016: This issue is not corrected yet. New timeline is till 31/04/16 On 08/06/2016: Report is available but inadequate. This issue is not corrected yet. Factory is behind time schedule. On 30/08/2016: Earth pit resistance record is not available for all earth pits. On 21/11/2016: Not corrected. Earth pit resistance record is not available for all earth pits. On 29/01/2017: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 14 | New Finding: No/Inadequate rubber (insulation) mat on the working are of distribution board/panel. | Put electrical insulation (rubber mat) on the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) | Completed | Jul 30 2015 | On 08/06/2016: Already verified in Accord second follow up inspection. Also found same during current inspection. | Within 2 Months | Corrected
Follow Up Inspection |  | 15 | New Finding: Battery cases are kept in wooden case | Use non-flammable case/shelf to store battery | Completed | Jul 30 2015 | On 08/06/2016: Already verified in Accord second follow up inspection. Also found same during current inspection. | Within 1 Month | Corrected
Follow Up Inspection |  | 16 | New Finding: Loop connection has used powering multiple MCBs/MCCBs. | Eliminate loop cables; use single cable for each MCBs/MCCBs. You may use bus bar to avoid multiple termination. | Completed | Jan 31 2016 | On 08/06/2016: Already verified in Accord second follow up inspection. Also found same during current inspection. | Within 2 Months | Corrected
Follow Up Inspection |  | 17 | New Finding: Multiple cables terminated at MCCB terminals/ Bus bar. | Terminate each power cable at single terminal and use proper sized cable lug. | Completed | Jan 31 2016 | On 08/06/2016: Already verified in Accord second follow up inspection. Also found same during current inspection. | Within 2 Months | Corrected
Follow Up Inspection |  | 18 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals | Completed | Apr 30 2016 | On 13/03/2016: This issue is not corrected yet. New timeline is till 31/04/16 On 08/06/2016: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 19 | New Finding: Light in store room/storage areas is uncovered. | Lights in store room/ storage areas shall be covered | Completed | Apr 10 2016 | On 13/03/2016: This issue is not corrected yet. New timeline is till 31/04/16 On 08/06/2016: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 20 | New Finding: Cables in service are joined (splicing) between terminations. | Existing cables with joints must be spliced using butt splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. | Completed | Jul 30 2015 | On 08/06/2016: Already verified in Accord second follow up inspection. Also found same during current inspection. | Within 2 Months | Corrected
Follow Up Inspection |  | 21 | New Finding: Wastage water drain in front of panel. | Put a arrangement to provide obstacle for water. Cover the drain or stop discharging waste water through this drain. Access route of the panel shall be free of water. | Completed | Apr 30 2016 | On 13/03/2016: Rubber mat shall be used in front of panel and keep the access route of the panel free of water. So, this issue is not corrected yet. New timeline is till 30/04/16 On 08/06/2016: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 22 | New Finding: Electric safety training program is not initiated/conducted. | Electrical safety training and awareness program for the electrical personal and workers must be initiated and recorded | Completed | Apr 30 2016 | On 13/03/2016: This issue is not corrected yet. New timeline is till 31/04/16 On 08/06/2016: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 23 | New Finding: Cable gland holes are left open. | Seal each distribution board's top/bottom and cable entering holes and use cable glands holding/supporting cables. | Completed | Oct 10 2016 | On 30/08/2016: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 24 | New Finding: Panel/Distribution box's doors can not be opened fully to perform maintenance work. | Take necessary initiative thus every panel/ distribution board can be easily accessible. | Completed | Oct 10 2016 | On 30/08/2016: This issue is not corrected yet. New committed timeline is given till 10/10/2016 On 21/11/2016: Not corrected. On 29/01/2017: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 25 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals | Completed | Nov 10 2016 | On 21/11/2016: Not corrected. Factory is asking till 25/01/2017 Timeline extension is not accepted. On 29/01/2017: Not Corrected. On 04/04/2017: Not corrected. On 20/07/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 26 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. | Amend Electrical SLD properly. Mention all required information by qualified engineer and get it reviewed by Accord. It shall be an as-built drawing (if currently modified) in the factory. | Completed | Oct 10 2016 | On 03/01/2018: Not corrected. On 12/07/2018: Not Corrected. On 27/03/2019: Not Corrected. Factory has submitted SLD to ACCORD. On 14/09/2023: Not Corrected. SLD is Accepted on 06/12/2022 & significant progress is observed. Some load mismatch, TOB identification, MCCB and busbar size mismatch with Accepted SLD. RPO Comments: On 15-01-2024, The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. On 24/03/2024: Not corrected. 75 percent work completed in field. Still CB rating mismatch, load identification missing, busbar size mismatch have been observed in some places of building 1 & 2. On 21/05/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding: Periodicity of Thermography survey is not continued. | Thermography survey must be done and recorded at least twice in a year. | Completed | Dec 30 2016 | On 29/01/2017: Not Corrected. Still hot spot presents. On 04/04/2017: Not corrected. On 20/07/2017: Not corrected. On 03/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding: Hazardous lights in store room /storage areas are uncovered. | Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. | Completed | Dec 30 2016 | On 29/01/2017: Not Corrected. On 04/04/2017: Not corrected. On 20/07/2017: Corrected. No such issue was found during inspection. | 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/under sized | Earth lead cable/ Earth Continuity Conductor (ECC) must be resized by half of the phase cable. Cable size shall be selected depending on the CB's response time and phase cables' size. | Completed | Jan 25 2017 | Factory is asking till 25/01/2017. Timeline extension is accepted. On 29/01/2017: Not Corrected. On 03/04/2017: Factory is asking till 25/05/2017, timeline extension is not accepted. On 04/04/2017: Not corrected. On 20/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 30 | New Finding: Multiple cables (came from different electrical consumers) terminated at MCCB terminals/Busbar. | Each electrical circuit must be terminated at single MCB/MCCB terminals. | Completed | Jan 25 2017 | On 29/01/2017: Not Corrected. On 13/03/2017: Factory is asking till 20/04/2017, timeline extension is not accepted. On 03/04/2017: Factory is asking till 20/04/2017, timeline extension is not accepted. On 04/04/2017: Not corrected. On 20/07/2017: Not corrected. On 03/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: Distribution Board's bottom is left open (typical issue) | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. | Completed | Jan 25 2017 | On 29/01/2017: Not Corrected. On 04/04/2017: Not corrected. On 20/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 32 | New Finding: Cables inside distribution board are disorganized. | Cables inside each distribution board shall be well organized to avoid misleading during any troubleshooting. distribution board's form is appreciated. | Completed | Jan 25 2017 | On 20/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: Cable channel/duct are left open for ingression of lint, dust or fluffs. | Cable ducts must be properly sealed to avoid ingression of any foreign particles. | Completed | Dec 30 2016 | On 29/01/2017: Not Corrected. Cables are barely visible due to dust. On 04/04/2017: Not corrected. Clean them periodically On 20/07/2017: Not corrected. On 03/01/2018: Not corrected. On 12/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 34 | New Finding: Meters and other electrical devices (Ammeter, Voltmeter) not functional on the main electrical equipment. | Different type meters and other electrical devices shall be installed in the main electrical distribution board/panel | Completed | Jan 25 2017 | On 29/01/2017: Not Corrected. On 04/04/2017: Not corrected. On 20/07/2017: Not Corrected. On 03/01/2018: Not corrected. On 12/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 35 | New Finding: Flexible PVC pipe has been used inside the panel covering cables. | Flexible PVC pipe shall not be used covering power cables. | Completed | Dec 30 2016 | On 29/01/2017: Not Corrected. On 20/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 36 | New Finding: Phase barrier/separators are missing in MCCBs. | Phases must be separated by insulator (a rubber type no-flammable materials shall be used for it) | Completed | Jan 25 2017 | On 29/01/2017: Not Corrected. On 04/04/2017: Not corrected. Power bus bar must be installed with adequate clearance (not less than 2.5 inch for LV) between two bars. Cables must not touch opposite bus bars in any case. On 20/07/2017: Not corrected. On 03/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Multiple cables connected/terminated at the bus bar using single cable lug. | Each power cable must be terminated at any point using single cable lug. | Completed | Jan 25 2017 | On 29/01/2017: Not Corrected. On 04/04/2017: Not corrected. On 20/07/2017: Not Corrected. On 03/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. | Completed | Dec 30 2016 | On 29/01/2017: Not Corrected. Cables are poorly supported almost everywhere. On 04/04/2017: Not corrected. On 20/07/2017: Not corrected. On 03/01/2018: Not corrected. On 12/07/2018: Not Corrected. On 27/02/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 39 | New Finding: Power cables entering or exiting from distribution board/panel are not properly fixed. | Power cables entering or exiting from distribution board/panel must be fixed through Panel base/top plate using proper sized cable glands (metal/PVC). | Completed | Jan 25 2017 | On 29/01/2017: Not Corrected. On 13/03/2017: Factory is asking till 20/04/2017, timeline extension is not accepted. On 04/04/2017: Not corrected. On 20/07/2017: Not corrected. On 03/01/2018: Not corrected. On 12/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: Power cables are laid on concrete floor. | Cables must be supported on cable ladder and riser with following standard cable laying technique. Cables may be laid in cable trench with covers. | Completed | Dec 30 2016 | On 29/01/2017: Not Corrected. On 04/04/2017: Not corrected. On 20/07/2017: Not Corrected. On 03/01/2018: Not corrected. On 12/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | Completed | Jan 25 2017 | Factory is asking till 25/01/2017. Timeline extension is accepted. On 29/01/2017: Not Corrected. On 04/04/2017: Not corrected. On 20/07/2017: Not corrected. On 03/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Maintenance record doesn't reflect with housekeeping. | Periodic maintenance must be done in the facility; proper and relevant documentation shall be kept. | Completed | Dec 30 2016 | On 29/01/2017: Not Corrected. Very poor maintenance work. On 04/04/2017: Not corrected. On 20/07/2017: Not corrected. On 03/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Cable connected to busbar/ MCCB/ MCB terminal without cable lug. | Each electrical circuit must be terminated at single busbar / MCB/ MCCB terminals using cable lug | Completed | Mar 20 2017 | On 13/03/2017: Timeline extended from 30-03-2017 to 20-03-2017 On 03/04/2017: Factory is asking till 30/04/2017, timeline extension is not accepted. On 04/04/2017: Not corrected. On 20/07/2017: Not corrected. On 03/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) must be ensured. | Completed | Mar 10 2017 | On 04/04/2017: Not corrected. On 20/07/2017: Not corrected. On 03/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Proper Electric safety training program has not initiated /conducted. | Electrical safety training and awareness program for the electrical personnel must be initiated. It is a periodic task which factory has to continue to improve overall electrical safety situation for the staffs | Completed | Mar 10 2017 | On 04/04/2017: Not corrected. On 20/07/2017: Not corrected. On 03/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Electrically operated machines (may have chance to be touched by operator/user) have no earth connection. | Each electrically operated machine (may have chance to be touched by user/operator) must have earth connection. Cable selection shall be made per CB response and circuit's power demand | Completed | Mar 10 2017 | On 04/04/2017: Not corrected. On 20/07/2017: Not corrected. On 03/01/2018: Not corrected. On 12/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Floor around control panel is wet. (Typical shock hazard) | A dry platform shall be in front of panel for maintenance purpose. Panel access shall be restricted to qualified people with proper equipment(e.g. rubber boot). | Completed | Apr 10 2017 | Timeline extended from 10-03-2017 to 10-04-2017 Factory is asking till 30/05/2017 Timeline extension is not accepted. On 04/04/2017: Not corrected. On 20/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Panel doors are not connected with earth | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution | Completed | Mar 20 2017 | Timeline extended from 10-03-2017 to 20-03-2017 On 04/04/2017: Not corrected. On 20/07/2017: Not corrected. On 03/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Insulation resistance record (cable information) is inadequate for the factory | Field information must be reflected in the record and significantly lower sized cables' record shall be avoided | Completed | May 30 2017 | On 20/07/2017: Not corrected. On 03/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Distribution boards have no clear identification markings. Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible location | Completed | May 30 2017 | On 20/07/2017: Not corrected. On 03/01/2018: Not corrected. On 12/07/2018: Not Corrected. On 27/02/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Inadequate sized earth cable connected to transformer & generator frame. | Two separate earth connection & one separate and distinct Neutral connection must be provided over transformer & generator. Generator & transformer body must have earth connection with half of phase conductor. | Completed | May 30 2017 | On 04/04/2017: Only one ECC pit is connected to generator On 20/07/2017: Not corrected. On 18/12/2017: Factory is asking till 18/12/2017; timeline extension is not acceptable. On 03/01/2018: Not corrected. On 04/03/2018: Factory is asking till 31/03/2018; timeline extension is not acceptable. On 12/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: BBT end cover is missing. Generator output box & tap-off box has openings. Combustible materials are tied with BBT. | BBT end covers shall be installed Seal the unwanted openings Combustible materials shall be removed from electrical system | Completed | May 30 2017 | On 20/07/2017: Not corrected. On 03/01/2018: Not corrected. On 12/07/2018: Not Corrected. On 27/02/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: Cable termination at the motor terminal box is directly connected to terminals without proper gland. Exhaust fans & Motor/Pumps are not earthed properly. | All equipment termination must be done with proper termination including cable glands to avoid ingression of moisture and dust entering the terminals. All Exhaust fans & Motor/Pumps shall be earthed properly. | Completed | May 30 2017 | On 20/07/2017: Not corrected. On 03/01/2018: Not corrected. On 12/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: Inadequate working space around panels and access to the panel is inconvenient. | Take necessary initiative thus every panel/ distribution board can be easily accessible. Ensure at least 1 meter (or equal to the width of board, whichever is higher) working clearance in front of each panel. To do so ensure uniform floor height around panel. | Completed | May 30 2017 | On 20/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding: Wooden support used for electrical installation/element. | Replace wooden support and it is preferable to fix each electrical devices with noncombustible support. | Completed | May 30 2017 | On 20/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 56 | New Finding: MCCB & magnetic contacts are installed without any enclosure No mechanical guards are provided for electrical equipment where necessary. Switch boards are not fixed properly | Each MCCB/MCB/ magnetic contact must be enclosed by proper type material. the material must not be more than 18 SWG graded. Provide mechanical guards for electrical equipment where necessary. Switch boards shall be fixed properly | Completed | May 30 2017 | On 20/07/2017: Not corrected. On 03/01/2018: Not corrected. On 12/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct) | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Completed | May 30 2017 | On 20/07/2017: Not corrected. On 18/12/2017: Factory is asking till 18/12/2017; timeline extension is not acceptable. On 03/01/2018: Not corrected. On 12/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: Electrical motors are installed in a non compliant location. Oil spillage/leakage has been observed in generator room. | Electrical motors shall be installed in a compliant location to avoid any unexpected accident. Any kind of oil spillage/leakage must be stopped; and generator must be kept always dry. | Completed | May 30 2017 | On 20/07/2017: Not corrected. On 03/01/2018: Not corrected. On 12/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: Power cable is buried in the concrete floor. Loop connection has been used powering multiple circuits through MCB/MCCBs. Three phase MCCB is used as double phase or single (input terminals are connected to three separate power bus bars) | Power cables must not be buried in the concrete. A cable trench shall be constructed or routing power cables. No loop connection shall be used; each single cable shall be terminated using cable lug (flat/I) at each terminal. Combo bus bar may be used (but incoming cable size must meet the rated capacity) A three phase MCCB/MCB must be used for three phase circuit. | Completed | May 30 2017 | On 20/07/2017: Not corrected. On 03/01/2018: Not corrected. On 12/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: Safety program is initiated but has no influence in the factory. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. | Completed | Aug 19 2018 | On 27/02/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Electrical Distribution board/panels are adjacent to water source. | Electrical distribution board/panels must not be installed within 2.5meter of any water source. | Completed | Aug 19 2018 | On 27/02/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Completed | Aug 19 2018 | On 27/02/2019: Corrected. No hot spots have been found. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Exhaust fan body and fan blade enclosure has no earth connection. | Adequate number of earth pits must be ensured for the factory with proper earth lead and earth electrode size as mentioned in BNBC requirements. mixing all together shall be avoided. | Completed | Aug 19 2018 | On 27/02/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 64 | New Finding: MCCBs are not installed/adjusted per load demand. | All the MCCBs/MCBs must be installed/adjusted as per connected load current; if adjustment is not possible, replacement will be the only way. | Completed | Nov 25 2023 | On 24/03/2024: Not corrected. Found in several places at Building 1, 2 and Utility area. On 21/05/2024: Corrected. | 2 MONTHS | Corrected
Follow Up Inspection |  | 65 | New Finding: Circuit breakers (MCCB/MCBs) are not easily accessible. | Each circuit breaker must be easily accessible from front of the panel board. | We already ensured circuit breaker are easily accessible from front of the panel board. Done | Nov 25 2023 | RPO Comments: 15-Jan-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 24/03/2024: Corrected. | 2 MONTHS | Corrected
Follow Up Inspection |  | 66 | New Finding: Insulation resistance test of electrical power cables is not satisfactory. | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off) | Done | Apr 27 2024 | On 21/05/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 67 | New Finding: Earth pit resistance record is not available for LPS. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made, and the result shall be available to the Inspector when required. | Done | Apr 27 2024 | On 21/05/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 68 | New Finding: Field information has no/less reflection in existing SLD. | As-built Electrical Single Line Diagram (SLD) must be prepared by a qualified engineer, including all essential details of the electrical system. This diagram must be reviewed and approved by the RSC. The accepted SLD needs to be implemented at the factory. All cables, all circuits, all terminals, all equipment are required to be identified as per the accepted Single line diagram. | The factory will engage a qualified electrical engineer to prepare and update the As-Built Electrical Single Line Diagram (SLD), obtain review and approval from RMG Sustainability Council (RSC), and implement the approved SLD by properly identifying and labeling all cables, circuits, terminals, and equipment accordingly. May 31, 2026 | Feb 3 2026 | RPO Comments: On 20-Apr-2026, The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 69 | New Finding: Oil spillage/leakage has been observed in generator room. | Any oil spillage or leakage around the generator must be promptly stopped, and the generator area must be kept dry at all times to prevent hazards and maintain safe operation. | All identified oil leakages around the generator have been repaired and cleaned, and the generator area has been secured, kept dry, and placed under regular monitoring and housekeeping control to ensure safe and hazard-free operation. Done | Jan 3 2026 | RPO Comments: 17-Feb-2026, the factory management reported the remediation completion. This item will be verified in the next inspectio. | 1 Month | Pending Verification
Follow Up Inspection |  | 70 | New Finding: Uncovered/Perforated type cable tray used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | The factory engineer will complete installation of all storage area wiring through GI pipe/solid metal duct or a concealed wiring system to ensure safety and compliance by 10 June 2026. | Jan 3 2026 | RPO Comments: On 20-Apr-2026, The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 71 | New Finding: Distribution boards have no clear identification markings. | Clearly mark all distribution boards, switchboards, sub-main boards, and switches for identification. | The factory engineer will clearly label and identify all distribution boards, switchboards, sub-main boards, and switches with permanent and visible markings to ensure proper identification, safe operation by June 10, 2026 | Jan 3 2026 | RPO Comments: On 20-Apr-2026, The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 72 | New Finding: Ceiling fan installed within reach of average human height. | Install the ceiling fan above average human height or ensure proper ventilation for the lift control room. | The ceiling fan has been removed from the finished goods area to eliminate potential hazards and ensure a safe working environment. Done | Jan 3 2026 | RPO Comments: 17-Feb-2026, the factory management reported the remediation completion. This item will be verified in the next inspectio. | 1 Month | Pending Verification