## Structural
Date
07-May-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Apparels JB21 Ltd., FS SFB #4,Road #2, Bay Area ,CEPZ, Chattogram, Dhaka
Date of Inspection |  | 2024-10-31
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Prepared design report needs to be reviewed against lateral loadings. Building 1 (MAIN PRODUCTION BUILDING) | The building engineer is required to revise the prepared DEA report based on as-built framing system & member sizes. Submit the revised DEA documents to the RSC for detailed review against lateral forces. | Drawings approved By RSC Structural Team on 31-05-2025. No Rettrofitting Needed. | Jan 5 2025 | On 13-Feb-2025: This issue is required cover in DEA. Factory submitted the DEA to RSC. DEA is currently under review. RPO Comments: On 24-Jun-2025, the design documents (DEA) have been reviewed and accepted by RSC on 31 May 2025. This item will be verified in the next inspection. | within 6 weeks | Pending Verification
Initial Inspection |  | 2 | Prepared design report needs to be reviewed against lateral loadings. Building 1 (MAIN PRODUCTION BUILDING) | Carry out suggested remedial works if required. | Drawings approved By RSC Structural Team on 31-05-2025. No Rettrofitting Needed. | May 24 2025 | On 13-Feb-2025: As per recommendation from the accepted DEA factory is required to carryout remediation work(if any). RPO Comments: On 24-Jun-2025, the design documents (DEA) have been reviewed and accepted by RSC on 31 May 2025. This item will be verified in the next inspection. | within 6 months | Pending Verification
Initial Inspection |  | 3 | Prepared design report needs to be reviewed against lateral loadings. Building 1 (MAIN PRODUCTION BUILDING) | Continue to implement a proper load management plan. | Drawings approved By RSC Structural Team on 31-05-2025. No Rettrofitting Needed. | May 24 2025 | On 13-Feb-2025: Load plan was posted. Loading was found within 63 psf. Factory is required to post and maintain final load plan after acceptance of DEA. RPO Comments: On 24-Jun-2025, the design documents (DEA) have been reviewed and accepted by RSC on 31 May 2025. This item will be verified in the next inspection. | within 6 months | Pending Verification
Initial Inspection |  | 4 | Discrepancy in as-built drawing. Building 1 (MAIN PRODUCTION BUILDING) | The building engineer is required to survey the whole structure and update the drawing reflecting on-site condition. | Drawings approved By RSC Structural Team on 31-05-2025. No Rettrofitting Needed. | Jan 5 2025 | On 13-Feb-2025: During inspection discrepancies were observed between as-built drawing and actual site conditions(e.g. steel column supported by RC water tanks, roof details of RO room etc.). Factory is required to update the as-built drawing with FEA model and submit to RSC as per review comments on the submitted DEA. RPO Comments: On 24-Jun-2025, CAP status has been changed Pending Verification based on the acceptence by the RSC on 31 May 2025. | within 6 weeks | Pending Verification
Initial Inspection |  | 5 | Gap between steel connection plates. Building 1 (MAIN PRODUCTION BUILDING) | The building engineer is required to fill the gap with suitable methods. | We already completed this issue. | Jan 5 2025 | .On 13-Feb-2025: The gaps between steel connection plates were filled. | within 6 weeks | Corrected
Initial Inspection |  | 6 | Dampness due to water ingress into the roof slab & brick wall. Building 1 (MAIN PRODUCTION BUILDING) | The factory is required to seal the source of water and repair the damp area with suitable method | We are working with our consultant for getting suitable method & it will complete by end of 31.01.25 | Jan 5 2025 | .On 13-Feb-2025: The source of water leakage were sealed. During the inspection, no further signs of dampness were observed. | within 6 weeks | Corrected
Initial Inspection |  | 7 | Corrosion of steel members. Building 1 (MAIN PRODUCTION BUILDING) | The building engineer is required to remove the corrosion and apply rust proof coating on steel members. | We already complete this issue. | Jan 5 2025 | .On 13-Feb-2025: Corrosion was removed from the affected steel members. A rust-proof coating was applied to the susceptible steel members to prevent further deterioration. | within 6 weeks | Corrected
Initial Inspection |  | 8 | Possibility of vehicle impact on columns. Building 1 (MAIN PRODUCTION BUILDING) | Factory is required to provide separate barriers for all exposed column/slabs at the loading-unloading zone floor to prevent from possible vehicle impact. | Done | Jan 5 2025 | On 13-Feb-2025: The factory installed vehicle impact protection for certain columns. However, some columns and edges of the protected columns remained unprotected and require vehicle impact protection. RPO Comments: On 21-Apr-2025, The factory management reported the remediation completion. This item will be verified in the next inspection. | within 6 weeks | Pending Verification
Initial Inspection |  | 9 | Column susceptible to trolly impact. Building 1 (MAIN PRODUCTION BUILDING) | Factory is required to provide a guard for all exposed columns and wall to prevent from possible trolly impact. | We already complete this issue. | Jan 5 2025 | .On 13-Feb-2025: Protective guards were installed to mitigate the impact of trolleys. | within 6 weeks | Corrected
Initial Inspection |  | 10 | Unbraced storage racks on different floors. Building 1 (MAIN PRODUCTION BUILDING) | The building engineer is required to provide anchorage/bracing to the storage racks to protect them from falling hazards. | We already complete this issue. | May 24 2025 | .On 13-Feb-2025: The storage racks were anchored. | within 6 months | Corrected

## Fire
Date
07-May-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Apparels JB21 Ltd., FS SFB #4,Road #2, Bay Area ,CEPZ, Chattogram, Dhaka
Date of Inspection |  | 2024-10-31
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The exit stairs are not separated from other spaces due to unprotected opening and penetrations. Location: Stair-2 at main Building. | Stair shall be enclosed with a minimum 2-hr fire-rated construction. Seal all unprotected openings and provide minimum 1.5-hr fire rated doors to separate the exit stairs from work areas and other building spaces on all floor levels. The clearance under the bottom of a door shall be a maximum of 3⁄4 in. (19 mm). Penetrations into and through an exit enclosure shall be prohibited with the exception of required exit doors, sprinkler piping, standpipes, electrical raceway for fire alarm equipment, and electrical conduit serving the exit enclosure. Ensure that the fire doors are self-closing, positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. | Corrected | Feb 24 2025 | On 23-Jul-25: Corrected. The exit stairs were found separated by fire rated construction and fire rated doors from operational areas at each floor. The penetrations were found sealed. On 02-Mar-26: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 2 | Storage room/areas discharges directly into the exit stair enclosure at ground floor and 1st floor. Location: main Building | Openings from exit enclosure to storage room, generator and transformer spaces shall be provided with a vestibule with fire rated construction and openings. The minimum width of a vestibule shall not be less than 1.1 m nor less than the width of the corridor leading to the vestibule. The minimum length of a vestibule in the direction of escape travel shall be 1.8 m. | Done | Feb 24 2025 | On 23-Jul-25: In-progress. Significant progress has been observed. The factory has closed a exit doors with stair enclosure on ground floor, and provided vestibule on 1st floor. However, during the inspection, it was observed that the vestibule was missing at the ground floor exit of Stair-2. On 02-Mar-26: Corrected. The factory has provided the vestibules at both ground and 1st floor between storage area and stair enclosures. | Within 3 months | Corrected
Initial Inspection |  | 3 | Penetrations through floor/ceiling assemblies due to electric cable are found unsealed. Location: Main Building | Seal all penetrations and openings in floor/ceiling assemblies by a listed through-penetration fire stop system tested in accordance with ASTM E814 or approved alternative standard to maintain minimum 3-hr. fire resistance rating. Installation shall be as per manufacturer published installation guideline and the certification authority's design criteria to ensure the required fire-rating. or, Provide a minimum 2-hr fire rated shaft to separate the penetration from each floor if required. or, If the aggregate area for busbar penetration through the floor/wall does not exceed 144 in², the factory can seal the busbar penetration using concrete, grout, or mortar installed to the full thickness of the floor/wall to maintain the fire resistance rating. | Corrected | Feb 24 2025 | On 23-Jul-25: Corrected. The penetrations due to electric cables were found sealed by mortar, as the area of those penetrations are within 144 in². On 02-Mar-26: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | Combustible storage was not separated from the Dining capacity at 4th for (reported more than 300 occupant) and the female prayer room with fire-rated construction. | To classify the occupancy as E4, it's necessary to limit the occupant load to 300 or below. Afterward, ensure a three-hour fire separation from other occupancies or remove the storage from the dining. Openings within such fire barriers shall be protected by opening protectives having a fire protection rating of not less than 3 hr. Additionally, ensure that there are required direct exits available for the dining facilities, or consider relocating them to a dedicated building. | Corrected | Feb 24 2025 | On 23-Jul-25: Corrected. No combustibles storages were found in the dining and female prayer room area on 4th floor during the inspection. On 02-Mar-26: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 5 | Office area (F1) was not separated from the Production area(G2) due to non rated door at main building. | Ensure the office area(F1) is fire separated by minimum 3-hr fire rated construction barrier with the production area(G2) as per table 3.2.1 of BNBC-2006. | Corrected | Feb 24 2025 | On 23-Jul-25: Corrected. The office area was found within 10 percent of total floor area and considered as an accessories occupancy of the production occupancy. So fire separation of office area is not required as per guideline. On 02-Mar-26: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 6 | Areas used for in-process storage of combustible materials are open to the surrounding occupancy. Location: Production Building | Provide defined storage areas and limit the storage arrangement as follows: Maximum height of 2.45 m and maximum area of 23 m² and is separated by a minimum 3.0 m (10ft) from other storage areas and they do not exceed 10 percent of the building area of the story in which they occur. or, If sprinkler protected, Maximum height 12 ft (3.66 m) and maximum area of 1000 ft² (93 m²) and separated by a at least 25 ft (7.62 m) and does not constitute more than 10 percent of the building area or 4000 ft² (372 m²) of the sprinklered area, whichever is greater. or, Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Corrected | Feb 24 2025 | On 23-Jul-25: Corrected. The in-process storages in production building were found as per the recommendation during the inspection. On 02-Mar-26: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 7 | Headroom clearance was found less than 6 feet 8 inches in the sewing area egress path due to the presence of the electrical channel, and main exit gate, and fire pump room | Ensure minimum headroom 6ft 8 inch or re-route the egress way to avoid the critical path. | Corrected | Dec 24 2024 | On 23-Jul-25: Corrected. The headroom clearance was found more than 6 feet 8 inches during the inspection. On 02-Mar-26: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 8 | Sliding type doors have provided along means of egress. Location: Inspection room and north east side main gate exit. | All doors in a means of egress shall be of the side---hinged swinging type. Roll-down and sliding gates and shutters shall not be allowed. Doors serving an occupant load of more than 50 shall swing in the direction of egress travel. | Corrected | Dec 24 2024 | On 23-Jul-25: Corrected. Sliding type door has been replaced by side hinged swinging type door in the inspection room. And a swinging type pocket door has been provided in the east side main gate exit. On 02-Mar-26: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 9 | The egress aisles available clear width were found less than 36 inch. Location: Accessories store main building. | Aisles shall be provided with a minimum unobstructed clear width of 0.9 m (36 in.). The path of egress travel along a means of egress shall not be interrupted by any obstruction. | Corrected | Dec 24 2024 | On 23-Jul-25: Corrected. The width of egress aisles in the accessories store on ground floor were found more than 36 inches during the inspection. On 02-Mar-26: Corrected. The width of aisles were not less than 36 inches during the inspection. | Immediately | Corrected
Initial Inspection |  | 10 | Building did not have occupant load signs at required locations. Locations: All Buildings | The occupant load shall be posted for every assembly and production floor in a facility in a conspicuous space near the main exit or exit access doorway for the space. | Corrected | Dec 24 2024 | On 23-Jul-25: Corrected. The occupant load signs were found at all the required locations. On 02-Mar-26: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 11 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. Location: Production Building | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Already Com[pleted This Issue. | Jan 24 2025 | On 23-Jul-25: The illumination levels were found inadequate through the means of egress at all the floors during the inspection. On 02-Mar-26: Significant progress has been observed since the last inspection. The factory has installed adequate emergency lights almost all the floors except 1st floor. The installation of emergency lights were found ongoig on 1st floor during the inspection. | Within 2 months | In Progress
Initial Inspection |  | 12 | Directional signs are not provided where direction of the path of travel to an exit has changed. Location: Production Building | Illuminated directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious. | Done | Jan 24 2025 | On 23-Jul-25: In-progress. The factory has increased the numbers of directional signs, but still found inadequate almost all the floors during the inspection. On 02-Mar-26: Significant progress has been observed since the last inspection. The factory has provided the directional exit sign almost all the floors where required, but still found inadequate in office areas during the inspection. | Within 2 months | In Progress
Initial Inspection |  | 13 | Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with the RSC standard. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with the RSC standard. Keep written records on-site. | Already Com[pleted This Issue. | Feb 24 2025 | On 23-Jul-25: Inspection, testing, and maintenance for the exit sign and emergency lighting system were not found in accordance with the RSC standard. On 02-Mar-26: Corrected. Inspection, testing, and maintenance for the exit sign and emergency lighting system were found during the inspection. | Within 3 months | Corrected
Initial Inspection |  | 14 | Updated Fire evacuation maps is not posted at the entrance of all exit stair. Locations: All Buildings | Fire evacuation maps shall be posted at the entrance to each exit stair. | Done | Jan 24 2025 | On 23-Jul-25: Updated fire evacuation maps were not posted at the entrance of exit stairs. On 02-Mar-26: Significant progress has been observed since the last inspection. The factory has provided the evacuatiom map in the stair enclosures at all the floors. But, the evacuation map on 1st floor was not updated as per floor layout change. | Within 2 months | In Progress
Initial Inspection |  | 15 | The buildings are not provided with compliant fire alarm and detection systems. The installation of the fire and detection system (FADS) has been completed . Locations: All Buildings | Addressable fire alarm and detection systems shall be installed throughout all buildings and structures (When complete sprinkler protection is provided throughout a floor with water flow devices designed to initiate the alarm notification, smoke and fire detection devices can be eliminated throughout that floor). Submit the proposed fire alarm system design to RSC for review. Once the design is reviewed, install the fire detection and alarm system throughout the building in accordance with review comment, RSC Technical Guidelines (Standard) and NFPA 72. After installation the owner shall conduct internal testing and commissioning and then contact the RSC for witness of final acceptance testing. | Already Com[pleted This Issue. | May 24 2025 | On 23-Jul-25: The factory has got the reviewed design drawing from RSC on 23-April-2025. The modification works as per reviewed design drawing as well as NFPA-72 was found ongoing during the inspection. Reportedly, the factory will apply for pre-T&CVI by 20-August-2025. During the inspection the FACP was found in normal condition. On 02-Mar-26: The factory has got a time extension till 15-March-2026 from RSC to complete the installation and submit the design drawing for pre-T&C review. Reportedly, the modification works as per reviewed design drawing as well as NFPA-72 has been completed and the factory will apply for pre-T&CVI by 15-March-2026. During the ispection the FACP was found in normal condition. | Design within 2 months and modification/ installation with 4 months | In Progress
Initial Inspection |  | 16 | Inspection, testing and maintenance for the fire detection and alarm system was not in accordance with standard. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with Table-14.3.1 of NFPA 72. | Already Com[pleted This Issue. | Jun 24 2025 | On 23-Jul-25: It is an integrated part of automatic fire alarm and detection system. On 02-Mar-26: It is an integrated part of automatic fire alarm and detection system. | Within 1 Month (after installation) | In Progress
Initial Inspection |  | 17 | The highest occupied floor of the main building is over 33 feet above grade, mandating a class III standpipe system. . Location: Main Building | A class III standpipe system (both a 40 mm connection with attached hose and a 65 mm connection) shall be installed throughout the production building (Where the building is protected throughout with automatic sprinklers a Class I standpipe (65 mm connections without attached hose) shall be permitted. The installation of Occupant Use (Class II 40 mm connections) shall not be required). Location: Production Building. Submit proposed fire Suppression System (fire pump, standpipe and sprinkler) design to RSC for review. Once the design is reviewed, install and modify the fire Suppression System throughout the building in accordance with review comment, RSC Technical Guidelines (Standard) and NFPA 13, 14, 20, 22 and 24. After installation the owner shall conduct internal testing and commissioning and then contact the RSC for witness of final acceptance testing. | Already Com[pleted This Issue. | May 24 2025 | On 23-Jul-25: The factory has submitted the proposed drawing for review on 16-July-2025 and awaiting for RSC's feedback. The installation of SUPS was found almost completed. Ventilation in pump room shall be as per manufacturer guideline. Emergency power shall be ensured for exhaust fan, mud pump etc. Drainage system shall be done properly in the pump room. Sprinklers were not installed in the pump room yet. On 02-Mar-26: The factory has got the reviewed design drawing on 21-Sep-2025 and supposed to complete the installation within the following next 3 months. The factory has got a time extension till 15-March-2026 from RSC to complete the installation and submit the design drawing for pre-T&C review. Reportedly, the modification works as per reviewed design drawing as well as relevant standard of NFPA has been completed and the factory will apply for pre-T&CVI by 15-March-2026. During the ispection the system was found in active condition. | Design within 2 months and modification/ installation with 4 months | In Progress
Initial Inspection |  | 18 | Inspection, testing and maintenance of the fire pump system is not in accordance with NFPA 25. | Inspect, test and maintain the fire pump system and keep written records on-site, in accordance with NFPA 25 and RSC standards. | Already Com[pleted This Issue. | Jun 24 2025 | On 23-Jul-25: It is an integrated part of fire pump system. On 02-Mar-26: It is an integrated part of fire pump system. | Within 1 Month (after installation) | In Progress
Initial Inspection |  | 19 | Inspection, testing and maintenance of the automatic sprinkler system is not in accordance with NFPA 25. | Inspect, test and maintain the automatic sprinkler system and keep written records on- site, in accordance with NFPA 25 and RSC standards. | Already Com[pleted This Issue. | Jun 24 2025 | On 23-Jul-25: It is an integrated part of sprinkler system. On 02-Mar-26: It is an integrated part of sprinkler system. | Within 1 Month (after installation) | In Progress
Initial Inspection |  | 20 | Inspection, testing and maintenance of the standpipe system is not in accordance with NFPA 25. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 25 and RSC standards. | Already Com[pleted This Issue. | Jun 24 2025 | On 23-Jul-25: It is an integrated part of standpipe and hose system. On 02-Mar-26: It is an integrated part of standpipe and hose system. | Within 1 Month (after installation) | In Progress
Initial Inspection |  | 21 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records on- site, in accordance with NFPA 10 and RSC standards. | Corrected | Jan 24 2025 | On 23-Jul-25: Corrected. Inspection, testing and maintenance of portable fire extinguishers were found in accordance with NFPA 10. On 02-Mar-26: Corrected. | Within 2 Months | Corrected

## Electrical
Date
07-May-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Apparels JB21 Ltd., FS SFB #4,Road #2, Bay Area ,CEPZ, Chattogram, Dhaka
Date of Inspection |  | 2024-10-31
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has less reflection in existing SLD. | As-built electrical Single Line Diagram (SLD) must be prepared by a qualified engineer, including all essential details of the electrical system. This diagram must be reviewed and approved by the RSC. The accepted SLD needs to be implemented at the factory. All cables, all circuits, all terminals, and all equipment are required to be identified as per the accepted single line diagram. | Done. | May 24 2025 | On 23/04/2025: SLD review status "Accepted" on 02-Feb-2025 from RSC. Corrected as per satisfactory pictorial evidence provided by factory. | 6 Months | Corrected
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not installed properly including improper air terminal spacing, missing air terminals, loose or disconnected conductors, rusty equipment. | Factory required to be redesign the Lightning Protection System (LPS) as per standard for the entire facility. Once the LPS is properly designed, it must be installed according to the design specifications to ensure effective protection against lightning strikes. | We already completed this issue. | Feb 24 2025 | On 23/04/2025: Corrected. | 3 Months | Corrected
Initial Inspection |  | 3 | No policies for LOTO (Lock-Out-Tag-Out) are introduced for the safety of the personnel during any kind of maintenance work. | Need to introduce and implement LOTO (Lock-Out-Tag-Out) policy using LOTO devices to ensure personnel safety during maintenance activities. All LOTO usage records must be maintained for compliance and safety monitoring. | We already completed this issue. | Dec 24 2024 | On 23/04/2025: Corrected. | 1 Month | Corrected
Initial Inspection |  | 4 | A programmed schedule for periodic inspection and testing of electrical equipment has been found but has not been updated. | Electrical maintenance programs should be developed to include regular inspections and testing of electrical systems, focusing on preventive and proactive measures. | We already complete this issue. | Dec 24 2024 | On 23/04/2025: Corrected as per satisfactory pictorial evidence provided by factory. | 1 Month | Corrected
Initial Inspection |  | 5 | Earth pit resistance test record doesn't match with field. | Field information must be accurately reflected in the record. All earthing systems must be tested for resistance on a dry day at least once every two years. Records of each earthing test and its results must be available for inspection when required. | We already complete this issue. | Dec 24 2024 | On 23/04/2025: Corrected. | 1 Month | Corrected
Initial Inspection |  | 6 | Insulation resistance record (cable information) doesn't match with field. | Field information must be accurately reflected in the record. Insulation resistance testing of all cables (excluding those less than 25 sq.mm) must be conducted once every two years and documented. This testing may require power shutdown to ensure accurate results and safety. | We already complete this issue. | Dec 24 2024 | On 23/04/2025: Corrected. | 1 Month | Corrected
Initial Inspection |  | 7 | Electrical motors are not fixed at base. | All electrical motors must be securely mounted at their base using proper anchoring and fastening methods. | We already complete this issue. | Jan 24 2025 | On 23/04/2025: Corrected as per satisfactory pictorial evidence provided by factory. | 2 Months | Corrected
Initial Inspection |  | 8 | Lead acid battery terminals are left open. | Lead-acid battery terminals must be covered or capped, and any rust must be thoroughly cleaned to ensure safe and efficient operation. | We already completed this issue. | Dec 24 2024 | On 23/04/2025: Corrected. | 1 Month | Corrected
Initial Inspection |  | 9 | Indicator lights are mounted without disconnecting device. | Indicator lights must be connected through a control device, such as a rated fuse or circuit breaker (CB), to ensure they are properly protected and can be safely operated. | We already completed this issue. | Jan 24 2025 | On 23/04/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 10 | Distribution board's top is left open (typical issue). | Each electrical distribution board or panel must be sealed to prevent the ingress of fluffs and dust. Adequate ventilation must also be ensured to maintain optimal operating temperatures. Cable glands should be used where required to secure cables and maintain the integrity of the seal. | We already complete this issue. | Jan 24 2025 | On 23/04/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 11 | Circuit breakers have no capacity information. | Each circuit breaker must be clearly labeled with its capacity information. | We already complete this issue. | Dec 24 2024 | On 23/04/2025: Corrected. | 1 Month | Corrected
Initial Inspection |  | 12 | Phase barrier/separators are missing in circuit breaker. | Phases must be separated by insulators made from non-flammable rubber-type materials to prevent electrical short circuits and enhance safety. | We already complete this issue. | Dec 24 2024 | On 23/04/2025: Corrected. | 1 Month | Corrected
Initial Inspection |  | 13 | Multiple cables from different electrical consumers are terminated at busbars. | Each electrical circuit must be terminated at a single circuit breaker terminal or busbar to ensure distribution and protection within the electrical system. | We already complete this issue. | Jan 24 2025 | On 23/04/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 14 | Nut-bolt, busbar & washer are rusted in the sub/ distribution board. | Rusted nut-bolt, busbar & washer must be replaced with new one. | We already complete this issue. | Jan 24 2025 | On 23/04/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 15 | Power cables are hanging without support. | Power cables must be supported by a cable tray (ladder- where needed). Outdoor cables must be covered, if required. | We already complete this issue. | Jan 24 2025 | On 23/04/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 16 | Power cables are buried in the concrete floor. | Power cables should be routed through a covered cable trench. |  | Jan 24 2025 | On 23/04/2025: Not corrected. Work is not done appropriately; still, cables are buried in the concrete floor. On 22/01/2026: Not corrected. Progress has been observed. This issue has been solved in the fire pump room but still exists on the ground floor of the main production building. | 2 Months | In Progress
Initial Inspection |  | 17 | Outdoor cable is not covered to protect from the weather effects. | All power cables exposed to weather shall have cover unless it is specified for outdoor wiring. | We already complete this issue. | Jan 24 2025 | On 23/04/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 18 | Exhaust fan body and fan blade enclosure are not equipped with earth connection. | Exhaust fan frame and its enclosure in the production area/s shall be connected to earth. | We already complete this issue. | Jan 24 2025 | On 23/04/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 19 | Indicator lamps and metering devices (Ammeter, Voltmeter) installed on panel board are not operational. | All indicator lamps and metering devices installed on the panel board must be fully operational to prevent the risk of false or misleading information, which could compromise the safety and proper functioning of the electrical system. Regular checks and maintenance should be conducted to ensure their accuracy and reliability. | We already complete this issue. | Jan 24 2025 | On 23/04/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 20 | Water bottle/ combustible/ flammable materials are attached with electrical panel board/ BBT/ cable channel/duct. | All flammable and combustible materials, including water bottles and other items, must be cleared from electric cable channels, ducts, and BBTs. Separate storage arrangements for these materials should be implemented. | We already complete this issue. | Jan 24 2025 | On 23/04/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 21 | No mechanical guards are provided for rotating electrical equipment where necessary. | Ensure all rotary installations are equipped with adequate safety measures, including the provision of mechanical guards to prevent accidents. | We already complete this issue. | Dec 24 2024 | On 23/04/2025: Corrected. | 1 Month | Corrected
Initial Inspection |  | 22 | Power sockets are kept on floor/hung without support. | Power sockets must be securely installed on rigid supports or bases, positioned at a minimum height of 200 mm above the floor level. | We already complete this issue. | Jan 24 2025 | On 23/04/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 23 | Maintenance movement is an obstacle due to the uneven height of cable trench in utility area. | The workspace surrounding the transformer, generator, or any other electrical installations must be level and uniform in height. This ensures safe and efficient access for maintenance and operational activities while minimizing potential trip hazards, thereby enhancing overall safety and productivity. | We already complete this issue. | Jan 24 2025 | On 23/04/2025: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 24 | New Finding: Hot spots have been observed at some points. | Hot spots throughout the entire electrical system must be eliminated to ensure safety and prevent potential equipment failures or hazards and reduce downtime and repair costs. | Already done. | May 23 2025 | On 22/01/2026: Corrected. | 1 Month | Corrected

## Boiler
Date
07-May-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Apparels JB21 Ltd., FS SFB #4,Road #2, Bay Area ,CEPZ, Chattogram, Dhaka
Date of Inspection |  | 2025-11-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 7214 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | Corrected | Apr 18 2026 | Comments on 03-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 7214 | Boiler's initial registration certificate was not available on-site during the inspection. | Boiler registration certificate from the government authority which was provided after the installation shall be available on-site during the inspection. | we will complete witin 18.04.2026 | Apr 18 2026 | Comments on 03-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 3 | BB 7214 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | we will complete witin 18.04.2026 | Apr 18 2026 | Comments on 03-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 4 | BB 7214 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Corrected | Apr 18 2026 | Comments on 03-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 7214 | The boiler nameplate was not in a standard language. | The boiler manufacturer's nameplate shall be available on the boiler with proper technical information and the boiler manufacturer's name in a standard language such as in English or Bengali. | Corrected | Apr 18 2026 | Comments on 03-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 7214 | Boiler exhaust gas pipeline inside the boiler room was found with improper insulation. | Proper insulation to boiler exhaust gas pipeline inside the boiler room causing heat exposure for personnel shall be provided. | Corrected | Mar 18 2026 | Comments on 03-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 7214 | Boiler body was found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | Corrected | Mar 18 2026 | Comments on 03-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 7214 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | Corrected | Mar 18 2026 | Comments on 03-Mar-2026: As per the pictorial evidence, the issue is not remediated yet. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. Please be informed that, only the valve wheels will remain outside insulation. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 9 | BB 7214 | Nameplates for feed pump were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | Corrected | Mar 18 2026 | Comments on 03-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 7214 | Drainage arrangement was not installed for safety valves. | Drainage arrangement must be installed for all safety valves as per manufacturer published guideline or at the lowest point of outlet line. | Corrected | Apr 18 2026 | Comments on 03-Mar-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 11 | BB 7214 | Valves were observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. | Corrected | Mar 4 2026 | Comments on 03-Mar-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 2 WEEKS | In Progress
Initial Inspection | External visual inspection | 12 | BB 7214 | Valves were observed between the boiler and the water level limiter sensor. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. Any modification shall be consulted with the manufacturer. | Corrected | Mar 25 2026 | Comments on 03-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | External visual inspection | 13 | BB 7214 | Boiler Steam Header Safety Valve outlet line was not directed outside of the boiler room. | Boiler Steam Header Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | Corrected | Mar 18 2026 | Comments on 03-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 14 | BB 7214 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | Corrected | Mar 4 2026 | Comments on 03-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 15 | BB 7214 | Carbon deposition was found in the smoke tubes and furnace chamber. | The furnace and inside of the fire tubes should be cleaned periodically to prevent excessive soot build-up. The fuel burner should be adjusted according to the manufacturer's guidelines. | we will complete witin 18.04.2026 | Apr 18 2026 | Comments on 03-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 16 | BB 7214 | The inside of the boiler was found corroded due to inadequate water treatment. | Feed water must be externally or internally treated. The boiler operator should blow down regularly as per the manufacturer’s recommendation. Rapid boiling should be avoided. Shell and end plate thicknesses must be within the allowable limit specified by the manufacturer. | we will complete witin 18.03.2026 | Mar 18 2026 | Comments on 03-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 17 | BB 7214 | No boiler air vent was available at the highest position of the boiler. | An air vent at the highest point of the boiler should be provided by consulting the manufacturer. | Corrected | Apr 18 2026 | Comments on 03-Mar-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | Functional test inspection | 18 | BB 7214 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | Corrected | Mar 25 2026 | Comments on 03-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 19 | BB 7214 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | Corrected | Mar 18 2026 | Comments on 03-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 20 | BB 7214 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | we will complete witin 18.03.2026 | Mar 18 2026 | Comments on 03-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress