## Structural
Date
19-Jun-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Basic Apparels Ltd., 135-138, Abdullahpur (1st & 2nd floor), Uttara, Dhaka, Dhaka
Date of Inspection |  | 2014-04-06
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | No loading plan in place | Factory Engineer to produce and actively monitor a loading plan for all floor plates within the factory, with consideration given to slab, column and foundation capacities. | Last 22 November' 2017 DEA was re-accepted & According the Safe Load Plan is posted in floor. Retrofitting work has been going. | Sep 30 2014 | On 23/11/2014: ACCORD structural team visit in 23/11/2014 and found they have collect equation to do DEA.DEA yet not start. This issue will cover under DEA. On 22/06/2017: Both proposed and safe load plan have been prepared as a part of DEA. Factory management got DEA acceptance from ACCORD on 25/05/2017. During inspection proposed load plan (2 kPa) was found posted. However, floor loading was found more than 3 kPa on 1st floor. Factory management needs to maintain safe load plan (1 kPa) until completion of retrofitting works. On 26/07/2017: A set of load plan has been prepared and submitted to ACCORD for review along with DEA report which got acceptance by ACCORD on 25-May-2017. During verification inspection, major discrepancies were observed at beam, column layout and dimension. Loading was found within 42 psf during inspection. However, factory has not started retrofitting work yet. Factory is required to maintain safe load plan until the completion of retrofitting works. On 26/10/2017: This issue will cover in DEA. DEA report got acceptance on 25-May-2017. On 26-July-2017 during verification inspection some discrepancies was found. Factory was submit the revised DEA on 19th September, 2017. A review mail was sent to the factory on 8th October to submit the revised documents within 25th October which has not submitted yet. On 04/12/2017: Load plan had been reviewed and re-accepted by Accord on 22 Nov, 2017. Factory is maintain safe load plan but no load plan was posted on the floor. Final load plan will be followed after completion of remediation works. On 12/07/2018: A safe load plan (21 psf for 1st and second floor, 42 psf for 3rd and 4th floor) has been prepared as part of DEA which was re-accepted from ACCORD on 22-Nov-2017. Safe load plan was found posted in the building. Load was found above 42 psf in some slab-panels in 3rd floor. Uncontrolled loading was observed making load management plan questionable. On 27/09/2018: Load plan has been prepared as part of DEA which was re-accepted from ACCORD on 22/11/2017. As per re-accepted DEA, factory building required column strengthening. Factory has completed all the remediation works. Factory is now following final load plan (allowable 2 kPa). On 20/11/2018: Load plans were found posted. During inspection, floor loading was found below the allowable limit of final load plan. Issue remains corrected. On 18/06/2019: This issue has been corrected as per 7th follow up inspection. Load plans were found posted on all floors. During inspection, load was found below the allowable limit of final load plan. On 30- Dec-2019: This issue is corrected from previous follow-up inspection. On 09-Dec-2020: This issue was corrected as per 7th follow up inspection. Load plans were found posted on all floors. On 28-Jun-2021: This issue was corrected from previous inspection. Load plan was produced and accepted as a part of DEA. All retrofitting work had been completed as per accepted drawing. During inspection, accepted load plan was found posted at every floor and load was found below the allowable limit (2 KPa). On 18-Jan-2023: Corrected from previous inspection. Load plan was prepared as part of DEA which was reviewed and re-accepted by Accord on 22-Nov-2017. During inspection, load plan was found posted on each floor and loading was found within allowable limit as per accepted load plan (2 kPa). On 24-Jun-2025: Corrected previously. During inspection, loading was found within the limit (typical-42 psf). Load plan was found posted on each floor. | Within 6 – weeks | Corrected
Initial Inspection |  | 2 | No loading plan in place | Maintain and enforce the loading plans. | Last 22 November' 2017 DEA was re-accepted & According the Safe Load Plan is posted in floor. Retrofitting work has been going. | Dec 31 2014 | On 23/11/2014: DEA yet not start. This issue will cover under DEA. On 22/06/2017: Both proposed and safe load plan have been prepared as a part of DEA. Factory management got DEA acceptance from ACCORD on 25/05/2017. During inspection proposed load plan (2 kPa) was found posted. However, floor loading was found more than 3 kPa on 1st floor. Factory management needs to maintain safe load plan (1 kPa) until completion of retrofitting works. On 26/07/2017: As part of DEA, a set of load plan has been prepared and submitted to ACCORD which was accepted by ACCORD on 25-May-2017. During verification inspection, major discrepancies were observed at beam, column layout and dimension. Loading was found within 42 psf during inspection. However, factory has not started retrofitting work yet. Factory is required to maintain safe load plan until the completion of retrofitting works. On 26/10/2017: During inspection no load plan was found posted. This issue will cover in DEA. DEA report got acceptance on 25-May-2017. On 26-July-2017 during verification inspection some discrepancies was found. Factory was submit the revised DEA on 19th September, 2017. A review mail was sent to the factory on 8th October to submit the revised documents within 25th October which has not submitted yet. On 04/12/2017: Load plan had been reviewed and re-accepted by Accord on 22 Nov, 2017. Factory is maintain safe load plan but no load plan was posted on the floor. Final load plan will be followed after completion of remediation works. On 12/07/2018: A safe load plan (21 psf for 1st and second floor, 42 psf for 3rd and 4th floor) has been prepared as part of DEA which was re-accepted from ACCORD on 22-Nov-2017. Safe load plan was found posted in the building. Load was found above 42 psf in some slab-panels in 3rd floor. Uncontrolled loading was observed making load management plan questionable. On 27/09/2018: Load plan has been prepared as part of DEA which was re-accepted from ACCORD on 22/11/2017. As per re-accepted DEA, factory building required column strengthening. Factory has completed all the remediation works. Factory is now following final load plan (allowable 2 kPa). Load plan was found posted on all floor plates. On 20-Nov-2018: Load plans were found posted. During inspection, floor loading was found below the allowable limit of final load plan. Issue remains corrected. On 18/06/2019: This issue has been corrected as per 7th follow up inspection. Load plans were found posted on all floors. During inspection, load was found below the allowable limit of final load plan. On 30- Dec-2019: This issue is corrected from previous follow-up inspection. On 09-Dec-2020: This issue has been corrected as per 7th follow up inspection. Load plans were found posted on all floors. During inspection, load was found below the allowable limit of final load plan. On 28-Jun-2021: This issue was corrected from previous inspection. All retrofitting work had been completed as per accepted drawing. Load plan was produced and accepted as a part of DEA. During inspection, accepted load plan was found posted at every floor and load was found below the allowable limit (2 KPa). On 18-Jan-2023: Corrected from previous inspection. Load plan was prepared as part of DEA which was reviewed and re-accepted by Accord on 22-Nov-2017. During inspection, load plan was found posted on each floor and loading was found within allowable limit as per accepted load plan (2 kPa). On 24-Jun-2025: Corrected previously. During inspection, loading was found within the limit (typical-42 psf). Load plan was found posted on each floor. | Within 6 months | Corrected
Initial Inspection |  | 3 | Capacity of the roof slab and columns under the water tanks | Verify the capacity of the slabs, beams and columns beneath the water tanks. | DEA retrofitting work has been start from 1st February' 2018. Now work on going | Sep 30 2014 | On 23/11/2014: DEA yet not start. This issue will cover under DEA. On 22/06/2017: This issue has been covered in DEA report. Factory management got DEA acceptance from ACCORD on 25/05/2017. As per DEA recommendation factory is required to retrofit some structural elements. During inspection it was observed that retrofitting works not started yet. Factory management told that they would start retrofitting works within one month. On 26/07/2017: Designated consultant of the factory has verified the capacity of the slabs, beams and columns beneath the water tanks which was included in DEA report. DEA was accepted by ACCORD on 25-May-2017. During verification inspection, major discrepancies were observed at beam, column layout and dimension. Factory is required to submit revised DEA to ACCORD within provided timeline and complete retrofitting works as per revised DEA as soon as possible. On 26/10/2017: This issue will cover in DEA. DEA report got acceptance on 25-May-2017. On 26-July-2017 during verification inspection some discrepancies was found. Factory was submit the revised DEA on 19th September, 2017. A review mail was sent to the factory on 8th October to submit the revised documents within 25th October which has not submitted yet. On 04/12/2017: This issue is covered under DEA report. DEA of this factory had been reviewed and re-accepted by Accord on 22 Nov, 2017. Remediation were required as per DEA recommendation. All the remedial works must be completed by March 24, 2018. Remediation works were not start yet. On 12/07/2018: This issue has covered under DEA report. DEA of this factory had been reviewed and re-accepted by Accord on 22 Nov, 2017. Column, grade beam, steel retrofitting is required as per DEA recommendation. Steel retrofitting work was found completed, other retrofitting work was found on-going. 25% of total remedial work is remaining. On 27/09/2018: This issue was covered in DEA which was re-accepted from ACCORD on 22/11/2017. On 20/11/2018: DEA was re-accepted on 22/11/2017. Issue remains corrected. On 18/06/2019: This issue has been corrected as per 7th follow up inspection. DEA was re-accepted on 22/11/2017. On 30- Dec-2019: This issue is corrected from previous follow-up inspection. On 09-Dec-2020: This issue was corrected as per 7th follow up inspection. On 28-Jun-2021: This issue was corrected from previous inspection. DEA was reviewed and re-accepted from Accord on 22/11/2017. On 18-Jan-2023: Corrected from previous inspection. This issue was covered under DEA which was reviewed and re-accepted by ACCORD on 22-Nov-2017. On 24-Jun-2025: Corrected previously. | Within 6 – weeks | Corrected
Initial Inspection |  | 4 | Capacity of the roof slab and columns under the water tanks | This item can be managed by the loading plan mentioned in the item 1. | DEA retrofitting work has been start from 1st February' 2018. Now work on going | Dec 31 2014 | On 23/11/2014: DEA yet not start. This issue will cover under DEA. On 22/06/2017: Both proposed and safe load plan have been prepared as a part of DEA. Factory management got DEA acceptance from ACCORD on 25/05/2017. During inspection proposed load plan (2 kPa) was found posted. However, floor loading was found more than 3 kPa on 1st floor. Factory management needs to maintain safe load plan (1 kPa) until completion of retrofitting works. On 26/07/2017: A set of load plan has been prepared and submitted to ACCORD for review along with DEA report which got acceptance by ACCORD on 25-May-2017. During inspection, loading was found within 42 psf. However, factory has not started retrofitting work yet. Factory is required to maintain safe load plan until the completion of retrofitting works. On 26/10/2017: During inspection no load plan was found posted. This issue will cover in DEA. DEA report got acceptance on 25-May-2017. On 26-July-2017 during verification inspection some discrepancies was found. Factory was submit the revised DEA on 19th September, 2017. A review mail was sent to the factory on 8th October to submit the revised documents within 25th October which has not submitted yet. On 04/12/2017: This issue is covered under DEA report. DEA of this factory had been reviewed and re-accepted by Accord on 22 Nov, 2017. Floor load was measured below 2 kpa. Final load plan will be followed after completion of remediation works. On 12/07/2018: A safe load plan (21 psf for 1st and second floor, 42 psf for 3rd and 4th floor) has been prepared as part of DEA which was re-accepted from ACCORD on 22-Nov-2017. Safe load plan was found posted in the building. Load was found above 42 psf in some slab-panels in 3rd floor. Uncontrolled loading was observed making load management plan questionable. On 27/09/2018: Load plan has been prepared as part of DEA which was re-accepted from ACCORD on 22/11/2017. As per re-accepted DEA, factory building required column strengthening. Factory has completed all the remediation works. Factory is now following final load plan (allowable 2 kPa). Load plan was found posted on all floor plates. On 20/11/2018: Factory management has completed all the remedial works. Load plans were found posted. During inspection, floor loading was found below the allowable limit of final load plan. Issue remains corrected. On 18/06/2019: This issue has been corrected as per 7th follow up inspection. Load plans were found posted on all floors. During inspection, load was found below the allowable limit of final load plan. On 30- Dec-2019: This issue is corrected from previous follow-up inspection. On 09-Dec-2020: This issue was corrected as per 7th follow up inspection. On 28-Jun-2021: This issue was corrected from previous inspection. Load plan was produced and accepted as a part of DEA. During inspection, accepted load plan was found posted at every floor and load was found below the allowable limit (2 KPa). On 18-Jan-2023: Corrected from previous inspection. Load plan was prepared as part of DEA which was reviewed and re-accepted by Accord on 22-Nov-2017. During inspection, load plan was found posted on each floor and loading was found within allowable limit as per accepted load plan (2 kPa). On 24-Jun-2025: Corrected previously. | Within 6 months | Corrected
Initial Inspection |  | 5 | Movement joint at each floor level | At the joint at each floor level, verify the cantilevered sections of slabs and beams. | We have appointed an Engineer. His name is Golam Sarwer BUET. At this point of time he is doing all tests and have said an additional 3 months time is required to complete the detailed study. Moreover as the building is built for the first 3 floor by us | Sep 30 2014 | On 23/11/2014: DEA yet not start. This issue will cover under DEA. On 22/06/2017: This issue has been covered in DEA report. Factory management got DEA acceptance from ACCORD on 25/05/2017. On 26/07/2017: Found corrected from previous inspection. On 26/10/2017: This issue was corrected from previous inspection. On 04/12/2017: Corrected in the previous follow up report, as a part of DEA which is re-accepted by Accord on 22 Nov, 2017. On 12/07/2018: Corrected in previous inspection. On 27/09/2018: This issue has been corrected as per 2nd follow up inspection. The issue was covered in DEA which was re-accepted by Accord on 22/11/2017. On 20/11/2018: DEA was re-accepted on 22/11/2017. Issue remains corrected. On 18/06/2019: This issue has been corrected as per 7th follow up inspection. DEA was re-accepted on 22/11/2017. On 30- Dec-2019: This issue is corrected from previous follow-up inspection. On 09-Dec-2020: This issue was corrected as per 7th follow up inspection. On 28-Jun-2021: This issue was corrected from previous inspection. DEA was reviewed and re-accepted from Accord on 22/11/2017. On 18-Jan-2023: Corrected from previous inspection. This issue was covered under DEA which was reviewed and re-accepted by ACCORD on 22-Nov-2017. On 24-Jun-2025: Corrected previously. | Within 6 – weeks | Corrected
Initial Inspection |  | 6 | Movement joint at each floor level | Produce an assessment by the Factory Engineer. | We have appointed an Engineer. His name is Golam Sarwer BUET. At this point of time he is doing all tests and have said an additional 3 months time is required to complete the detailed study. Moreover as the building is built for the first 3 floor by us | Sep 30 2014 | On 23/11/2014: DEA yet not start. This issue will cover under DEA. On 22/06/2017: This issue has been covered in DEA report. Factory management got DEA acceptance from ACCORD on 25/05/2017. On 26/07/2017: Corrected in the previous follow-up inspection. On 26/10/2017: This issue was corrected from previous inspection. On 04/12/2017: This issue was corrected from previous inspection. On 12/07/2018: Corrected in previous inspection. On 27/09/2018: This issue has been corrected as per 2nd follow up inspection. The issue was covered in DEA which was re-accepted by Accord on 22/11/2017. On 20-Nov-2018: DEA was re-accepted on 22/11/2017. Issue remains corrected. On 18/06/2019: This issue has been corrected as per 7th follow up inspection. DEA was re-accepted on 22/11/2017. On 30- Dec-2019: This issue is corrected from previous follow-up inspection. On 09-Dec-2020: This issue was corrected as per 7th follow up inspection. On 28-Jun-2021: This issue was corrected from previous inspection. DEA was reviewed and re-accepted from Accord on 22/11/2017. All retrofitting work had been completed as per accepted drawing. On 18-Jan-2023: Corrected from previous inspection. This issue was covered under DEA which was reviewed and re-accepted by ACCORD on 22-Nov-2017. On 24-Jun-2025: Corrected previously. | Within 6 – weeks | Corrected
Initial Inspection |  | 7 | Shear cracks located at the intersection of the main and secondary beams. | Produce an assessment by the Factory Engineer for the validation for the shear design of the beams. | The factory engineer has made a detailed assessment. His recommendation is being followed by the construction workers and doing the necessary repair work.Some part is already completed. | Dec 31 2014 | On 23/11/2014: DEA yet not start. This issue will cover under DEA. On 22/06/2017: This issue has been covered in DEA report. Factory management got DEA acceptance from ACCORD on 25/05/2017. On 26/07/2017: Found corrected from previous inspection. On 26/10/2017: This issue was corrected from previous inspection. On 04/12/2017: Corrected in the previous follow up report and no cracks was observed during inspection. On 12/07/2018: Corrected in previous inspection. On 27/09/2018: This issue has been corrected as per 2nd follow up inspection. On 20/11/2018: Issue remains corrected. On 18/06/2019: This issue has been corrected as per 2nd follow up inspection. On 30- Dec-2019: This issue is corrected from previous follow-up inspection. On 09-Dec-2020: This issue was corrected as per 2nd follow up inspection. On 28-Jun-2021: This issue was corrected from previous inspection. DEA was reviewed and re-accepted from Accord on 22/11/2017. During inspection no crack was observed. On 18-Jan-2023: Corrected from previous inspection. This issue was covered under DEA which was reviewed and re-accepted by ACCORD on 22-Nov-2017. During inspection, no cracks were observed. On 24-Jun-2025: Corrected previously. No further crack was found on the beams. | Within 6 months | Corrected
Initial Inspection |  | 8 | Steel shed at roof level | Produce a Detailed Engineering Assessment of the steel shed at roof level. | Steel shade remediation work has completed. | Dec 31 2014 | On 23/11/2014: DEA yet not start. This issue will cover under DEA. On 22/06/2017: This issue has been covered in DEA report. Factory management got DEA acceptance from ACCORD on 25/05/2017. As per DEA recommendation retrofitting is required for the roof top steel shed. Retrofitting was not started yet. On 26/07/2017: As part of DEA, factory designated consultant has produced a detailed engineering assessment of the steel shed at roof level which got acceptance by ACCORD on 25-May-2017. As per DEA recommendations, retrofitting is required for the steel shed. However, factory has not started retrofitting work yet. Factory is required to complete retrofitting works as per DEA within provided timeline. On 26/10/2017: This issue will cover in DEA. DEA report got acceptance on 25-May-2017. On 26-July-2017 during verification inspection some discrepancies was found. Factory is required to submit their revised DEA report to ACCORD within given time line. On 04/12/2017: Steel shed at roof level had been reviewed and re accepted by Accord on 22 Nov, 2017. As per DEA recommendation, remediation were required for this shed but remediation were not start yet. On 12/07/2018: This issue has covered under DEA report. DEA of this factory had been re-accepted by Accord on 22 Nov 2017. Column, grade beam, steel retrofitting is required as per DEA recommendation. Steel retrofitting work was found completed as per drawing. On 27/09/2018: This issue has been corrected as per 6th follow up inspection. This issue was covered in DEA which was accepted from ACCORD on 25/05/2017. On 20-Nov-2018: DEA was re-accepted on 22nd Nov 2017. Issue remains corrected. On 18/06/2019: This issue has been corrected as per 6th follow up inspection. DEA was re-accepted on 22/11/2017. On 30- Dec-2019: This issue is corrected from previous follow-up inspection. On 09-Dec-2020: This issue was corrected as per 6th follow up inspection. On 28-Jun-2021: This issue was corrected from previous inspection. DEA was re-accepted on 22/11/2017. Steel retrofitting work was found completed as per drawing. On 18-Jan-2023: Corrected from previous inspection. This issue was covered under DEA which was reviewed and re-accepted by ACCORD on 22-Nov-2017. On 24-Jun-2025: Corrected previously. | Within 6 months | Corrected
Initial Inspection |  | 9 | Roof appears not to have any waterproofing system applied. | Apply a new waterproofing membrane. | We have started this work but with the advent of the rainy season we had to stop temporarily. Will continue and finish the work as soon as the dry season start. | Dec 31 2014 | On 23/11/2014: yet not start work On 22/06/2017: Water proofing membrane has been provided on roof. On 26/07/2017: Corrected in the previous follow-up inspection. On 26/10/2017: This issue was corrected from previous inspection. On 04/12/2017: Corrected in the previous follow up report and same as correct. On 12/07/2018: Corrected in previous inspection. On 27/09/2018: This issue has been corrected as per 2nd follow up inspection. Water proofing membrane has been provided on roof On 20-Nov-2018: Water proofing has been applied. Issue remains corrected. On 18/06/2019: This issue has been corrected as per 2nd follow up inspection. On 09-Dec-2020: This issue was corrected as per 2nd follow up inspection. On 28-Jun-2021: This issue was corrected from previous inspection. Water proofing has been applied and no water ponding was found. On 18-Jan-2023: Corrected from previous inspection. Factory has provided water proofing layer to avoid water ponding. On 24-Jun-2025: Corrected previously. | Within 6 months | Corrected
Follow Up Inspection |  | 10 | New Finding-1: Exposed rebar | Engage a qualified structural engineer to provide further analysis and develop a remediation plan, if required. | Report submitted with DEA Report | Sep 7 2017 | On 26/07/2017: During inspection, exposed rebar was observed at rooftop and at the side of the building from slab. Factory is required to cut these exposed rebar's or provide coating on these rebar's. On 26/10/2017: Few rebar was found still exposed. Factory is required to take necessary step regarding this issue. On 04/12/2017: During inspection rebar was found exposed, after that factory management send some picture regarding this issue by mail. Factory has been provided red oxide coating on expose rebar. On 12/07/2018: Exposed rebar's were found painted during inspection. On 27/09/2018: This issue has been corrected as per 6th follow up inspection. On 20-Nov-2018: Issue remains corrected. On 18/06/2019: This issue has been corrected as per 6th follow up inspection. On 30- Dec-2019: This issue is corrected from previous follow-up inspection. On 09-Dec-2020: This issue was corrected as per 6th follow up inspection. On 28-Jun-2021: This issue was corrected from previous inspection. Factory has been provided red oxide coating on expose rebar. On 18-Jan-2023: Corrected from previous inspection. Factory has cut off the expose rebar. On 24-Jun-2025: Corrected previously. Exposed rebar was found painted with rust-proofing chemical. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 11 | New Finding-2: Dampness in slab, beam and wall | Engage a qualified structural engineer to provide further analysis and develop a remediation plan, if required. | The issues Is correted. | Sep 7 2017 | On 26/07/2017: During inspection, dampness was observed at 4th floor in slab, beam and wall. Factory is required to engage a qualified structural engineer to provide further analysis and develop a remediation plan, if required. On 26/10/2017: During inspection dampness was found. Factory is required to take necessary step regarding this issue. On 04/12/2017: Dampness was found during inspection. Factory is required to take necessary step regarding this issue. On 12/07/2018: During inspection, dampness was observed in the exterior walls. On 27/09/2018: During inspection, dampness was observed on the exterior facade walls. On 20/11/2018: Dampness was found in the toilet zone. Factory later provided some pictorial evidences only painting the dampness. Factory is required to prepare investigation report with proper remediation and submit to ACCORD. On 18/06/2019: Factory has prepared an investigation report and repaired the locations of dampness. On 30- Dec-2019: This issue is corrected from previous follow-up inspection. On 09-Dec-2020: This issue is corrected from previous follow-up inspection. On 28-Jun-2021: This issue was corrected from previous inspection. Factory has repaired all damp areas and during inspection no dampness was observed, On 18-Jan-2023: Corrected from previous inspection. During inspection, no dampness was observed and as per investigation report factory has repaired all damp areas. On 24-Jun-2025: Corrected previously. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 12 | New Finging-3: Installation of immediate prop | Immediate props are to be installed in the ground floor. | Corrected | Oct 15 2017 | On 26/10/2017: As per accepted load plan and prop lay out plan, two column in main building is required to immediate prop in the ground floor which was installed as per recommendation. On 04/12/2017: Corrected in the previous follow up report. Props had been installed. On 12/07/2018: Corrected in previous inspection. Props were found installed as per drawing. On 27/09/2018: This issue was corrected as per 3rd follow up inspection. During inspection all remediation works were found completed. On 20/11/2018: Issue remains corrected. On 18/06/2019: This issue has been corrected as per 3rd follow up inspection. On 30- Dec-2019: This issue is corrected from previous follow-up inspection. On 09-Dec-2020: This issue was corrected as per 3rd follow up inspection. On 28-Jun-2021: This issue was corrected from previous inspection. On 18-Jan-2023: Corrected from previous inspection. Factory has completed all the remediation works. On 24-Jun-2025: Corrected previously. Factory has completed all the remediation works previously. | Immediately | Corrected
Follow Up Inspection |  | 13 | New finding-4: 3 Undocummented steel stairs adjucent to the main building. | Engage a qualified structural engineer to provide further analysis and develop a remediation plan, if required. | Steel Stair DEA has approved on dated last 28 / 12/ 2021. | Aug 23 2018 | On 12/07/2018: During inspection, 3 undocumented steel stair was observed which has not been covered in the initial report. Factory is required to engage a qualified structural engineer to provide further analysis and develop a remediation plan, if required. On 27/09/2018: Factory has not prepared any documents regarding this issue. During inspection, a work order for preparing the documents for those stairs were found on site. Factory is required to submit the documents with analysis of stairs to ACCORD as soon as possible. On 20/11/2018: Factory has appointed a consultant to prepared documents for the undocumented steel stair. Till the date of inspection, factory has not submitted the documents. Factory is required to submit the documents within required timescales. On 18/06/2019: Factory has submitted the documents to ACCORD which is under review. On 30- Dec-2019: As per last accepted documents, factory was required to demolish existing stairs and construction of proposed stairs within 25th Dec 2019. One of the three stairs was found demolished. One of the two proposed steel stairs construction was found on-going. Factory is required to complete all remediation works immediately. On 09-Dec-2020: EA of the steel stairs were accepted from Accord on 26-Sep-2019. As per recommendation of accepted EA documents, factory was required to replace the existing stairs with proposed stairs within 25th Dec 2019. Factory has completed the single stair though one of the beam on the roof of the single stair was found missing. Factory is required to install the missing beam. Moreover, Factory has started construction of the double stair. But the constructed ground floor portion of the double stair do not match the proposed steel stair drawing which was accepted previously. Factory is required to complete all remediation works as per recommendation of accepted drawings immediately. On 28-Jun-2021: Revised retrofitting scheme of steel stair has been accepted from RSC on 24th March 2021. However, during retrofitting verification inspection some discrepancies were observed between as-built drawing and as-built condition (See Retrofitting verification report). Factory is required to submit the revised documents (see required remediation in verification report) within 10 days of receiving the report. On 18-Jan-2023: This issue was covered under DEA which was reviewed and re-accepted by ACCORD on 28-Dec-2021. During inspection, accepted as-built drawings matched with on site condition. On 24-Jun-2025: Corrected previously. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 14 | New issue-5: Small new structures within factory premises: Office Shed, Toilet block, Generator Shed, Toilet Block, Entrance Shed. | Produce as-built drawing. | Shed drawing has approved also on dated last 28 / 12/ 2021. | Jul 15 2021 | .On 28-Jun-2021: During inspection Small new structures within factory premises: Office Shed, Toilet block, Generator Shed, Toilet Block, Entrance Shed which were not covered in initial inspection but being used under this factory. Factory engineer is required to produce as-built drawing of all of these new structures. On 18-Jan-2023: The toilet block area, Office Shed are being used by other factory now. Factory has prepared as-building for generator shed and demolished the entrance shed. During inspection, as built drawing of generator shed matched with onsite condition. On 24-Jun-2025: Corrected previously. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 15 | New issue-6: Lack of lateral stability of Office shed. | Check lateral stability of this shed. | Corrected, Waitting for ACCORD verification | Jul 15 2021 | .On 28-Jun-2021: No obvious stability system was found in Office Shed. No compression member and bracing system were found to transfer the lateral load. Factory is required to check the lateral stability of this shed and implement remediation work if required. On 18-Jan-2023: This toilet block area is being used by other factory now. So this issue is not valid anymore. On 24-Jun-2025: Corrected previously. N/A. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 16 | New issue-7: Damaged found in column-Generator shed (single story, area-300 sft) | Repair the damaged areas as per guidance by qualified consultant. | Corrected waitting for next RSC verification | Jul 15 2021 | .On 28-Jun-2021: During inspection, damaged found in column-Generator shed (single story, area-300 sft). Repair the damaged areas as per guidance by qualified consultant. On 18-Jan-2023: During inspection, it was observed that factory has repaired the damaged column on Generator shed by micro concrete under the supervision of building engineer. On 24-Jun-2025: Corrected previously. No further damage was found in the column of the generator shed. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 17 | New issue-8: Apparently non engineered entrance shed. | Provided engineered connection, replace undersized columns (east side) and provide compression member. | Corrected, Waitting for ACCORD verification | Jul 15 2021 | .On 28-Jun-2021: Entrance shed at west side of Main Factory building was appeared to be non engineered. Factory is required to provide engineered connection, replace undersized columns (east side) and provide compression member. On 18-Jan-2023: During inspection, it was observed that factory has demolished the entrance shed. On 24-Jun-2025: Corrected previously. Factory demolished the entrance shed. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 18 | New issue-9: Crack on brick wall of Toilet Block | Repair the cracked areas as per guidance by qualified consultant. | Corrected, But note that, the office shade is not belongs to BASIC Apparels | Jul 15 2021 | .On 28-Jun-2021: During inspection, crack was observed on brick wall of Toilet Block. Factory is required to repair the cracked areas as per guidance by qualified consultant. On 18-Jan-2023: This toilet block area is being used by other factory now. So this issue is not valid anymore. On 24-Jun-2025: Corrected previously. N/A. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 19 | New finding-10: Undocummented life core adjucent to the main building. | Engage a qualified structural engineer to provide further analysis and develop a remediation plan, if required. | Retrofitting work has completed and ready for followup verification | Mar 14 2023 | On 18-Jan-2023: During inspection, an undocumented life core was observed which has not been covered in the initial report. Factory is required to engage a qualified structural engineer to provide further analysis with remediation plan, if required and submit to RSC for review. On 24-Jun-2025: Factory prepared Engineering Assessment (EA) documents for the Five Storied Lift core of Main RC Building and received acceptance from RSC on 15 December 2024. Accepted drawings matched the site conditions. As per accepted EA factory completed all the remediation works. Also, construction completion certificate was found onsite. | (within 6 weeks) | Corrected

## Fire
Date
19-Jun-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Basic Apparels Ltd., 135-138, Abdullahpur (1st & 2nd floor), Uttara, Dhaka, Dhaka
Date of Inspection |  | 2014-04-15
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Hazardous materials storage area is not separated by fire-rated construction openings, non-rated doors and penetrations all present. | Separate the hazardous materials / flammable liquid storage room by a minimum 2hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | As we have more then 10 feets empty area between work place and temporary store, so we don't need to make Fire Resistance wall Infront of it, confirmed by Mr. Mahmudur Rahman (ACCORD Engineer) in a meeting with Shawkat Zaman & Ajay Agal (CEO, M.A.C.K & Basic respectively) at ACCORD office. | Apr 27 2016 | On 16-10-2018: Corrected. On 02/04/2019: Corrected. On 11-03-2020: Corrected. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Corrected. On 10/05/2023: Corrected. On 26-Dec-24: Corrected | Within 3 months | Corrected
Initial Inspection |  | 2 | The boiler room is not adequately separated by fire-rated construction (openings, non-rated doors, penetrations all present on the first floor only. | Separate the boiler room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations | Corrected the Issue | Apr 20 2016 | On 11-03-2020: Corrected as per previous follow-up. Note: Required fire door accessories shall be installed and maintain as per standard. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Corrected. On 10/05/2023: Corrected. On 26-Dec-24: Corrected | Within 3 months | Corrected
Initial Inspection |  | 3 | The exit stairs are not separated from work areas on each floor by fire-rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automaticclosing devices tied to the fire alarm system. | corrected | Apr 27 2016 | On 28/06/2021: Fire door installation had been done but interfacing with FACP didn't complete. (RCH) 19-Jul-2021: Time extension till 31 Aug 21 are not accepted. Remediation work must be completed as per approved timeline. (RCH) 12-Oct-2021: Time extension till 15 Nov 21 are not accepted. Remediation work must be completed as per approved timeline. On 27/06/2022: Magnetic door holder of fire door installation done. But door interfacing remaining with FACP.. Door kept opened by external objects. On 07/12/2022: The fire doors have been interfaced with FACP. Still the Stair-3 was not separated with store area. On 10/05/2023: All fire doors have been interfaced with FACP through magnetic door holder, but the magnetic door holder was not functioning properly during the inspection. On 26-Dec-24: Corrected. Fire doors were found to be functional during the inspection. Magnetic door holders were functional. | Within 3 months | Corrected
Initial Inspection |  | 4 | Unsealed penetrations and openings are located in exit stair enclosures. | Seal all penetrations and openings in exit stair enclosure walls and floors to maintain the fire separation. | we have sealed all the penetrations accordingly. | Oct 12 2015 | On 16-10-2018: Corrected. On 02/04/2019: Corrected as per previous follow-up. On 11-03-2020: Corrected as per previous follow-up. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Corrected. On 10/05/2023: Corrected. On 26-Dec-24: Corrected | Within 3 months | Corrected
Initial Inspection |  | 5 | Floors 1 and 2, combustible storage is not separated by firerated construction throughout factory. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Corrected. We are maintained regular | Apr 30 2016 | On 16-10-2018: Fire separation has been started. On 02/04/2019: Storage room at 1st floor was separated by fire rated construction. Defined storage area at several floors were not found within limit. On 11-03-2020: Storage areas at several floors were observed not maintaining as per recommendation. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Not corrected. (RCH) 19-Jul-2021: Time extension till 31 Aug 21 are not accepted. Remediation work must be completed as per approved timeline. On 27/06/2022: First floor store separated done. But in process storage was not maintained as recommendation at 3rd & 4th floor package section. On 07/12/2022: Corrected base on site condition. On 10/05/2023: Corrected. On 26-Dec-24: Corrected | Within 3 months | Corrected
Initial Inspection |  | 6 | Exit capacity is not adequate for the occupant load. The calculated egress capacity is not adequate for the number of employees on the first and second floors, this has to addressed immediately. First Floor:702 to 598 Second Floor: 702 to 598 | Immediately reduce occupant load to not more than available exit capacity. If possible, provide additional exits in the future to increase egress capacity. | The issue is corrected. It has complied with NFPA standard | Apr 3 2016 | On 16-10-2018: Corrected. On 02/04/2019: Corrected as per previous follow-up. On 11-03-2020: Corrected. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Corrected. On 10/05/2023: Corrected. On 26-Dec-24: Corrected | Immediate | Corrected
Initial Inspection |  | 7 | Collapsible steel sliding gated doors are provided at building exits, exit stairs, along egress routes on the first floor and main exit discharge at ground level. All egress doors were open with locks in sealed position. | Replace all gates / sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | We have removed all the collapsible gates accordingly and installed fire rated door all the exit points. | Oct 12 2015 | On 16-10-2018: Corrected. On 02/04/2019: Corrected. On 11-03-2020: Corrected. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Corrected. On 10/05/2023: Corrected. On 26-Dec-24: Corrected | Within 1 months | Corrected
Initial Inspection |  | 8 | The width of egress aisles is less than 36-in on the first and second floor due to structural column layout and design of sewing machine productions. | Provide minimum aisle widths of 36-in. | Corrected | Apr 20 2016 | On 02/04/2019: Corrected as per previous follow-up. Note: In few locations aisles width was observed less than 36 in. On 11-03-2020: Corrected as per previous follow-up. Note: Still in few location aisles width was observed less than 36 inch. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Corrected as per previous follow up. On 10/05/2023: Corrected. On 26-Dec-24: Corrected | Within 3 months | Corrected
Initial Inspection |  | 9 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | System is ready & fully functional. Waitting for RSC followup verification | May 30 2016 | On 28/06/2021: Still installation work is ongoing. On 27/06/2022: Installation of FADS completed except exhaust fan, lift & fire door interfacing. One fire control panel active & other one inactive due to power supply board of control panel faulty. Reportedly factory gave order new power supply board. On 07/12/2022: The Pre T&C has been conducted on dated 07 Dec 2022. The Fire Alarm & Detection System is not ready for Full T&C VI. See the details in Pre T&C VI report. On 10/05/2023: The Pre T&C has been conducted on dated 10 May 2023. The Fire Alarm & Detection System is not ready for Full T&C VI. See the details Pre T&C VI report. On 26-Dec-24: Fire alarm panel was functional & found to be in normal condition. Factory has resubmitted design & documents for Pre-T&C on 18-Dec-2024 which is under review. However, required input module supervisory signals were not found during the Suppression System T&CVI. Also, some modules were not properly marked & labeled. On 28-May-2025: Pre T&CVI was conducted and it was found that another Pre-T&CVI is required. See the details in the Pre-T&CVI report. RPO Comments on 14-May-2026 the factory management informed their system installation completed. T&CVI documents are under RSC's review | Design within 4 months, install within 9 months | In Progress
Initial Inspection |  | 10 | Inspection, testing, and maintenance for the fire alarm system was not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | System is ready & fully functional. Waitting for RSC followup verification | Apr 30 2016 | On 02/04/2019: It is an integrated part of fire alarm system. On 11-03-2020: It is an integrated part of fire alarm system. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: It is an integrated part of fire alarm system. On 27/06/2022: Ii is an integrated part of fire alarm system. On 07/12/2022: It is an integrated part of fire alarm system. On 10/05/2023: It is an integrated part of fire alarm system. On 26-Dec-24: It is an integrated part of fire alarm system. RPO Comments on 14-May-2026 the factory management informed their system installation completed. T&CVI documents are under RSC's review | Within 3 months | In Progress
Initial Inspection |  | 11 | Exit signage was not adequately illuminated in line with Bangladesh national building code. Located on the Second floor finishing section. | Provide illuminated signage above all egress exit door points. | Done | Mar 27 2016 | On 02/04/2019: Corrected. On 11-03-2020: Corrected. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Corrected. On 10/05/2023: Corrected. On 26-Dec-24: Corrected | Within 3 months | Corrected
Initial Inspection |  | 12 | Inspection, testing, and maintenance records for the emergency lighting system were not available. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | We have the report maintaining accordingly as per ACCORD standard. | Apr 20 2016 | On 16-10-2018: Corrected. On 02/04/2019: Corrected. On 11-03-2020: Corrected. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Corrected. On 10/05/2023: Corrected. On 26-Dec-24: Corrected | Within 3 months | Corrected
Follow Up Inspection |  | 13 | New finding: The existing factory building with an occupiable floor greater than 10 m (33 ft) above the finished grade is not protected with an approved standpipe system. | Provide a standpipe system throughout the building in accordance with NFPA 14. | All the documents has updated & submitted to RSC. Now, Full system is functional & ready for testing. Waiting for RSC next verification. | Jun 10 2016 | On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: See the Pre T&C report. On 27/06/2022: SUPS is ready for full T&C on date 21-Oct-2021. On 07/12/2022: The T&C of standpipe system has been conducted on dated 07 Dec 2022. The System is not approved. See the details in T&C VI report. On 10/05/2023: The Pre T&C has been conducted on dated 10 May 2023. The standpipe System is not ready for Full T&C VI. See the details Pre T&C VI report. On 14-Oct-2024: Pre-T&CVI has conducted & found that SUPS(standpipe system) is ready for full T&CVI. See the details Pre-T&CVI report. On 26-Dec-24: T&CVI was conducted & it was found that another T&CVI is required. Please see the details in the T&CVI report. RPO Comments on 12-Jan-2026: The T&CVI documents are reviewed & accepted. The factory is now ready for T&CVI. The systems will be checked in the next inspection. | Within Design: 1 month & Installation: 3 months | Pending Verification
Follow Up Inspection |  | 14 | New finding: Stair case was construction by combustible material. | Remove the old one and rebuild the stair case by incumbustable material. | Corrected | Mar 27 2016 | On 11-03-2020: Corrected. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Corrected. On 10/05/2023: Corrected. On 26-Dec-24: Corrected | Within 1 months | Corrected
Follow Up Inspection |  | 15 | New Finding: The north exterior exit stair is not properly separated from the building. | Exterior exit stairs shall be separated from the building with a rating requirement of 1 hr. fire rating for 3 or fewer stories or 2 hr. fire rating for 4 or more stories. The rating of the exterior wall shall extend 3.05 m (10ft) beyond the ends of the stair structure. | corrected | Mar 27 2016 | On 02/04/2019: Corrected as per previous follow-up. Issue is merged with issue no: 3. On 11-03-2020: Corrected as per previous follow-up. Issue is merged with issue no: 3. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected as per previous follow-up. Issue is merged with issue no: 3. On 27/06/2022: Corrected as per previous follow-up. Issue is merged with issue no: 3. On 07/12/2022: Corrected as per previous follow-up. Issue is merged with issue no: 3. On 10/05/2023: Corrected as per previous follow-up. Issue is merged with issue no: 3. On 26-Dec-24: Corrected | Within 1 month | Corrected
Follow Up Inspection |  | 16 | New Finding (3rd Follow Up): Storage was located in the egress path. | Keep egress paths and stairs clear of storage. | corrected | Mar 31 2016 | On 02/04/2019: Corrected. On 11-03-2020: Corrected. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Combustible storage was found at stair case. On 10/05/2023: Combustible storage was found beside & under the stair case. On 26-Dec-24: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 17 | New Finding (3rd Follow Up): Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | corrected | Apr 27 2016 | On 16-10-2018: Corrected. On 02/04/2019: Corrected. On 11-03-2020: Corrected. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Issue re-open. Inadequate emergency lights were observed at all floors. On 10/05/2023: During the inspection some emergency light have been found burn out, some missing & in some area inadequate illumination. On 26-Dec-24: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 18 | New Finding (4th follow-up): Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10 | Inspect, test and maintain the portable fire extinguishers and keep written records onsite,in accordance with NFPA 10. | corrected | Jul 20 2016 | On 02/04/2019: Corrected. On 11-03-2020: Corrected. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Corrected. On 10/05/2023: Corrected. On 26-Dec-24: Corrected | Within 1 month | Corrected
Follow Up Inspection |  | 19 | New Finding (4th follow-up): Penetrations through floor/ceiling assemblies are found unsealed. | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. | The work has corrected. | Jul 20 2016 | On 16-10-2018: In progress. gypsum board has been installed but installation shall be matched with Documentation. . On 02/04/2019: Corrected. Sealed. On 11-03-2020: Corrected. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Corrected. On 10/05/2023: Corrected. On 26-Dec-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 20 | New Finding (8th Follow Up): The elevator discharges inside the production floor. | Provide a minimum 2-hr fire rated construction to separate the elevator shaft from each floor level. Seal all penetrations and openings in floors/ceiling assemblies to maintain the fire separation. | Corrected, Waiting for ACCORD verification Note: Elevator front of all fire doors are again reinstall and now, the gap in between finished floor to fire door not more than 18mm | Jul 14 2017 | On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Fire door installation had been done but interfacing with FACP didn't complete. (RCH) 19-Jul-2021: Time extension till 31 Aug 21 are not accepted. Remediation work must be completed as per approved timeline. (RCH) 12-Oct-2021: Time extension till 15 Nov 21 are not accepted. Remediation work must be completed as per approved timeline. On 27/06/2022: Magnetic door holder of fire door installation done. But door interfacing remaining with FACP. On 07/12/2022: The Fire door have been interfaced with FACP. The gap between finished floor and fire door shall be not more than 19 mm. (RCH) 04-Jan-2022: Time extension till 15 Mar 2023 are not accepted. Remediation work must be completed as per approved timeline On 10/05/2023: Corrected. During the inspection it has been found that the factory provided fire door to separate the elevator with production area. The fire door has been found properly interfaced with FACP. On 26-Dec-24: Corrected. Fire doors were properly interfaced with the FACP. | Within 2 months | Corrected
Follow Up Inspection |  | 21 | New Finding in 9th: Aisles were obstructed by process goods & finished cartons at several floors. | Aisles shall always be free of any kind of storages and obstructions. | corrected | Mar 4 2018 | On 02/04/2019: Corrected. On 11-03-2020: Corrected. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Issue re-open. Aisles was found block at 3rd floor. On 10/05/2023: Within the factory building, maximum aisles have been found clear from obstruction except a DB board found on a single aisles where the aisles need to rearrange. On 26-Dec-24: Corrected. | Within 3 days | Corrected
Follow Up Inspection |  | 22 | New Finding (10th FUI): Compressor Room is not separated from other occupancies. | Compressor room shall be separated from other occupancies by 2hr Fire rated construction. | Corrected, Waiting for ACCORD verification | Nov 17 2018 | On 11-03-2020: Corrected based on lead engineer mail confirmation. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Corrected. On 10/05/2023: Corrected. On 26-Dec-24: Corrected | Within 1month | Corrected
Follow Up Inspection |  | 23 | New Finding (11th Follow Up): Building did not have stair designation signs or occupant load signs at the required locations. | Provide stair designation signs and occupant load signs at the required locations. | Corrected, Waiting for ACCORD verification | May 2 2019 | On 02/04/2019: New Finding On 11-03-2020: Corrected. On 09/12/2020 (Special Escalation Inspection): Not checked during special inspection. On 28/06/2021: Corrected. On 27/06/2022: Corrected. On 07/12/2022: Corrected. On 10/05/2023: Corrected. On 26-Dec-24: Corrected | Within 1 month | Corrected
Follow Up Inspection |  | 24 | New Finding (16th Follow Up): Handrails are not provided on both sides of the stair. | Provide both side handrail in all stair | corrected | Jun 10 2023 | On 10/05/2023: New Finding On 26-Dec-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 25 | New Finding (17th FUI): Parapet height was less than 42 inches (39 inches available). | All occupiable roofs shall be provided with parapets or guards with a minimum height of 1067 mm (42 in.). | The issue is underconcern with building owner. Since the issue is financioanl matter. Still waitting to clossing the pending for work permission. | Jan 31 2025 | On 26-Dec-24: New Finding RPO Comments on 14-May-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the recommendation given with immediate concern. | Within 1 month | In Progress

## Electrical
Date
19-Jun-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Basic Apparels Ltd., 135-138, Abdullahpur (1st & 2nd floor), Uttara, Dhaka, Dhaka
Date of Inspection |  | 2014-04-15
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Service cables (HT) are not supported. | Service cables shall be supported on trays or raisers throughout its length. HT cable shall be protected in steel pipe of required size from the ground level to protect from physical damage. | Corrected | Dec 31 2014 | On 15/12/2015: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 2 | Cables terminating to generator output terminal box are laid on floor. | Cable Generator outgoing cable shall be supported on trays. Existing cables laid on floor may be installed in cable trench or on trays with cover. | Corrected | Dec 15 2014 | On 15/12/2015: Corrected. | Dec 15 2014 | Corrected
Initial Inspection |  | 3 | Silica gel in transformer breather, discolored. | Silica gel in transformer-breather shall be checked during routine inspection and replaced if required. If the color of the silica gel is blue, then it’s dry. The oil container attached below breather shall be filled with transformer oil to trap moisture in air. | Corrected | Dec 1 2015 | On 15/12/2015: Corrected. | Within 1 Month | Corrected
Initial Inspection |  | 4 | Cables terminating at panel, not supported. | Cables shall be protected from external damages and shall be laid/ supported on cable trays. It is recommended to lay cable in covered trenches, under floor level or covered cable-ducts installed on floor. | Corrected | Jan 31 2016 | On 27/03/2016: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 5 | Oil cup below transformer breather is empty. | Breather oil cup shall be filled with transformer oil to required level as instructed by the manufacturer. | Corrected | Dec 15 2014 | On 15/12/2015: Corrected. | Dec 15 2014 | Corrected
Initial Inspection |  | 6 | Cables/wires passing through wall not protected and remaining gaps around the cable/wiring not sealed. | Cables/wirings passing through permanent wall shall be protected and remaining gaps shall be sealed with appropriate fire resistant materials. | Corrected | Apr 30 2016 | On 27/03/2016: Not Corrected. New timeline to close this issue is 30th April, 2016. On 20/06/2016: Not Corrected. On 27/09/2016: Still not corrected. On 04/12/2016: Corrected. | Within 1 Month | Corrected
Initial Inspection |  | 7 | Excess cable length not arranged and supported. | Cables laid outside building shall be supported in covered cable trays and protected against weather and possible physical damages. | Corrected | Dec 31 2014 | On 15/12/2015: Corrected. | Within 6 Months | Corrected
Initial Inspection |  | 8 | Cables or wiring drawn in flexible PVC conduits, laid outside (building walls) without support. | Cables laid outside building shall be supported in covered cable trays and protected against weather and possible physical damages. | Corrected | Dec 31 2014 | On 15/12/2015: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 9 | Cables partially supported in tray and raceways (cables are not placed inside tray in few sections). | Cables tray or raceway shall be continuous & supported rigidly through-out its length. | Corrected | Jan 31 2016 | On 27/03/2016: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 10 | Cable on the walkway. | Cable laid on the walkway shall have mechanical protection. Cable shall be laid in trench with cover or in concrete slab. | Corrected | Dec 31 2014 | On 15/12/2015: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 11 | Cables terminating to generator output terminal not supported. | Cable trays shall be installed with complete accessories to prevent damages and stress to the cables. | Corrected | Dec 31 2014 | On 15/12/2015: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 12 | Storage in generator room. | Materials and wastage stored in generator room shall be removed. | Corrected | Dec 15 2014 | On 15/12/2015: Corrected. | Dec 15 2014 | Corrected
Initial Inspection |  | 13 | Inadequate working space around panels. | Some of the panels shall be relocated, to other location, to provide adequate and safe working space for ease of its operation. | Corrected | Dec 15 2014 | On 15/12/2015: Corrected. | Dec 15 2014 | Corrected
Initial Inspection |  | 14 | Panel doors not connected with earth bond. | Provide earth connection for body and doors of metallic distribution boards using green cables preferably braid so that the metallic door remains at zero potential all the time. | Corrected | Dec 15 2014 | On 15/12/2015: Corrected.. On 20/06/2016: The Factory didn't maintained it. Still door earthlings' are missing. On 27/09/2016: Corrected. | Dec 15 2014 | Corrected
Initial Inspection |  | 15 | Cables or wiring drawn in flexible PVC conduits, laid outside (building walls) without support. | Cables laid outside building shall be supported in cable trays with cover and protected against weather and possible physical damages. | Corrected | Dec 31 2014 | On 15/12/2015: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 16 | Burning sign visible at terminal(s) inside panel. | Arrange periodic inspection & thermal scan to identify the overloading, loose connection, unbalanced load which may cause the excessive heat-rise and take action accordingly. | Corrected | Sep 9 2014 | On 15/12/2015: Corrected. | Within 3 Months | Corrected
Initial Inspection |  | 17 | Panel base plates removed to allow cable entry. | Make circular hole at the base plate/top plate of panels and provide cable gland according to the respective cable size for cable entry and exit so that the cables are not stressed on the sharp edges of the hole of panels. Provide covers (of noncombustible material) if any additional gap remains after installing cable glands. | Corrected | May 31 2016 | On 27/03/2016: Not Corrected. New committed timeline has been given till 31st May,2016. On 20/06/2016: Not Corrected. On 27/09/2016: Corrected. | Within 2 Months | Corrected
Initial Inspection |  | 18 | Excessive lint deposit in cable duct | Provide cover made of noncombustible material on the channel for preventing ingress of dust and debris in future. Disconnect the power source of the cable laid into channel and clean dust and debris of all interior components. Establish a periodic cleaning program and maintain records of the activities. | Corrected | Apr 30 2016 | On 27/03/2016: Cable duct is left Open. New timeline to close this issue is 30th April, 2016. On 20/06/2016: Not Corrected. On 27/09/2016: Corrected. | Within 1 Month | Corrected
Initial Inspection |  | 19 | Multiple cables connected at a terminal of the bus bar/MCB. | Rearrange the devices inside panel such that it can be easily accessible during operation and maintenance. Install slotted wiring duct to latch the cable kept haphazardly inside the panel. | Corrected | Apr 30 2016 | On 27/03/2016: Not Corrected. New timeline to close this issue is 30th April, 2016. On 20/06/2016: Corrected. | Within 1 Month | Corrected
Initial Inspection |  | 20 | Spacing around the MCCBs narrow and crowded inside panel. | Rearrange the devices inside panel such that it can be easily accessible during operation and maintenance. Install slotted wiring duct to latch the cable kept haphazardly inside the panel. | Corrected | Dec 31 2014 | On 15/12/2015: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 21 | Cables partially supported in tray and raceways (cables are not placed inside tray in few sections). | Cable shall be supported on cable trays on floors and ceilings and on raisers/ladders on walls to prevent any physical damage to cable-insulation. | Corrected | Jan 31 2016 | On 27/03/2016: Corrected. | Dec 15 2014 | Corrected
Follow Up Inspection |  | 22 | New Finding: Low oil level is traced in transformer. | Transformer oil shall be filled to the required level. | Corrected | Mar 30 2015 | On 15/12/2015: Corrected. | Dec 15 2014 | Corrected
Follow Up Inspection |  | 23 | New Finding: Arcing horn has not installed. | Install transformer arcing horn with proper alignment. | Corrected | Jan 31 2016 | On 27/03/2016: Corrected. | Dec 15 2014 | Corrected
Follow Up Inspection |  | 24 | New Finding: Buchholz relay is not connected with the protection system. | Connect the Buchholz relay with the protection system. | Corrected | Mar 30 2015 | On 15/12/2015: Corrected. | Dec 15 2014 | Corrected
Follow Up Inspection |  | 25 | New Finding: Generator frame is not earthed by 2 separate and distinct earth. | Generator shall be connected to earth securely at least two points. | Corrected | Apr 30 2016 | On 27/03/2016: Earthing has been done using undersized cable. New timeline to close this issue is 30th april,2016. On 20/06/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 26 | New Finding: Battery terminals are left open. | Use insulated rubber cap to cover all the battery terminals. | Corrected | Apr 30 2016 | On 27/03/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding: Generator output supply terminal box open. | Cable terminating at the generator box shall be fixed bottom plate with cable gland. | Corrected | Mar 30 2015 | On 15/12/2015: Corrected. | Dec 31 2014 | Corrected
Follow Up Inspection |  | 28 | New Finding: Lint and dust deposited inside MDB/SDB. | Keep always clean inside MDB/SDB. | Corrected | May 31 2016 | On 27/03/2016: Not Corrected. New timeline to close this issue is 31st May, 2016. On 20/06/2016: Not Corrected. On 27/09/2016:Corrected.Need to clean periodically. | Within 2 Months | Corrected
Follow Up Inspection |  | 29 | New Finding: Cables terminated at electrical bus bar/MCCB without cable lugs. | Terminate all the power/earth/neutral cable with proper sized cable lug. | Corrected | Mar 30 2015 | On 15/12/2015: Corrected.. On 20/06/2016: The Factory didn't maintained it. Still cables are terminated without lug.. On 27/09/2016: Still not corrected. On 04/12/2016: Corrected. | Dec 15 2014 | Corrected
Follow Up Inspection |  | 30 | New Finding: Electrical devices installed on combustible material. | Need to use non-combustible enclosure. | Corrected | Mar 30 2015 | On 15/12/2015: Corrected. | Dec 15 2014 | Corrected
Follow Up Inspection |  | 31 | New Finding: Barrier/ separators between different phases are not installed. | Install separators between different phases of MCCB. Standard separators provided by the MCCB manufacturer shall be used. | Corrected | Mar 30 2015 | On 15/12/2015: Corrected.. On 20/06/2016: Not Corrected. On 27/09/2016: Corrected. | Dec 15 2014 | Corrected
Follow Up Inspection |  | 32 | New Finding: Loop connections have been used for powering multiple MCBs/MCCBs. | Eliminate loop cables; use single cable for each MCBs/MCCBs. You may use bus bar to avoid multiple termination. | Corrected | Mar 30 2015 | On 15/12/2015: Corrected. | Dec 15 2014 | Corrected
Follow Up Inspection |  | 33 | New Finding: Combustible material attached with the panel. | Remove combustible materials from the panel immediately. | Corrected | Mar 30 2015 | On 15/12/2015: Corrected. | Dec 15 2014 | Corrected
Follow Up Inspection |  | 34 | New Finding: Combustible material is using as cover for cable trench. | Use non-combustible material as cover for cable trench. | Corrected | Mar 30 2015 | On 15/12/2015: Corrected. | Dec 15 2014 | Corrected
Follow Up Inspection |  | 35 | New Finding: Cable tray and steam line close to each other. | Cables and all electrical installations near steam line shall be protected from external heat from stream pipes. | Corrected | Jan 31 2016 | On 27/03/2016: Corrected. | Dec 31 2014 | Corrected
Follow Up Inspection |  | 36 | New Finding: Electrical Single Line Diagram (SLD) is not available. | Draw as built electrical SLD by qualified engineer and review it by Accord. |  | Apr 30 2016 | On 04/12/2016: Not Corrected. On 13/02/2017: Not corrected. SLD need to submit for further review. On 14/05/2017: Not corrected. On 01/03/2018: Not Corrected. On 16/10/2018: Not corrected. SLD needs modification. On 02/04/2019: Not corrected. SLD needs modification. On 28/06/2021: SLD is under review. On 27/04/2022: Not Corrected. SLD accepted on 2nd Nov 2021. Information has mismatched between accepted SLD and field. Identification for cables, breakers, and equipment are not started yet. On 07/12/2022: Significant progress is not observed. On 11/01/2024: Not Corrected. The factory has prepared an updated SLD. Cable identification has been done but mismatch with SLD observed at few panels. Oversized circuit breaker has been observed in panels. RPO Comments: On 02-Jun-2024 the design documents (SLD) have been accepted by the RSC on 30-MAY-2024. The remediation needs to be completed based on accepted design. On 02/10/2024: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Cable insulation resistance test record is absent. | Record insulation resistance for main power cables up to Distribution/Sub distribution board. | Corrected | Apr 30 2016 | On 27/03/2016: Not Corrected. New timeline to close this issue is 30th April, 2016. On 20/06/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | Hang this instruction near all electrical equipment (LT panel, MDB, FDB, DB, SDB) on a visible location. | Corrected | Jan 31 2016 | On 27/03/2016: Corrected. | Feb 28 2015 | Corrected
Follow Up Inspection |  | 39 | New Finding: Thermo graphic scanning of the entire electrical system has not been tested and recorded. | Thermo graphic scanning of the entire electrical system shall be performed on a bi-annual basis and recorded. | Corrected | Feb 28 2016 | On 27/03/2016: Corrected. | Feb 28 2015 | Corrected
Follow Up Inspection |  | 40 | New Finding: Transformer Oil Test report is absent. | Check the transformer oil condition by performing oil test once per year and keep the record in a report form. | Corrected | Mar 30 2015 | On 15/12/2015: Corrected. | Feb 28 2015 | Corrected
Follow Up Inspection |  | 41 | New Finding: Earth Pit resistance record is absent. | Record earth pit resistance for all the earth pit and do once in a year. | Corrected | Feb 28 2016 | On 27/03/2016: Corrected. | Feb 28 2015 | Corrected
Follow Up Inspection |  | 42 | New Finding: Maintenance record is not available. | Maintenance in charge/Safety officer should check the record with housekeeping. | Corrected | Mar 30 2015 | On 15/12/2015: Corrected. | Feb 28 2015 | Corrected
Follow Up Inspection |  | 43 | New Finding: Absence of Lightning Protection System(LPS). | Design and Install LPS for your factory; Factory have to submit LPS design to Accord before starting installation. | LPS Installation work has completed according on last follow-up observations. And design & drawing updated. Waiting for RSC verification | May 31 2016 | On 14/05/2017: Not corrected. On 01/03/2018: Not Corrected. Class II material is required for the shed, as it crosses 75 feet. On 16/10/2018: Not corrected. Misplaced AT and main conductor missing. At several places down conductor is not shown in the drawing. The water tank needs coverage. Do adequate metal bonding. For utility portion calculate risk index and install LPS accordingly or show the zone of protection. On 02/04/2019: Not corrected. On 28/06/2021: Need to install class II material where height crosses 75 feet. Conductor connection shall be of the bolted, welded, high compression, or crimp type. Crimp connection shall not be used with a class II conductor. Make sure all pits are accessible to measure the electrode diameter. On 27/04/2022: Not Corrected. Installation is done at the main building but the substation room is not under the protection zone of LPS or the protection zone calculation required. On 07/12/2022: The required number of Class-II down conductors is not installed. Mention the total perimeter and down conductor for class II in the drawing. On 11/01/2024: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 44 | New Finding: Personal Protective Equipment (PPE) for Electrical Work is not available. | Personal Protective Equipment (PPE) shall be arranged by the factory management team for the safety of their employee and worker. | Corrected | Apr 30 2016 | On 27/03/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Excess cables kept at the back of panel. | Rearrange cables using cable tray/ladder; or trim the unnecessary cables and use only the required length (If it is HT cable, do not trim it rather rearranging it). | Corrected | Feb 25 2016 | On 27/03/2016: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 46 | New Finding: Wiring has done using flexible PVC cable around vertical boiler surface. | Wires close/attached to boiler shall be protected from external heat. In unavoidable case use metal type flexible pipe. Again Power cable should keep 0.9m apart from hot area. | Corrected | Jan 25 2016 | On 27/03/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Earth connections are not segregated. Earth pits are not identifiable. | Ensure separate earthing connection for all neutrals Generator body, transformer body, Electrical system and Lightning Protection System. Mark them all. | Corrected | May 31 2016 | On 20/06/2016: Not Corrected. On 27/09/2016: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 48 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly. | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. |  | May 31 2016 | On 20/06/2016: Not Corrected. On 27/09/2016: Still not corrected. On 04/12/2016: Not Corrected. On 13/02/2017: Not corrected. On 14/05/2017: Not corrected. On 01/03/2018: Not corrected. On 16/10/2018: Not corrected On 02/04/2019: Not corrected. On 28/06/2021: The issue is not found in a few panel boards. On 27/04/2022: Not Corrected. Still found in a few panel boards. On 07/12/2022: Circuit breakers are not selected considering the equipment kw rating. On 11/01/2024: Not Corrected. Significant amount of oversized circuit breaker has been observed on several floors. On 02/10/2024: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 49 | New Finding: Earth Continuity Conductor (ECC) is undersized/improper. | Increase ECC size for whole factory according to BNBC 2006 Part 8 Chapter 2 section 2.8 (Usually ECC should be equal to the half of the respective phase cable). | Done | May 31 2016 | On 20/06/2016: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 50 | New Finding: Neutral Cable is inadequate. | Neutral Cable should be same as phase cable. | Done | Apr 30 2016 | On 20/06/2016: Not Corrected. On 27/09/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Oil/water spillage in generator room. | Stop oil leaking from generator and keep the floor dry. | Done | Jul 31 2016 | On 27/09/2016: Corrected. No such issue was found. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Hot spots at terminations inside panel. | Identify the overloading, loose connection, unbalanced load which may cause the excessive heat-rise and take action accordingly. However, immediately correct such points. | Some points we founded lose connection, so coming Hot spot. Instantly our Electrical Expert solve the Issue. Now this is corrected. | Oct 15 2016 | On 27/09/2016: Not corrected. Committed Timeline: Within 15/10/2016. On 04/12/2016: Not Corrected. On 13/02/2017: Not corrected. The periodicity of Thermography survey is not continued. On 14/05/2017: Corrected | Immediate | Corrected
Follow Up Inspection |  | 53 | New Finding: Lint and dust is deposited inside MDB/SDB. | Ensure regular maintained to keep the panel board clean. | Corrected | Jan 11 2017 | On 13/02/2017: Not corrected. On 14/05/2017: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: Lead acid battery terminals are left open. | Lead acid battery terminals shall be covered/capped and rust shall be checked and cleaned. | Corrected the issue. | Jan 11 2017 | On 13/02/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding: Earth pits are not identifiable. | Each earth pit shall be properly identifiable and marked for periodic maintenance. | The Issue is corrected | Jan 11 2017 | On 13/02/2017: Not corrected. On 14/05/2017: Not corrected. On 01/03/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 56 | New Finding: Power sockets are not installed by any permanent means. | Every electrical installation shall be installed rigidly. | Corrected | Jan 11 2017 | On 13/02/2017: Not corrected. Combustible materials used for electrical installation/element. On 14/05/2017: Not corrected. On 01/03/2018: Not corrected. On 16/10/2018: Corrected. Not found this time. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: Uninsulated electrical tools are used by maintenance personnel in the factory. | For maintenance purposes, all the electrical tools shall be properly insulated and these insulations shall be checked periodically. | The Issue is corrected | Jan 18 2017 | On 13/02/2017: Not corrected. On 14/05/2017: Not corrected. On 01/03/2018: Corrected. | 6 weeks | Corrected
Follow Up Inspection |  | 58 | New Finding: (i) Insulation resistance test record (cable information) doesn't match with field. (ii) Earth Pit resistance test record doesn't match with field. | (i) Field information shall be reflected in the record and significantly lower sized cables' record shall be avoided. (ii) Adequate number of earth pits shall be ensured (if it's lower in numbers) and record shall be made accordingly. | Corrected | Apr 20 2017 | On 14/05/2017: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 59 | New Finding: Hazardous lights in store room / storage areas are uncovered. | Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. | The Issue is corrected | Jun 30 2017 | On 14/05/2017: Not corrected. Time extension is given till 30/06/2017. On 01/03/2018: Corrected. Non-hazardous lights (LED) has been installed. | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: Earth connections for different electrical installation are not segregated. | All the earth connections (transformer, generator and electrical systems) shall be segregated and clearly marked (for TT earthing system). | Basic has partially done the job, but substation room earth pit are not Identity market and segration. We had discuss with Land owner to complete the job. They will take action immediately. | Jun 30 2017 | On 14/05/2017: Not corrected. Time extension is given till 30/06/2017. On 01/03/2018: Not corrected. On updated CAP for the month of April 2018 factory asked time extension to complete the remediation work till 20 May 2018 but time extension are not accepted. On 16/10/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Panel base plates are removed to allow cable entry. | Panel base plates shall be installed, at all time, and cables entering panel shall be firmly fixed with cable gland. | The Issue is corrected | Jun 30 2017 | On 14/05/2017: Not corrected. Time extension is given till 30/06/2017. On 01/03/2018: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 62 | New Finding: (i) Circuit is drawn from bus bar without any protective means. (ii) Rewireable fuse (cutout fuse) used for circuit protection. (iii) Indicator lights are mounted without disconnecting device. | (i) Each electrical circuit shall be drawn from distribution board busbar using a proper type protection arrangement (MCCB/MCB). (ii) Re-wire able fuse shall not be used; MCB/MCCB shall be used for protection. (iii) Indicator lights should be connected by control device such as rated fuse or MCB. | Work has done. Corrected | Jun 30 2017 | On 14/05/2017: Not corrected. Time extension is given till 30/06/2017. On 01/03/2018: Not Corrected. On updated CAP for the month of April 2018 factory asked time extension to complete the remediation work till 30 June 2018 but time extension are not accepted. On 16/10/2018: Not corrected. On 02/04/2019: Corrected. | 2 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: (i) Loop connection has been used powering multiple circuits through MCB/MCCBs. (ii) Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ Busbar. | (i) No loop connection shall be used; each single cable shall be terminated using cable lug (flat/I) at each terminal. Combo bus bar may be used (but incoming cable size shall meet the rated capacity) (ii) Each electrical circuit shall be terminated at single MCB/MCCB terminals. | Corrected | Mar 20 2017 | On 14/05/2017: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 64 | New Finding: Panel doors are not connected with earth. | All metal installation which are part of electrical system shall be connected to earth to avoid electrical shock or electrocution. | Corrected | Jun 30 2017 | On 14/05/2017: Not corrected. Time extension is given till 30/06/2017. On 01/03/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 65 | New Finding: No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) shall be ensured. | Corrected | Jun 30 2017 | On 14/05/2017: Not corrected. Time extension is given till 30/06/2017. On 01/03/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 66 | New Finding: (i) Panel/Distribution boxes are inaccessible or cannot be opened to perform any maintenance work. (ii) Maintenance movement is obstacle due to improper cable trench cover in the utility area (Generator/Substation/Boiler/Compressor). | (i) Each electrical distribution board/panel shall be easily accessible. In case of height its top shall not be higher than 2m from base; and door opening shall be at least 90 degree. (ii) Covered cable trench shall be equal to working floor height. If not, extended area shall be sloped at both sides to avoid obstacle. | Corrected | Jun 30 2017 | On 14/05/2017: Not corrected. Time extension is given till 30/06/2017. On 01/03/2018: Corrected. Panel has been shifted to another place. | 2 Months | Corrected
Follow Up Inspection |  | 67 | New Finding: (i) Cables are hanged outside wall of the building without proper support and protection. (ii) Cables passing through wall/floor slab are not protected at the entry/exit point(s). | (i) Service/distribution cables shall not be hanged on wall; it shall be distributed through a cable duct (covered cable ladder). Cable tray or ladder can also be used (if there is no chance of seasonal effect) (ii) Cables passing through permanent wall/floor slab shall be protected. Floor to floor openings shall be sealed by proper type materials (consult with fire expert). |  | Jun 30 2017 | On 14/05/2017: Not corrected. Time extension is given till 30/06/2017. On 01/03/2018: Not Corrected. On updated CAP for the month of April 2018 factory asked time extension to complete the remediation work till 31 May 2018 but time extension are not accepted. On 16/10/2018: Not corrected. On 02/04/2019: Not corrected. On 28/06/2021: This issue is found in two places. On 27/04/2022: Not Corrected. Still found this issue few areas. On 07/12/2022: Cables are not protected at the wall penetration point of the wall. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 68 | New Finding: Inadequate working clearance around the generator/s. | Working clearance around each generator should be 1.07m. If multiple generators are installed then the gap between two generators shall be equal to the width of bigger generator. | Corrected | Jun 30 2017 | On 14/05/2017: Not corrected. Time extension is given till 30/06/2017. On 01/03/2018: Not corrected. On updated CAP for the month of April 2018 factory asked time extension to complete the remediation work till 30 June 2018 but time extension are not accepted. Remediation work shall be completed as per Accord approved timeline. On 16/10/2018: Not corrected. On 02/04/2019: Not corrected. On 28/06/2021: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 69 | New Finding: Hot spots at terminations inside panel. | Identify the overloading, loose connection, unbalanced load which may cause the excessive heat-rise and take action accordingly. However, immediately correct such points. | Done | Mar 7 2018 | On 16/10/2018: Not corrected. Troubleshooting and remediation of the hotspot are needed. On 02/04/2019: Not corrected. On 28/06/2021: Hot spots are found in a few panel boards. On 27/04/2022: Not Corrected. Still found several areas. On 07/12/2022: This issue is corrected based on the evidence sent by the factory after the audit. | 1 week | Corrected
Follow Up Inspection |  | 70 | New Finding: Safety program is initiated but has no influence in the factory. | Electrical safety training and awareness program for the electrical personal and workers shall be conducted and recorded. Training shall have an impact on the safety attitude of the personnel. Arrange adequate PPE for maintenance personnel. | Work has done. Corrected. Waiting for RSC verification Note that: we are regularly maintaining and make sure by monthly awareness training also checking feedback assessment by Compliance team. | Nov 30 2018 | On 02/04/2019: Not corrected. No impact on the safety attitude of the personnel. On 28/06/2021: Safety training has initiated but has less influence on attitude. On 27/04/2022: Not Corrected. On 07/12/2022: No initiative is taken yet to introduce the safety training program to the electrician. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 71 | New Finding: Boiler room has poor/inadequate ventilation. | Boiler room shall be well ventilated (cross ventilation). | Corrected | Dec 30 2018 | On 02/04/2019: Not corrected. On 28/06/2021: Corrected. | 2 Month | Corrected
Follow Up Inspection |  | 72 | New Finding: Lead acid battery terminals are left open. | Lead acid battery terminals shall be covered/capped and rust shall be checked and cleaned. | Corrected | Nov 30 2018 | On 02/04/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 73 | New Finding: Electrical distribution box/panels are full of fluffs (lint/dirt). | Each electrical distribution board/panel shall be properly sealed to avoid ingression of fluffs; but an adequate ventilation system shall also be ensured. | Corrected | Nov 30 2018 | On 02/04/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 74 | New Finding: Panel/Distribution boxes are inaccessible or cannot be opened to perform any maintenance work. | Each electrical distribution board/panel shall be easily accessible. In case of height its top shall not be higher than 2m from base; and door opening shall be at least 90 degree. | Work has done. Corrected. Waiting for RSC verification | May 3 2019 | On 28/06/2021: This issue exists in one place. On 27/04/2022: Not Corrected. On 07/12/2022: No action has been taken after the last follow-up inspection. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 75 | New Finding: Distribution Board's top/bottom is left open (typical issue). Generator output terminal box's bottom plate removed to allow cable entry. | Each electrical distribution board/panel shall be properly sealed to avoid ingression of fluffs; but an adequate ventilation system shall also be ensured. Gland shall be used, where required. Seal bottom of the terminal box and use cable glands for holding/supporting cables. | Work has done. Corrected. Waiting for RSC verification | Aug 10 2021 | On 27/04/2022: Not Corrected. On 07/12/2022: One generator output terminal box is not sealed. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 76 | New Finding: Phase barrier/separators are missing in MCCBs. | Phases shall be separated by insulator (a rubber type no-flammable materials shall be used for it). | Work has done. Corrected. Waiting for RSC verification | Aug 10 2021 | On 27/04/2022: Not Corrected. On 07/12/2022: Phase separator is yet to provide at the few circuit breaker terminals. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 77 | New Finding: Conductor size less than size 1/0 AWG is connected in parallel to meet the ampacity of the load. | The parallel conductors in each phase used to meet the ampacity shall have same length, the same size in circular mil area, same insulation type, and same conductor material and shall be terminated in the same manner. (Aluminum, copper-clad aluminum, or copper conductors of size 1/0 AWG and larger, comprising each phase, polarity, neutral, or grounded circuit conductor shall be permitted to be connected in parallel (electrically joined at both ends).) | Work has done. Corrected. Waiting for RSC verification | Aug 10 2021 | On 27/04/2022: Not Corrected. On 07/12/2022: This issue has been found within a panel board only. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 78 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels/ducts shall be kept neat and clean. The channels/ducts shall be sealed properly thus no scope of ingress of fluffs. | Corrected. Waiting for RSC verification | Aug 10 2021 | On 27/04/2022: Not Corrected. On 07/12/2022: No progress is observed after the last follow-up inspection. On 11/01/2024: Not Corrected. Significant progress observed. Channels cover missing at few locations in 1st and 2nd floor. RPO Comments: On 03-Apr-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/10/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 79 | New Finding: No LOTO (Lock-Out-Tag-Out) policy is introduced for the safety of the personnel during any kind of maintenance work. | Need to introduce and implement LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure the safety of the personnel during any maintenance. Need to keep all user records. |  | Aug 10 2021 | On 27/04/2022: Not Corrected. On 07/12/2022: No LOTO policy is introduced yet. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 80 | New Finding: Transformer Breather oil cup is empty. | Transformer breather oil cup shall be filled not more than 70% of its capacity. | Corrected | Aug 10 2021 | On 27/04/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 81 | New Finding: Electrical distribution box/panels are full of fluffs (lint/dirt). | Each electrical distribution board/panel shall be properly sealed to avoid ingression of fluffs; but an adequate ventilation system shall also be ensured. | Corrected. Waiting for RSC verification | Aug 10 2021 | On 27/04/2022: Not Corrected. On 07/12/2022: No progress is observed after the last follow-up inspection. On 11/01/2024: Not Corrected. Significant progress observed. Dust observed in few consumer boxes. RPO Comments: On 03-Apr-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/10/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 82 | New Finding: Loop connection has been used powering multiple circuits through MCB/MCCBs. | No loop connection shall be used; each single cable shall be terminated using cable lug (flat/I) at each terminal. Combo bus bar may be used (but incoming cable size shall meet the rated capacity). |  | Aug 10 2021 | On 27/04/2022: Not Corrected. On 07/12/2022: This issue still exists in the consumer box. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 83 | New Finding: Outdoor Cable trays are not covered to protect from weather effect. | Outdoor cable tray/ladders shall be covered properly to avoid seasonal effect on cables and its longevity. | Done | Aug 10 2021 | On 27/04/2022: Not Corrected. On 07/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 84 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) shall be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Work has done. Corrected. Waiting for RSC verification | Aug 10 2021 | On 27/04/2022: Not Corrected. On 07/12/2022: No action has been taken. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 85 | New Finding: Cable insulation may damaged by sharp edge of the tray cover. | Install cover on cable tray properly thus no cable may damage by the sharp edge. | Work has done. Corrected. Waiting for RSC verification | Aug 10 2021 | On 27/04/2022: Not Corrected. On 07/12/2022: No action has been taken. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 86 | New Finding: Non-metallic sheathed (Types NM, NMC, and NMS) cables are run and exposed over the suspended ceiling. | Use the metallic sheathed cable or provide enclosed cable raceway to run the cable over the suspended ceiling. Suspended ceiling shall not be used to support non-metallic cable. | Work has done. But note that, the laying cable is optical fiber for using "CC camera and Internet. | Aug 10 2021 | On 27/04/2022: Not Corrected. On 07/12/2022: No action has been taken. On 11/01/2024: Corrected. Wiring has been removed. | 1 Month | Corrected
Follow Up Inspection |  | 87 | New Finding: Hazardous lights in store room / storage areas are uncovered. Exposed wiring by PVC conduit observed in the storage area. | Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. In the storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Corrected. Waiting for RSC verification | Aug 10 2021 | On 27/04/2022: Not Corrected. On 07/12/2022: This issue still exists in a few storage areas. On 11/01/2024: Not Corrected. No Hazardous light observed in store room. But wiring done by PVC. In the storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. RPO Comments: On 03-Apr-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/10/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 88 | New Finding: Unterminated live wire is kept inside the electrical panel/cable tray. Cables in service are joined (splicing) between terminations. | All the unterminated live power cables shall be removed as soon as possible. Splicing in the power cables shall be avoided; in unavoidable cases splicing, shall be made following proper guidance. | Work has done. Corrected. Waiting for RSC verification | Aug 10 2021 | On 27/04/2022: Not Corrected. On 07/12/2022: Proper splicing kits are not used for cable jointing or tapping. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 89 | New Finding: Circuit breaker knob is broken or not operational. | All circuit breaker shall be operational. Replace the faulty circuit breaker with new one. | Work has done. Corrected. Waiting for RSC verification | Aug 10 2021 | On 27/04/2022: Corrected. On 07/12/2022: This issue is found in a panel only. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 90 | New Finding: Distribution boards have no clear identification markings. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. | Done | Aug 10 2021 | On 27/04/2022: Not Corrected. On 07/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 91 | New Finding: Burnt sign visible at (MCCB/MCB/Cable Lug/Bus Bar). | Check the connections and circuit breaker. Find out the exact reason of burning. If required, replace the burned breaker. Assign an engineer to take necessary action depending on the problem. | Done | Jun 7 2022 | On 07/12/2022: No burning sign is observed. | 1 Month | Corrected
Follow Up Inspection |  | 92 | New Finding: Periodicity of thermographic survey is not continued. | Thermography survey shall be conducted on entire electrical system in the facility at least twice in a year. And the remediation suggestions mentioned in the report shall be carried out. | Done | Jun 7 2022 | On 07/12/2022: Corrected based on the evidence sent by the factory after audit. | 1 Month | Corrected
Follow Up Inspection |  | 93 | New Finding: Insulation resistance record (cable information) doesn't match with field. | Field information shall be reflected in the record. Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) shall be performed once in every 2 years’ cycle and recorded (this shall require a complete power shut off). |  | Jun 7 2022 | On 07/12/2022: Insulation resistance test of cables is outdated. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 94 | New Finding: Circuit breaker has no capacity information. | Each Circuit breaker shall have its own capacity information. |  | Jun 7 2022 | On 07/12/2022: Still, a few breakers need to replace. On 11/01/2024: Not Corrected. The issue is observed at few panels on the production floors. RPO Comments: On 02-Jun-2024 the design documents (SLD) have been accepted by the RSC on 30-MAY-2024. The remediation needs to be completed based on accepted design. On 02/10/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 95 | New Finding: Panel doors are not connected with earth. | All metal installation which are part of electrical system shall be connected to earth to avoid electrical shock or electrocution. |  | Jun 7 2022 | On 07/12/2022: This issue still exists in a few panels. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 96 | New Finding: No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) shall be ensured. | Work has done. Corrected. Waiting for RSC verification. Note: Newly provided. | Jun 7 2022 | On 07/12/2022: The insulation mat shall be Class-0 for the distribution board. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 97 | New Finding: Oil spillage/leakage has been observed in generator room. | Any kind of oil spillage/leakage shall be stopped; and generator shall be kept always dry. | Done | Jun 7 2022 | On 07/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 98 | New Finding: Lead acid battery terminals are left open. | Lead acid battery terminals shall be covered/capped and rust shall be cleaned. | Work has done. Corrected. Waiting for RSC verification | Jun 7 2022 | On 07/12/2022: No action has been taken yet. On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 99 | New Finding: Lint and dust deposited on and around the transformer. | Transformer top and around it shall be kept neat and clean. | Done | Jun 7 2022 | On 07/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 100 | New Finding: Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ Busbar. | Each electrical circuit shall be terminated at single MCB/MCCB terminals. |  | Jun 7 2022 | On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 101 | New Finding: Interlocking is not provided for powering a common busbar from different sources. | Interlocking shall be provided for feeding power from multiple sources. |  | Jan 15 2023 | On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 102 | New Finding: Power socket is kept on floor unsafely | Power socket shall be install at minimum 200mm above the floor with a rigid support. | Corrected. Waiting for RSC verification | Jan 15 2023 | On 11/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 103 | New Finding: Field information has no/less reflection in existing SLD. | As-built Electrical Single Line Diagram (SLD) must be prepared by a qualified engineer, including all essential details of the electrical system. All cables, all circuits, all terminals, all equipment are required to be identified as per the accepted Single line diagram. | In Progress | Aug 10 2026 |  | 2 Months | In Progress
Follow Up Inspection |  | 104 | New Finding: Protective device is not installed/adjusted per load demand. | Protective devices must be installed or adjusted according to the connected load current. If adjustment is not feasible, replacement is necessary. Each motor load exceeding 376W requires separate protection, adhering to nameplate data for selecting the appropriate protective device. | In Progress | Aug 10 2026 |  | 2 Months | In Progress
Follow Up Inspection |  | 105 | New Finding: Hot spots have been observed at some points. | Hot spots throughout the entire electrical system must be eliminated to ensure safety and prevent potential equipment failures or hazards and reduce downtime and repair costs. | In Progress | Jul 10 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 106 | New Finding: Circuit breaker has no capacity information. | Each circuit breaker must be clearly labeled with its capacity information. | In Progress | Jul 10 2026 |  | 1 Month | In Progress

## Boiler
Date
19-Jun-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Basic Apparels Ltd., 135-138, Abdullahpur (1st & 2nd floor), Uttara, Dhaka, Dhaka
Date of Inspection |  | 2022-01-30
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 4078 | Boiler's initial registration certificate was not available on-site during the inspection. | Boiler registration certificate from the government authority which was provided after the installation shall be available on-site during the inspection. | Corrected and waitting for next RSC Verification | Oct 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 4079 | Boiler's initial registration certificate was not available on-site during the inspection. | Boiler registration certificate from the government authority which was provided after the installation shall be available on-site during the inspection. | Corrected and waitting for next RSC Verification | Oct 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 4078 | Boiler exhaust gas pipeline inside the boiler room was found with improper insulation. | Proper insulation to boiler exhaust gas pipeline inside the boiler room causing heat exposure for personnel shall be provided. | Corrected and waitting for next RSC Verification | Sep 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 4079 | Boiler exhaust gas pipeline inside the boiler room was found with improper insulation. | Proper insulation to boiler exhaust gas pipeline inside the boiler room causing heat exposure for personnel shall be provided. | Corrected and waitting for next RSC Verification | Sep 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 4078 | Boiler steam pipelines were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | Corrected and waitting for next RSC Verification | Sep 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 4079 | Boiler steam pipelines were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | Corrected and waitting for next RSC Verification | Sep 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 4079 | Necessary technical documents (except operation logbook and electrical wiring diagram) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Work on going. | Nov 30 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 8 | BB 4078 | Direct groundwater was used as feed water for the boiler. | Boiler feed water shall be treated. The feedwater and boiler water quality should meet the manufacturer's specifications. When unavailable, should meet manufacturer's standard or BS EN 12953-10. | Corrected and waitting for next RSC Verification | Oct 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 4079 | Direct groundwater was used as feed water for the boiler. | Boiler feed water shall be treated. The feedwater and boiler water quality should meet the manufacturer's specifications. When unavailable, should meet manufacturer's standard or BS EN 12953-10. | Corrected and waitting for next RSC Verification | Oct 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 4078 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Corrected and waitting for next RSC Verification | Oct 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 3 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 4079 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Corrected and waitting for next RSC Verification | Oct 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 3 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 12 | BB 4078 | Nameplates for feed pump covered with paint and scratches. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | Corrected and waitting for next RSC Verification | Sep 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 13 | BB 4079 | Nameplates for feed pump were covered with paint and scratches. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | Corrected and waitting for next RSC Verification | Sep 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 14 | BB 4078 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | Corrected and waitting for next RSC Verification | Oct 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 15 | BB 4079 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | Corrected and waitting for next RSC Verification | Oct 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 16 | BB 4078 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | Corrected and waitting for next RSC Verification | Sep 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 17 | BB 4079 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | Corrected and waitting for next RSC Verification | Sep 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 18 | BB 4078 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Work on going. | Nov 15 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 19 | BB 4078 | Inadequate ventilation systems were observed in the boiler room. | An adequate ventilation system shall be ensured as per BNBC 2020 for habitability, combustion air, housekeeping, personal safety, and general safety considerations. | Work on going. | Nov 15 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 20 | BB 4078 | The boiler's bottom blowdown line was not safely installed and was posing a scalding hazard. | The blowdown line must be installed safely and directed either into a drain line or outside of the boiler room without creating any scalding hazard. | Work on going. | Nov 30 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 21 | BB 4079 | Valves were observed between the boiler and the only pressure gauge. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. | Corrected and waitting for next RSC Verification | Aug 24 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 22 | BB 4078 | The boiler was found not properly mounted on the base. | The boiler must be properly mounted to the base according to the manufacturer's recommendations. | Corrected and waitting for next RSC Verification | Sep 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 23 | BB 4078 | The control panel cabinet does not specify the names of all boiler interlock alarm functions. | Names of boiler interlock alarm functions should be specified on the cabinet. | Work on going. | Nov 30 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 3 MONTHS | In Progress
Initial Inspection | External visual inspection | 24 | BB 4079 | The control panel cabinet does not specify the names of all boiler interlock alarm functions. | Names of boiler interlock alarm functions should be specified on the cabinet. | Work on going. | Nov 30 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 3 MONTHS | In Progress
Initial Inspection | External visual inspection | 25 | BB 4078 | Foreign system (steam) was installed inside the electrical panel. | Foreign systems (e.g., steam, water, air, gas, drainage) should not be installed inside the electrical panel. | Work on going. | Nov 30 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 WEEKS | In Progress
Initial Inspection | External visual inspection | 26 | BB 4079 | Foreign system (steam) was installed inside the electrical panel. | Foreign systems (e.g., steam, water, air, gas, drainage) should not be installed inside the electrical panel. | Work on going. | Nov 30 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 WEEKS | In Progress
Initial Inspection | External visual inspection | 27 | BB 4078 | There is no drainage available for water level gauge glass | A suitable discharge pipe shall be fitted with each water gauge drain cock or valve | Work on going. | Nov 15 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 28 | BB 4079 | There is no drainage available for water level gauge glass | A suitable discharge pipe shall be fitted with each water gauge drain cock or valve | Work on going. | Nov 15 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 29 | BB 4078 | Boiler renewal certificate was not available. | Factory shall apply to the appropriate authority for renewal certificate and ensure updated renewal certificate is available on site. | Corrected and waitting for next RSC Verification | Oct 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 30 | BB 4079 | Boiler renewal certificate was not available. | Factory shall apply to the appropriate authority for renewal certificate and ensure updated renewal certificate is available on site. | Corrected and waitting for next RSC Verification | Oct 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 31 | BB 4078 | Salt and scale formation was observed on the waterside around the whole fire tube, Hard scale. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | Work on going. | Nov 30 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 32 | BB 4079 | Salt and scale formation was observed on the waterside on fire drum. (Soft Scale) | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | Work on going. | Nov 30 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 33 | BB 4078 | There was no acoustic or optical alarm when the limiter was activated. | An acoustic with optical alarm should be installed. | Work on going. | Nov 15 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 34 | BB 4079 | There was no acoustic or optical alarm when the limiter was activated. | An acoustic with optical alarm should be installed. | Work on going. | Nov 15 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 35 | BB 4078 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | Work on going. | Nov 30 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 36 | BB 4078 | The Air Pressure Limiter was not functional. | Air Pressure Limiter shall be kept functional. | Work on going. | Nov 15 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 37 | BB 4079 | The Air Pressure Limiter was not functional. | Air Pressure Limiter shall be kept functional. | Corrected and waitting for next RSC Verification | Sep 11 2025 | Comments on 02-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 38 | BB 4078 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | Work on going. | Nov 30 2025 | Comments on 02-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 WEEK | In Progress