## Structural
Date
29-Apr-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Chorka Textile Ltd., Kazir Chor Danga Palash Narshingdi, -, Narsingdi, Dhaka
Date of Inspection |  | 2014-05-04
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The telecoms mast at the in front of building 3 to be made safe. | Priority-1: The telecom mast is currently un-restrained. Mast to be restrained/stayed or taken down immediately, stayed system to be engineered prior to placement. | Done. Report had sent earlier. Drawing attached. | Jul 29 2014 | On 21/05/15: The factory has re located and re constructed with proper drawing and designing. On 20/06/16: Found corrected from previous inspection. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: Telecom mast has been relocated, its not connected to any structure system now. On 25-Feb-2018: Mast was relocated which is not connected to any structures. Issue remains corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. Telecom mast has been relocated, its not connected to any structure system now. On 28-Nov-2024: Previously corrected. | Immediately | Corrected
Initial Inspection |  | 2 | The telecoms mast at the in front of building 3 to be made safe. | Priority 2: Permit to be sought for mast. | Mast height below 180 ft. does not required permission. | Jul 31 2014 | On 21/05/15: The factory has re located and re constructed with proper drawing and designing. On 20/06/16: Found corrected from previous inspection. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: Telecom mast has been relocated, its not connected to any structure system now. On 25-Feb-2018: Mast was relocated which is not connected to any structures. Issue remains corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. Telecom mast has been relocated, its not connected to any structure system now. On 28-Nov-2024: Previously corrected. | Within 6 weeks | Corrected
Initial Inspection |  | 3 | No edge protection at first floor of the warehouse. | Priority-1: Restrict access to 1st floor levelof the warehouse building untill construction is completed. | Completed before received the report from accord. | Jul 29 2014 | On 21/05/15: They have completed construction, so why no need to put any edge protection. On 20/06/16: Found corrected from previous inspection. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: Construction is complete of the warehouse. there is no falling hazard for this building. On 25-Feb-2018: No construction was found going on. Issue was found corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. Construction is completed of the warehouse. There is no falling hazard for this building. On 28-Nov-2024: Previously corrected. Construction completed, no falling hazard issure observed. | Immediately | Corrected
Initial Inspection |  | 4 | The design for lateral loads within building 1 & 3 | Priority-2: ○ Building engineer to carry outthe calculations with a model based design check to assess the safety and serviceability of the building against loading as set out in BNBC-2006 | We have submitted required design and drawing to Accord for review and received final comments on 21.03.2016 and It will take 15 days to complete the retrofitting work recommended by Accord. | Apr 15 2016 | On 21/05/15: factory Engineer has to submit computer based modeling. On 20/06/16: This issue was covered in EA report. EA for production shed 1 & 3 have been accepted by Accord on 16 the April, 2016. According to the accepted EA report, they were required to built shear walls at some places to ensure the lateral stability. We observed construction of all required shear walls were completed. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: Corrected in previous follow-up. On 25-Feb-2018: Factory management has completed all the remedial works. Issue was found corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. On 28-Nov-2024: Previously corrected. | Within 6 weeks | Corrected
Initial Inspection |  | 5 | The design for lateral loads within building 1 & 3 | ○ Lateral stability of the production building to be part of check. | We have submitted required design and drawing to Accord for review and received final comments on 21.03.2016 and It will take 15 days to complete the retrofitting work recommended by Accord. | Apr 15 2016 | On 21/05/15: factory Engineer has to submit computer based modeling. On 20/06/16:This issue was covered in EA report. EA for production shed 1 & 3 have been accepted by Accord on 16 the April, 2016. According to the accepted EA report, they were required to built shear walls at some places to ensure the lateral stability. We observed construction of all required shear walls were completed. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: Corrected in previous follow-up. On 25-Feb-2018: Factory management has completed all the remedial works. Issue was found corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. Lateral stability check was performed as part of EA and factory has completed all the remedial works. On 28-Nov-2024: Previously corrected. | Within 6 weeks | Corrected
Initial Inspection |  | 6 | The design for lateral loads within building 1 & 3 | ○ The lateral stability system to be clear laid out and member sizes chacked for this loading condition. | We have submitted required design and drawing to Accord for review and received final comments on 21.03.2016 and It will take 15 days to complete the retrofitting work recommended by Accord. | Apr 15 2016 | On 21/05/15: factory Engineer has to submit computer based modeling. On 20/06/16: This issue was covered in EA report. EA for production shed 1 & 3 have been accepted by Accord on 16 the April, 2016. According to the accepted EA report, they were required to built shear walls at some places to ensure the lateral stability. We observed construction of all required shear walls were completed. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: Corrected in previous follow-up. On 25-Feb-2018: Factory management has completed all the remedial works. Issue was found corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. Lateral stability check was performed as part of EA and factory has completed all the remedial works. On 28-Nov-2024: Previously corrected. | Within 6 weeks | Corrected
Initial Inspection |  | 7 | The design for lateral loads within building 1 & 3 | Priority-3: Amend building as required from engineering assessment. | We have submitted required design and drawing to Accord for review and received final comments on 21.03.2016 and It will take 15 days to complete the retrofitting work recommended by Accord. | Apr 15 2016 | On 21/05/15: factory Engineer has to submit computer based modeling. On 20/06/16:This issue was covered in EA report. EA for production shed 1 & 3 have been accepted by Accord on 16 the April, 2016. According to the accepted EA report, they were required to built shear walls at some places to ensure the lateral stability. We observed construction of all required shear walls were completed. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: Corrected in previous follow-up. On 25-Feb-2018: EA was accepted on 16th April 2016. Factory management has completed all the remedial works. Issue was found corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. Lateral stability check was performed as part of EA and factory has completed all the remedial works. On 28-Nov-2024: Previously corrected. | Within 6 months | Corrected
Initial Inspection |  | 8 | Design strength of the columns to resists lateral loads in bending. | Priority-2: ○ Building engineer to carry outthe calculations with a model based design check to assess the safety and serviceability of the building against loading as set out in BNBC-2006 | We have submitted required design and drawing to Accord for review and received final comments on 21.03.2016 and It will take 15 days to complete the retrofitting work recommended by Accord. | Apr 15 2016 | On 21/05/15: factory Engineer has to submit computer based modeling. On 20/06/16: This issue was covered in EA report. EA for production shed 1,2 & 3 and Facility building have been accepted by Accord. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: Corrected in previous follow-up. On 25-Feb-2018: EA was accepted on 16th April 2016. Factory management has completed all the remedial works. Issue was found corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. On 28-Nov-2024: Previously corrected. | Within 6 weeks | Corrected
Initial Inspection |  | 9 | Design strength of the columns to resists lateral loads in bending. | ○ Adequicy of the RC columns in the production units and facilities building to be part of check. | We have submitted required design and drawing to Accord for review and received final comments on 21.03.2016 and It will take 15 days to complete the retrofitting work recommended by Accord. | Apr 15 2016 | On 21/05/15: factory Engineer has to submit computer based modeling. On 20/06/16: This issue was covered in EA report. EA for production shed 1,2 & 3 and Facility building have been accepted by Accord. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: Corrected in previous follow-up. On 25-Feb-2018: EA was accepted on 16th April 2016. Issue was covered in EA. Issue remains corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. On 28-Nov-2024: Previously corrected. | Within 6 weeks | Corrected
Initial Inspection |  | 10 | Documents do not match the as-built in the warehouse or show masts | Priority-2: Building engineer to surveyand amend drawings to includes alterations to warehouse and additional structure such as the two masts. | Building engineer surveyed and amend drawings to includes alterations to warehouse and additional structure such as the two masts. | Jul 29 2014 | On 21/05/15: Factory engineer has prepared as built drawing which reflect actual site condition. On 20/06/16: Masts were removed. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: Documents provided to ACCORD match with as-built condition. During inspection mast was observed at new location. On 25-Feb-2018: As built drawing was prepared and found satisfactory with the accepted drawing. Mast was relocated which has no connection with any structures. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. During inspection, accepted as-built drawing matched with onsite condition. On 28-Nov-2024: Previously corrected. As-built drawing was found satisfactory with on-site condition. | Within 6 weeks | Corrected
Initial Inspection |  | 11 | Cracking noted in the wall panels of the warehouse | Priority-2: Building engineer to investigate wall panel cracking noted in the ware house building. | Building engineer has investigated and no settlement have found in building. So this crack is not flexural Find that there is no structural crack found. Crack arises in brick wall due to TEMPERATURE AND SHRINKAGE. We repair this portion and in continuous | Jul 29 2014 | On 21/05/15: The crack was non structural crack. On 20/06/16: Found corrected from previous inspection. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: This issue was corrected from previous inspection. Factory management investigate and said that was a non structural crack. On 25-Feb-2018: Cracks were repaired and no cracks were visible during inspection. Issue remains corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. Factory has repaired all the cracks in wall panels and during inspection, no cracks were observed. On 28-Nov-2024: Corrected previously. The factory has repaired all the cracks. During Inspection, no further cracks were found. | Within 6 weeks | Corrected
Initial Inspection |  | 12 | Cracking noted in the wall panels of the warehouse | Priority-3: Carry out any remedial/strengthening works following engineering investigation. | Completed all remedial/strengthening works following engineering investigation. | Jul 29 2014 | On 21/05/15: The crack was non structural crack. On 20/06/16:This issue was covered in EA report. EA for production shed 1,2 & 3 and Facility building have been accepted by Accord. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: This issue was corrected from previous inspection. Factory management investigate and said that was a non structural crack. On 25-Feb-2018: Cracks were repaired and no cracks were visible during inspection. Issue remains corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. Factory has repaired all the cracks in wall panels and during inspection, no cracks were observed. On 28-Nov-2024: Corrected previously. The factory has repaired all the cracks. During Inspection, no further cracks were found. | Within 6 months | Corrected
Initial Inspection |  | 13 | Concreat internal columns noted off plumb in production building. | Priority-2: Building engineer to investigate the cause and impact of the internal off-plumb RC columns. | Advised to monitor the issue. | Jul 11 2015 | On 21/05/15: Though factory engineer confirm that the problem occur for poor workmanship. We advise them to monitor this issue. On 20/06/16: This issue was covered in EA report. EA for production shed 1,2 & 3 and Facility building have been accepted by Accord. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: corrected in previous follow-up. No aligned column was found. On 25-Feb-2018: Issue was covered in EA which was accepted from ACCORD. Factory has completed all the remedial works. Issue remains corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. On 28-Nov-2024: Previously corrected. | Within 6 weeks | Corrected
Initial Inspection |  | 14 | Concreat internal columns noted off plumb in production building. | Priority-3: Carry out remedial works as required engineering investigation. | Advised to monitor the issue. | Jul 11 2015 | On 21/05/15: Though factory engineer confirm that the problem occur for poor workmanship. We advise them to monitor this issue. On 20/06/16: Comments are same as previous follow-up inspection. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: corrected in previous follow-up. column was found ok. On 25-Feb-2018: Issue was covered in EA which was accepted from ACCORD. Factory has completed all the remedial works. Issue remains corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. Factory has completed all the remedial works as per accepted EA. On 28-Nov-2024: Previously corrected. | Within 6 months | Corrected
Initial Inspection |  | 15 | Non-engineered roofs to the stair wells of the warehouse and over the water treatment plant. | Priority-2: The roofs to the stair wells in the ware house and the roof over the water treatment plant to be assessed by building engineer. | o We remove non engineer roof from ware house and reconstruction is running on the basis of BNBC-2006. o For Water treatment Plant non engineered roof will change as per BNBC-2006 | Jul 29 2014 | On 21/05/15: The factory has reconstructed the roof in a proper way. On 20/06/16: Found corrected from previous inspection. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: corrected in previous follow-up. On 25-Feb-2018: Roof has been reconstructed in proper way. Issue remains corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. Factory has completed all the remedial works as per accepted EA and roof has been reconstructed in engineered way. On 28-Nov-2024: Corrected previously. Roofs have been reconstructed in engineered way. | Within 6 weeks | Corrected
Initial Inspection |  | 16 | Non-engineered roofs to the stair wells of the warehouse and over the water treatment plant. | Priority-3: Implement actions arising from assessment. | Implemented all the actions arising from the assessment. | Nov 30 2014 | On 21/05/15: The factory has reconstructed the roof in a proper way. On 20/06/16: Found corrected from previous inspection. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: corrected in previous follow-up. As per EA recommendation remedial work found completed. On 25-Feb-2018: Issue was covered in EA which was accepted from ACCORD. Factory has completed all the remedial works. Issue remains corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. Factory has completed all the remedial works as per accepted EA. On 28-Nov-2024: Corrected previously. The factory has completed all the remedial works. | Within 6 months | Corrected
Initial Inspection |  | 17 | Canopy fixing in the warehouse not properly engineered. | Priority-2: The canopy fixing to the warehouse building have not been properly engineered. Building engineer to review and make recommendations. | We remove all Canopy that support from building column and provide as per our modification drawing | Jul 29 2014 | On 21/05/15: The factory has fixed all canopy by providing individual column. On 20/06/16: Found corrected from previous inspection. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: As per EA recommendation extra column and lateral support has been found added to strengthen the canopy. This issue was corrected from previous inspection. On 25-Feb-2018: Issue was covered in EA which was accepted from ACCORD. Factory has completed all the remedial works. Issue remains corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. Factory has completed all the remedial works as per accepted EA. On 28-Nov-2024: Corrected previously. | Within 6 weeks | Corrected
Initial Inspection |  | 18 | Canopy fixing in the warehouse not properly engineered. | Priority-3: Carry out the above works. | All canopy fixing in the premises as engineered. | Jul 29 2014 | On 21/05/15: The factory has fixed all canopy by providing individual column. On 20/06/16: Found corrected from previous inspection. On 22-Nov-2016: This issue is corrected as per previous inspection. On 13-Jul-2017: As per EA recommendation extra column and lateral support has been found added to strengthen the canopy. This issue was corrected from previous inspection. On 25-Feb-2018: Issue was covered in EA which was accepted from ACCORD. Factory has completed all the remedial works. Issue remains corrected from previous follow up inspection. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. Factory has completed all the remedial works as per accepted EA. On 28-Nov-2024: Corrected previously. Individual column installed. | Within 6 months | Corrected
Follow Up Inspection |  | 19 | New Findings: As-built drawings for ware house do not match properly | Prepare complete set of as-built drawings properly | Factory has received design, drawing acceptance from Accord on 22 May 2017 and completed the Retrofitting work as per instruction. | Aug 1 2016 | On 20/06/16: Follow ACCORD recommendation properly. On 22-Nov-2016: Factory submitted the as built drawing in 17 Aug 2016. During inspection, the drawing was found incomplete and not fully match with as built condition. Factory told that they will submit the corrected drawing with in 30th Nov 2016. On 13-Jul-2017: A set of as built drawing was produce and re-accepted along with EA report from ACCORD on 22-May-2017. As per EA recommendation remedial work was on going and completed yet. On 25-Feb-2018: A set of as-built drawing has been prepared along with EA. EA was accepted from ACCORD and factory has completed all the remedial works as per EA recommendation. On 13-Aug-2018: This issue was corrected from previous inspection. On 13- Sep-2022: Corrected from previous inspection. During inspection, accepted as-built drawing matched with onsite condition. On 28-Nov-2024: Corrected previously. During Inspection, as-built drawing was found satisfactory with on-site condition. | Within 6 weeks | Corrected
Follow Up Inspection |  | 20 | New Findings: No load plan was available for warehouse. | Produce and actively manage a loading plan for mezzanine floor of the building giving consideration to floor capacity and column capacity according to BNBC. | Factory has further submitted design, drawing and other report as per requirement of Accord on 12 Apr 2017 after receiving comments from Accord on previous submission. After submission on 12 Apr 2017 Accord has invited factory and structural consultants to a EA presentation session to conclude the issues on 27 Apr 2017. As per EA presentation session comments structural consultants has submitted required designs, drawings and reports to Accord finally by incorporating necessary changes on 07 May 2017. | Aug 1 2016 | On 20/06/16: Follow ACCORD recommendation properly. On 22-Nov-2016:Factory submit the load plan in 17th Aug 2016 to ACCORD but without analysis file. Factory told that they will submit the analysis file with in 30th Nov 2016. During inspection load was found less that 42 psf. Factory is required to post the load plan after getting approval. On 13-Jul-2017: Load plan found posted and load was found below allowable loading limit. On 25-Feb-2018: Load plan has been prepared and found posted. Floor loading observed below the limit of final load plan. On 13-Aug-2018: This issue was corrected from previous inspection. During inspection, loading was found within allowable limit (4KN/m2) of accepted documents. On 13- Sep-2022: Corrected from previous inspection. During inspection, load plan was found posted on each floor and loading was found within allowable limit as per re-accepted load plan (4 kPa). On 28-Nov-2024: Corrected previously. Load plan was posted on each floor, and loading was found within the allowable limit (4 KPa). | Within 6 weeks | Corrected
Follow Up Inspection |  | 21 | New Findings: Corrosion observed in steel member | Provide protection to avoid corrosion | Factory has completed color coating to prevent corrosion. | Apr 8 2018 | On 25-Feb-2018: During inspection, corrosion was found in steel member. Factory management is required to provide protective coating to resist corrosion. On 13-Aug-2018: During inspection, no significant corrosion was found in steel members except in roof bracing. As well as roof bracing were found loose. The Roof bracing were tighten & paint was applied by factory. The pictorial evidence was sent by email. On 13- Sep-2022: Corrected from previous inspection. Factory has provided rust proofing paint on steel members and during inspection no corroded member was observed. On 28-Nov-2024: Corrected previously. The factory has remove corrosion. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 22 | New Finding-4: New structure- single storied Facility Shed-2 (Admin Building, approximate floor area 9,500 sft). Lack of As-built drawing and assessment report. | Prepare complete set of as-built drawings and Engineering Assessment (EA) report for the shed and submit to RSC for review. | A complete set of as-built drawings and the Engineering Assessment (EA) report for the single storied Facility Shed-2 were prepared and submitted to RSC for review. The submission was reviewed and accepted by RSC on 24-02-2026. | Jan 9 2025 | On 28-Nov-2024: During the inspection, we observed an uncovered single-storied large shed structure within the factory premises which has not covered during initial inspection. This shed (referred to as both Admin Building and Facility Shed-2, with an approximate floor area of 9500 sq. ft) is primarily used as a dining area, with a portion serving as office space. The building engineer is required to prepare a set of as-built drawings and Engineering Assessment (EA) report for the shed. Submit documents to the RSC for review. RPO Comments: On 29-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 weeks) | Pending Verification
Follow Up Inspection |  | 23 | New Finding-5: New structure- single storied Facility Shed-2 (Admin Building, approximate floor area 9,500 sft). Lack of As-built drawing and assessment report. | Carry out remedial works if required. | Remadial work not required | May 28 2025 | On 28-Nov-2024: Once the EA is accepted by the RSC, carry out remedial works if required. RPO Comments: On 29-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 months) | Pending Verification
Follow Up Inspection |  | 24 | New Finding-6: New structure- single storied Common Service (CS) Shed (approximate floor area 2,450 sft). Lack of As-built drawing and poor connection details and apparently inadequate member for the extension parts at front & back. | Prepare a set of as-built drawing and safety check report for the CS Shed and submit it to the RSC for review | A complete set of as-built drawings and the Engineering Assessment (EA) report for the single storied Common Service (CS) Shed were prepared and submitted to RSC for review. The submission was reviewed and accepted by RSC on 24-02-2026. | Jan 9 2025 | On 28-Nov-2024: During the inspection, we observed an uncovered single-storied shed structure within the factory premises which has not covered during initial inspection. This shed (referred to as Common Service (CS) Shed, with an approximate floor area of 2450 sq. ft) is primarily used as a shopping mall, accessories storage of different engineering departments. The building engineer is required to prepare a set of as-built drawings and Safety Check report for the shed and submit to RSC for review. RPO Comments: On 29-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 weeks) | Pending Verification
Follow Up Inspection |  | 25 | New Finding-7: New structure- single storied Common Service (CS) Shed (approximate floor area 2,450 sft). Lack of As-built drawing and poor connection details and apparently inadequate member for the extension parts at front & back. | Carry out remedial works where required. | Remadial work not required | May 28 2025 | On 28-Nov-2024: Once the safety check report is accepted by the RSC, carry out remedial works if required. RPO Comments: On 29-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 months) | Pending Verification

## Fire
Date
29-Apr-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Chorka Textile Ltd., Kazir Chor Danga Palash Narshingdi, -, Narsingdi, Dhaka
Date of Inspection |  | 2014-05-08
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The boiler room is not separated by fire rated construction, openings, non-rated doors and penetrations. | Separated the boiler room by a minimum 2 hours fire rated construction. Seal and protected all openings to maintain the required fire separations | Corrected | Jun 11 2015 | On 26/04/2016: Corrected. On 13/06/2016:Corrected. Separated boiler room has been provided. On 13/07/2016: Corrected. On 22/11/2016: Corrected On 18/02/2018: Corrected as on previous follow ups. On 16/07/2018: Corrected. On 30/12/2019: Corrected. On 04/10/2022: Corrected. On 12-Dec-24: Corrected On 20-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 2 | Areas used for storage on the shade 5 are not separated by fire rated construction (Fire door) | provide minimum 1.5 hrs fire rated door and seal all unprotected openings to separate the storage from work areas and egress path. Ensures that the fire doors are self closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reason, provide automatic closing devices tied to fire alarm system. | Corrected | Jun 11 2015 | On 26/04/2016: Corrected. On 13/06/2016: Corrected. Fire door has been installed. Note: Door coordinators shall be in all double leaf fire doors. Exit stairs shall be separated properly. On 13/07/2016: Corrected. On 22/11/2016: Corrected On 18/02/2018: Refer to issue 12. On 16/07/2018: Corrected. On 30/12/2019: Corrected. On 04/10/2022: Corrected. On 12-Dec-24: Corrected On 20-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 3 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72 | Corrected | Jan 7 2016 | On 26-04-16: Corrected. Testing commissioning of the total system done by Accord in-front of the contractor. On 13/06/2016: Corrected. On 13/07/2016: Corrected. On 22/11/2016: Corrected On 18/02/2018: Refer to issue 10. On 16/07/2018: Refer to issue 10. On 30/12/2019: Refer to issue 10. On 04/10/2022: Corrected. Factory shall maintain the system according to the NFPA 72 and RSC standard. On 12-Dec-24: Corrected. The system was functional during the inspection. Note: Device identification numbers were not proper at a few locations. Complete address shall be legibly labeled on addressable devices. On 20-May-25: Corrected. The installed fire alarm and detection system were active and the FACP was found in normal condition. As-built drawing was found updated. Exhaust fan, elevator and fire rated door interfacings were functioning properly. | Design within 4 months, install within 9 months | Corrected
Initial Inspection |  | 4 | Inspection, testing and maintenance for the fire alarm system was not accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on site, in accordance with NFPA 72 | Corrected | Jun 11 2015 | On 26/04/2016: Corrected. On 13/06/2016: Corrected. ITM has been found as per NFPA 72. On 22/11/2016: Corrected On 13/07/2016: Corrected. On 18/02/2018: Corrected as on previous follow ups. On 16/07/2018: Corrected. On 30/12/2019: Corrected. On 04/10/2022: Corrected. On 12-Dec-24: Corrected On 20-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 5 | Inspection, testing and maintenance records for the fire detection system was not accordance with NFPA 72. | Inspect, test and maintain the fire detection system, and keep written records on site, in accordance with NFPA 72 | Corrected | Jun 11 2015 | On 26/04/2016: Corrected. On 13/06/2016: Corrected. ITM has been found as per NFPA 72. On 13/07/2016: Corrected. On 22/11/2016: Corrected On 18/02/2018: Corrected as on previous follow ups. On 16/07/2018: Corrected. On 30/12/2019: Corrected. On 04/10/2022: Corrected. On 12-Dec-24: Corrected On 20-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 6 | The building is equipped with single station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Replace the single station smoke alarm with automatic smoke detectors tied in to the fire alarm system. Configure the fire alarm system to initiate occupant notification upon activation of any two smoke detectors in addition to the manual fire alarm station. | Corrected | Jan 7 2016 | On 07-12-15: It is an integrated part of fire alarm system. On 26-04-16: Corrected. Testing commissioning of the total system done by Accord in-front of the contractor. On 13/06/2016: Corrected. On 13/07/2016: Corrected. On 22/11/2016: Corrected On 18/02/2018: Refer to issue 10. On 16/07/2018: Corrected as per last follow ups. Integrated part of fire alarm system. On 30/12/2019: Corrected as per last follow ups. On 04/10/2022: Corrected. On 12-Dec-24: Corrected On 20-May-25: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 7 | Manual on-off switches is provided for emergency lighting units. | Remove manual on-off switches from emergency lighting and exit signage to prevent them from being switched off. | Corrected | Jun 11 2015 | On 26/04/2016: Corrected. On 13/06/2016: Corrected. Manual on-off switch was not found. On 13/07/2016: Corrected. On 22/11/2016: Corrected On 18/02/2018: Corrected as on previous follow ups. On 16/07/2018: Corrected. On 30/12/2019: Corrected. On 04/10/2022: Corrected. On 12-Dec-24: Corrected On 20-May-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 8 | Inspection, testing and maintenance records for the emergency lighting was not accordance with NFPA 72 | Inspect, test and maintenance the emergency lighting system in accordance with the Accord standard. Keep written records on-site. | Corrected | Jun 11 2015 | On 26/04/2016: Corrected. On 13/06/2016: Corrected. ITM has been found as per NFPA 72. On 13/07/2016: Corrected. On 22/11/2016: Corrected On 18/02/2018: Corrected as on previous follow ups. On 16/07/2018: Corrected. On 30/12/2019: Corrected. On 04/10/2022: Corrected. On 12-Dec-24: Corrected On 20-May-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 9 | New Finding (1st Follow up): Areas used for combustible storage in shed-3 are not separated by fire-rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2. - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Corrected | Jun 11 2015 | On 26/04/2016: Corrected. On 13/06/2016: Corrected. Defined area has been provided. On 13/07/2016: Corrected. On 22/11/2016: Corrected On 18/02/2018: Refer to issue 12. On 16/07/2018: Corrected On 30/12/2019: Corrected. On 04/10/2022: Corrected. On 12-Dec-24: Refer to issue 12. On 20-May-25: Refer to issue 12. | Within 1 months | Corrected
Follow Up Inspection |  | 10 | New Finding (5th Follow up): Some discrepancies have been found during the follow-up; the system panel, devices & accessories were not certified. Also, the placement of the detectors was not correct. However, the system was working properly during the testing mode. | The non-certified fire alarm system control panel and devices shall have to be replaced with the certified ones. Installation of the devices shall have to be as per NFPA 72 such as the placement of the detectors shall have to be proper. NAC shall have to be a separate circuit. After completion of these modification prepare the as-built drawing as per NFPA 72 & keep it at site for future follow-ups. | Corrected | Jan 22 2017 | On 30/12/2019: The system installation has been completed. Pre T & C done by the Accord. Full T & C has been pending. On 27/11/2019(T&C): T&CVI found that final verification required. For details follow the full report. On 09/02.2021: T&CVI found that the system is corrected. On 04/10/2022: Corrected. Factory shall maintain the system according to the NFPA 72 and RSC standard. On 12-Dec-24: Corrected On 20-May-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 11 | New Finding (5th Follow-up): The exit stairs are not separated from (work areas, other spaces) on each floor by fire-rated construction. The fire separation work was going on. | Stair shall be enclosed with a minimum 1-hr fire-rated construction. Seal all unprotected openings and provide minimum 1-hr fire rated doors to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing, positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. | Factory will provide 1 hour fire rated construction and will provide self closing fire door to seal all unprotected openings and to separate the exit stairs from work areas and other building spaces on all floor levels by 15 Apr 2025. | Dec 22 2016 | On 22/11/2016: In progress. Final CAP TimeLine: Expired Committed Timeline: 22/12/2016 On 18/02/2018: Door coordinator not found in any fire door. Some door were found damaged and welded. Fabric inspection room not separated yet in ground floor. On 16/07/2018: Not corrected. The fire rated doors were not found functional. On 30/12/2019: The fire rated doors were not working properly. On 04/10/2022: Fire rated doors were in working condition but have observations. Door's accessories have been damaged due to lack of proper maintenance. Smoke seals have been damaged. Repairing of doors by authorized technicians is recommended. On 12-Dec-24: The factory has replaced the doors. However, an unprotected opening was observed at the ground floor due to the lift opening within the stair enclosure, which connects to the first-floor production area. In addition, racks were observed within the stair enclosure which shall be removed. On 20-May-25: Corrected. Separated by fire rated construction and openings are protected by fire rated doors. Installed listed fire rated doors and door accessories were found functional, doors were interfaced with FACP and gap beneath fire rated doors were found less than 19 mm. | Within 1 month | Corrected
Follow Up Inspection |  | 12 | New Finding (5th Follow-up): Areas used for in-process storage of combustible materials are open to the surrounding occupancy in the production shed | Provide defined storage areas and limit the storage arrangement as: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Factory has provided designated space for the temporary storage as per NFPA. | Dec 22 2016 | On 22/11/2016: In progress. On 18/02/2018: Not maintaining as per standard. On 16/07/2018: Corrected. On 30/12/2019: Corrected. On 04/10/2022: Corrected. On 12-Dec-24: In-process storage was observed in an unplanned manner at shed 1 & shed 2. On 20-May-25: In progress. In process storage management for combustible materials at Shed-2 was found well defined and within permitted limit. But, at the Shed-1, Shed-3 & Shed-4 (ground floor-sewing section) were observed improper and exceeded the permitted limit. RPO Comments on 5-Oct-2025: the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 13 | New Finding (5th Follow-up): Storage was located in the exit stair. | Remove all storage from exit stairs. | Corrected | Dec 22 2016 | On 22/11/2016: In progress. Partially done. Toilet and Dv board found under stair. On 18/02/2018: Electric distribution board not removed yet. On 16/07/2018: Corrected. On 30/12/2019: Corrected. On 04/10/2022: Corrected. On 12-Dec-24: Corrected On 20-May-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 14 | New Finding: Doors along means of egress are provided with non compliant locking system. (Two storied building) | Remove all non compliant locking features from egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Feb 22 2018 | On 16/07/2018: Corrected. On 30/12/2019: Corrected. On 04/10/2022: Corrected. On 12-Dec-24: Corrected. On 20-May-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 15 | New Finding: Adequate egress aisles not provided. | Aisles shall be provided with a minimum unobstructed clear-width of 0.9 m (36 in.). | Corrected | Mar 18 2018 | On 16/07/2018: Corrected. On 30/12/2019: Corrected. On 04/10/2022: Corrected. On 12-Dec-24: Corrected. On 20-May-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 16 | New Finding: Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Factory has tested Emergency Lighting System as per guideline. | Mar 18 2018 | On 16/07/2018: Corrected. On 30/12/2019: In progress. In some places emergency light & directional sign needs to increase. On 04/10/2022: Adequate illumination is not observed in shed 1, 2, 3 and 1st floor of building 4. On 12-Dec-24: Corrected. Adequate emergency light observed all areas. On 20-May-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 17 | New Finding: Wastage store is not separated from the production shed (shed-1). | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour construction. | Corrected | Apr 18 2018 | On 16/07/2018: Corrected. On 30/12/2019: Corrected. On 04/10/2022: Corrected. On 12-Dec-24: Corrected. On 20-May-25: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 18 | New Finding (9th F-up): Printing section is not separated. | Printing section shall be separated from storage occupancy with a minimum 1 hour construction. | Factory will provide 1 hour fire rated construction to separate printing area from storage occupancy. It will be completed during Eid holidays. | Feb 29 2020 | New finding On 04/10/2022: Progress is observed but unsealed penetration is still exist. On 12-Dec-24: Store room is separated from printing section but still not separated from sucker room. In addition, the storeroom is not separated from the adjacent occupancy in Shed 03. On 20-May-25: Corrected. Separated by fire rated construction. | Within 2 months | Corrected
Follow Up Inspection |  | 19 | New Finding (10th F-up): Storage was located on the egress path and within the exit stair enclosure. | Remove storage from the egress path and exit stair | Factory has removed storage from the egress path and exit stair | Oct 7 2022 | On 04/10/2022: New Finding On 12-Dec-24: Removed. On 20-May-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 20 | New Finding (10th F-up): Egress doors/gates with non-complaint locking features are provided at building exits. | Remove non-complaint locking features from all egress doors/gates. | Factory has remove non-complaint locking features from all egress doors/gates. | Oct 7 2022 | On 04/10/2022: New Finding On 12-Dec-24: The locking feature was found at site but it was removed by the factory personnel immediately during the inspection. Factory is recommended to follow the recommendation. On 20-May-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 21 | New Finding (10th F-up): Exit stair door/egress door serving 50 or more occupants does not swing in the direction of egress travel at the main discharge path. | Modify the egress door to swing in the direction of egress travel. | Factory has modifies the egress door to swing in the direction of egress travel. | Nov 4 2022 | On 04/10/2022: New Finding On 12-Dec-24: Corrected. Side hinged door has been provided. On 20-May-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 22 | New Finding (10th F-up): Room used for combustible storage is not separated by fire rated construction from the production floor and egress path at shed 2. | Separate the storage room by a minimum 1- hr fire-rated construction. Seal and/or protect all openings to maintain the required fire separations. | Factory has Separated the storage room by a minimum 1- hr fire-rated construction and Sealed all openings to maintain the required fire separations. | Nov 4 2022 | On 04/10/2022: New Finding On 12-Dec-24: Not Found, the factory has removed the store from shed 2. On 20-May-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 23 | New Finding (11th FU): The factory has modified the means of egress by abandoning exits in Shed 3 and on the first floor of the warehouse building. During the inspection, it was observed that the maximum travel distance exceeded 45 meters in Shed 3, and the common path of egress travel exceeded 23 meters on the first floor of the warehouse building. | Reconfigure the egress arrangement or provide additional exits to ensure that the travel distance does not exceed 45 meters and the common path of egress travel does not exceed 23 meters. | Factory will provide additional exit to reduce travel distance within 15 Apr 2025. | Jan 12 2025 | New Finding on 12-Dec-2024. On 20-May-25: Corrected as per site observation. Additional exit provided. | Within 1 Month | Corrected
Follow Up Inspection |  | 24 | New Finding (12th FU): Fire evacuation maps is not posted at the entrance of all exit/exit stair. Evacuation map was found missing on several locations at various structures. | Fire evacuation maps shall be posted at the entrance to each exit/exit stair in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 13.3 | Factory make Fire Evacuation map available in all exit / stairs. | Jul 20 2025 | On 20-May-25: New Finding. RPO Comments on 24-Sep-2025: the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 Month | Pending Verification
Follow Up Inspection |  | 25 | New Finding (12th FU): Building does not have stair/floor level designation signs at required locations on all floors. Stair/floor level designation signs ware found missing on several locations at various structures. | Provide stair designation sign at each floor entrance from the stair to the floor in English and Bengali. Signs shall indicate the name of the stair and the floor level. Signs shall be posted adjacent to the door in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.9.3. | Factory has provided floor level designation in all floors. | Jul 20 2025 | On 20-May-25: New Finding. RPO Comments on 24-Sep-2025: the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 Month | Pending Verification
Follow Up Inspection |  | 26 | New Finding (12th FU): Building does not have occupant load signs at required locations on all floors. Occupant load signs was found missing on several locations at various structures. | Post the occupant load for every assembly and production floor in a facility in a conspicuous space near the main exit or exit access doorway for the space in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.4.4 . | Facility has posted occupant load sign at required locations on all floors. | Jul 20 2025 | On 20-May-25: New Finding. RPO Comments on 24-Sep-2025: the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 Month | Pending Verification

## Electrical
Date
29-Apr-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Chorka Textile Ltd., Kazir Chor Danga Palash Narshingdi, -, Narsingdi, Dhaka
Date of Inspection |  | 2014-05-08
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | HT service cable dropping from pole is not protected near the base of the pole, above ground level. | HT cable dropping from the pole must be protected in steel/PVC pipe of required size at least 2m from the ground level to protect from physical injury by moving objects. | HT cable dropping by PVC pipe will be completed by 31 Aug 2014. | Aug 31 2014 | On 13/06/2016: Corrected. On 21/05/2015: Corrected. | Within 12 weeks | Corrected
Initial Inspection |  | 2 | Cable trench without cover in transformer room. | The cable trench must be tightly covered to avoid physical damage to the cables from falling objects. The cover must prevent the trench from falling debris, dust and lint. | The cable trench has covered to avoid physical damage to the cables from falling objects. | Jul 15 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 12 weeks | Corrected
Initial Inspection |  | 3 | Panel base plate missing and excessive dust exist inside panel. | Panel base plate must be installed, at all time, and cables entering panel must be firmly fixed with cable gland to protect panel from ingression of dust and lint. | Completed | May 21 2015 | On 13/06/2016: Corrected. On 21/05/2015: Corrected. | Within 3 weeks | Corrected
Initial Inspection |  | 4 | Panel doors not connected with earth bond. | Provide earth connection for body and doors of metallic distribution boards using green cables preferably braid so that the metallic door and body remain at zero potential all the time. | Completed | May 21 2015 | On 13/06/2016: Corrected. On 21/05/2015: Corrected. | Within 3 weeks | Corrected
Initial Inspection |  | 5 | Generator's battery terminal covers are missing. | Provide insulating cover to the battery terminal to prevent short circuit due to falling foreign metal on it. | Completed | May 21 2015 | On 13/06/2016: Corrected. On 21/05/2015: Corrected. | Within 1 week | Corrected
Initial Inspection |  | 6 | Cables rising from the trench and passing through the wall is not protected and remaining gaps around the cable not sealed. | Cables passing through permanent wall must be protected and remaining gaps must be sealed with fire resistant material. Concrete slab should be extended to the point meeting the wall. | Cable passing through permanent wall has made protected and remaining gaps sealed with fire resistant material. | Jul 15 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 12 weeks | Corrected
Initial Inspection |  | 7 | Wires connected directly to bus bar without using cable lug. | Wires should be properly terminated and connected to bus bar using cable lug of proper size and rating. | Completed | May 21 2015 | On 13/06/2016: Corrected. On 21/05/2015: Corrected. | Within 3 weeks | Corrected
Initial Inspection |  | 8 | Ducts not covered and cables in it are randomly placed. | Cable ducts must be cleaned regularly and covered to prevent ingression of dust and lint. | Production unit cable ducts are covered by steel sheet and clean regularly. | Jul 15 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 12 weeks | Corrected
Initial Inspection |  | 9 | Multiple wires terminating to single point of earth bar. | Terminate each cable individually on the earth bar. Multiple cables shall not be terminated on same point of earth bar. | Multiple cable removed from same point of earth bar. | Jul 31 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 12 weeks | Corrected
Follow Up Inspection |  | 10 | New Finding: Transformer silica gel discolored & Breather oil cup is empty | Change silica gel & Fill the transformer breather oil cup by transformer oil. | Changed silica gel & transformer breather oil cup filled by transformer oil. | Jul 11 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 2 weeks | Corrected
Follow Up Inspection |  | 11 | New Finding: No separation between LT panels and HT units (Transformer, HT switchgear ) | Make a brick built separation between LT and HT units; ensure that after making separator you have adequate ventilation (cross ventilation) and working clearance around each electrical equipment | Provided brick built separation between LT and HT units keeping necessary ventilation. | Jul 11 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 12 | New Finding: Generator output cables (laid on floor) are not protected and supported. | If possible route all the power cable through overhead cable tray. Or ensure adequate protection for power cables arranging cable trench with checkered plate. Do not make any arrangement that obstacle personnel's movement within working clearance. | Generator output cable has protected. | Jul 11 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 13 | New Finding: Power cable is covered by sand in the cable trench. | Remove sand from cable trench avoiding physical damage of LT cable, route all cables through overhead cable tray or cover the trench with checkered plate or proper materials. Accumulation of rain water inside cable trench is not also acceptable. | Routed all cables through overhead cable tray. | Jul 11 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 14 | New Finding: Exposed and heated steam line is close to cables. | Wires close/attached to steam line/heat source must be protected from external heat. In unavoidable case provide proper insulation for the heat source/steam line. Normally power cable should keep 0.9m apart from hot area. | Wires close/attached to steam line/heat source has removed. | Jul 11 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 15 | New Finding: Cables in service are joined (splicing) between terminations. | Existing cables with joints must be spliced using butt splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. | Cable joints spliced using splicing kits and insulated by electrical tape. | Jul 11 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 16 | New Finding: Unterminated wire is kept inside production floor. | All unterminated wires shall be removed | All unterminated worse has removed. | Jul 11 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 17 | New Finding: MCCBs are not adjusted accordingly | Adjust all the MCCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals | Adjusted all the MCCBs according to cable ampacity. | Jul 11 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 18 | New Finding: Compressors have been installed congested. | Ensure minimum 1.07 m (42 inch) working clearance around every electrical installation | Compressors installation rearranged accordingly. | Jul 11 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 19 | New Finding: Wiring has done using flexible PVC cable around vertical boiler surface. | Wires close/attached to boiler must be protected from external heat. In unavoidable case use metal type flexible pipe. Again Power cable should keep 0.9m apart from hot area. | Wires close/attached to boiler has protected from external heat by using metal type pipe. | Jul 11 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 20 | New Finding: Haphazard cable dressing inside panel board. | Cables should be supported and dressed properly. | Cables inside the panel has organized. | Jul 11 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 21 | New Finding: Lightning Protections System (LPS) is inadequate for the factory | Redesign/modify LPS for your factory to increase safety; Factory have to submit LPS design to Accord before starting | Design reviewed by Accord. LPS installation has completed. | Nov 25 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 22 | New Finding: Insulation resistance test of electrical cable is not performed | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off) | Insulation resistant test of all cables has performed. | Nov 25 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 23 | New Finding: Thermo graphic scanning of the entire electrical system has not been tested and recorded. | Thermo graphic scanning for the entire electrical system must be performed on a bi-annual basis and recorded | Thermographic scanning for the entire electrical system has performed by a Third party named SDS and report submitted to Accord and adjust accordingly. | Jul 11 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 24 | New Finding: Transformer Oil Test report is unavailable | Check the transformer oil condition by performing oil test. Do it once in a year and keep the record. | Transformer oil condition tested. | Jul 11 2015 | On 13/06/2016: Corrected. On 07/12/2015: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 25 | New Finding: Inadequate working space around transformer for performing maintenance work | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained | Done and Corrected by Accord on 30 Dec 2019 | Oct 30 2018 | On 30-Dec-2019: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 26 | New Finding: Electrical power cables are not identified properly | Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables used in the system according to SLD. | Updated & provided Proper identification (by using cable marker, tag, colored heat shrink) according to SLD. | Sep 30 2018 | On 30-Dec-2019: Not Corrected. On 13-Sep-2022: Not Corrected. Still some work is pending. SLD is needed to be reviewed by RSC. On 04/01/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 27 | New Finding: Safety program is initiated but has no influence in the factory. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. | Done and Corrected by Accord on 30 Dec 2019 | Aug 30 2018 | On 30-Dec-2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding: Loop connection has been used powering multiple circuits through MCB/MCCBs. | No loop connection shall be used; each single cable shall be terminated using cable lug (flat/I) at each terminal. Combo bus bar may be used (but incoming cable size must meet the rated capacity) | Done and Corrected by Accord on 30 Dec 2019 | Aug 31 2018 | On 30-Dec-2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding: Drop out fuse is missing on HT main feeder line. | Drop out fuse must be connected at HT line in order to ensure electrical safety. | New Drop out fuse connected at HT line in order to ensure electrical safety. | Jan 30 2020 | On 13-Sep-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 30 | New Finding: Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ Busbar. | Each electrical circuit must be terminated at single MCB/MCCB terminals. | Each electrical circuit has terminated at single MCB/MCCB terminals. | Jan 30 2020 | On 13-Sep-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: Manually operated machines (may have chance to be touched by operator/user) have no earth connection. | Manually operated each machine (may have chance to be touched by user/operator) must have earth connection. Cable selection shall be made per CB response and circuit's power demand. | Manually operated each machine (may have chance to be touched by user/operator has provided new Plug with earth connection and cable selection has made per CB response and circuit's power demand. | Jan 30 2020 | On 13-Sep-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 32 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Heat source (steam line) & Electrical installation has separated. | Jan 30 2020 | On 13-Sep-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: Transformer Oil Test (dielectric strength test) report is available but result is not satisfied. Oil leakage from transformer has been observed. | Transformer oil test (dielectric strength test for oil) shall be done once in a year. In case of getting poor result the possible reason should be identified with proper maintenance/repair. Oil leakage from transformer must be stopped and top of transformer must also be kept clean. | Transformer oil test has done and it will be maintaining as per guideline. maintenance/repair. Oil leakage repaired and top of transformer has kept clean. | Oct 19 2022 | On 04/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 34 | New Finding: Outdoor Cable trays are not covered to protect from weather effect. | Outdoor cable tray/ladders shall be covered properly to avoid seasonal effect on cables and its longevity. | Outdoor cable has covered properly to avoid seasonal effect on cables and its longevity. | Oct 19 2022 | On 04/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 35 | New Finding: Inadequate working space around (or in front of) board/panels and access to the board/panels is obstacles. | At least 1.07 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel. | Working clearance has maintained in front of each Electrical Board/Panel. | Oct 19 2022 | On 04/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 36 | New Finding: Cable connected to busbar/MCCB/MCB terminal without cable lug. | Each electrical circuit must be terminated at single busbar/MCB/MCCB terminal using cable proper sized cable lug (where applicable). | Each electrical circuit has terminated at single busbar/MCB/MCCB terminal using cable proper sized cable lug (where applicable). | Oct 19 2022 | On 04/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Lightning Protection System (LPS) is not installed properly including improper air terminal spacing, inadequate earth electrode size, absence of bi-metallic joints where required. | Factory required to be redesign the Lightning Protection System (LPS) as per standard for the entire facility. Once the LPS is properly designed, it must be installed according to the design specifications to ensure effective protection against lightning strikes. | Factory has redesign the Lighting Protection System (LPS) as per guideline in standard by giving proper air terminal spacing, adequate earth electrode size and required provided bi-metalic joints. | Mar 14 2025 | RPO Comments: On 13-Aug-2025: the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 Months | Pending Verification
Follow Up Inspection |  | 38 | New Finding: Field information has no/less reflection in existing SLD. | As-built Electrical Single Line Diagram (SLD) must be prepared by a qualified engineer, including all essential details of the electrical system. This diagram must be reviewed and approved by the RSC. The accepted SLD needs to be implemented at the factory.. | Factory has submitted reviewed SLD to RSC and received review comments on 17 Nov 2025. Further submission on 10 Jan 2026 in corporating the review comments given on 17 Nov 2025. Received SLD Acceptance from RSC on 14 Jan 20026. Factory has implemented the chenges as per Accepted SLD design documents. | Mar 14 2025 | RPO Comments: On 29-Apr-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 Months | Pending Verification