## Structural
Date
31-Mar-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Denimach, Kewa Mouja, Ward No. 5, Gorgoria Masterbari, Sreepur, Gazipur, Dhaka
Date of Inspection |  | 2014-05-22
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | No structural documentation for: Washing Building Extension, Steel Mezzanine Extension for AC System Support, Steel Roof at Utility Building, Bridge between Main Building and Utility Building | Provide certified as-built drawings for Washing Building Extension, Steel Mezzanine Extension for AC System Support, Steel Roof at Utility Building, and Bridge between Main Building and Utility Building. Provide letter from EOR indicating that the impact on the structure from these additions has been considered. | We have done this | Jan 3 2016 | On 11/10.2015: At the time of inspection we were provided with all the related documents but they did no submit those documents to alliance for approval. On 14/03/2017: This issue is required to be covered in DEA. Factory management has submitted DEA report to Alliance and it is under reviewed. On 28/11/2017: Factory lead brand Levis conducted a DEA by BRTC BUET. Factory consultant (Prudential Consultants) has also conducted a DEA under BUET's supervision. Factory submitted all the documents to Alliance on Sep 09, 2016. In 3rd RVV report Alliance marked this issue status as 'completed' with the comment "DEA has been reviewed by BUET". Hence this issue is considered as 'corrected'. On 18/07/2018: Corrected in previous follow-up inspection. On 16/05/2019: Corrected in previous follow up inspection. On 17th Nov 2019: Corrected from previous inspection. On 25-Aug-2024: Corrected previously. DEA of the Main Building and Washing Building was re-accepted by BUET on 28-May-2019. The DEA of the Utility Building was accepted by BUET on 22-Apr-2018. As per the CCVV on 20-Nov-2018, the steel bridge was accepted by Alliance. On 23-Nov-2025: Previously corrected. On 04-Mar-2026: Previously corrected. | 25/02/2015 | Corrected
Initial Inspection |  | 2 | Main Building: Storage Racks at 2nd Floor of Admin Wing reaches ceiling (10 boxes). Main Building: Isolated areas of storage boxes on 1st through 6th Floor may exceed design Live Load. Washing Building: Boxes of loose denim stacked 9 feet high at 1st Floor Destroy Section | Have a qualified structural engineer confirm that capacity to support the load is available. Load Plans complying with Alliance Standard Part 8 Section 8.20.4.3 should also be developed. | We have done this | Jan 3 2016 | On 11/10.2015: Load plan was prepared as a part of DEA and loading plan was posted on floors but that was not approved from alliance till the time of inspection. On 14/03/2017: A set of load plan was produced and included in DEA. DEA was submitted to Alliance which is under review. Factory was required to maintain safe load (42psf). Overloading observed in washing building. The factory is suggested to reduce the load as per allowable limit. On 28/11/2017: Factory lead brand Levis conducted a DEA by BRTC BUET. Factory consultant (Prudential Consultants) has also conducted a DEA under BUET's supervision. Factory submitted all the documents to Alliance on Sep 09, 2016. In 3rd RVV report Alliance marked this issue status as 'completed' with the comment "This issue cover under DEA". During inspection load plans were posted and loading was below load plan limit. Hence this issue is corrected. Hence this issue is considered as 'corrected'. On 18/07/2018: Corrected in previous follow-up inspection. On 16/05/2019: Corrected in previous follow up inspection. On 17th Nov 2019: Corrected from previous inspection. DEA of this factory has been reviewed and re-accepted from BUET on 28th May 2019. Load plan has also been produced and re-accepted as a part of DEA. On 25-Aug-2024: Corrected previously. During load plan was found posted on floors of the Main Building and Washing Building. The floor loading was within allowable limit of accepted load plan (Main Building- Storage 157.7psf, production area 84 to 157.7psf & Dormitory 63 psf. Washing Building- storage 105 psf, production area 42 to 63 psf, dining and office area 63 psf). On 23-Nov-2025: Previously corrected. On 04-Mar-2026: Previously corrected. | 25/02/2015 | Corrected
Initial Inspection |  | 3 | Racks requiring bracing: Main Building - 1st through 6th Floor; Washing Building - 1st Floor; Utility Building - Mezzanine and Ground Floor | Adequately anchor and brace all non-structural elements to resist earthquake forces to comply with the BNBC and Alliance Standard. | We have done this | Feb 25 2015 | On 11/10.2015: This issue has been done. On 14/03/2017: This issue has been corrected in the 2nd follow up. Racks were found anchored properly to resist earthquake force. On 28/11/2017: This issue has been corrected in the previous follow up. During inspection racks were found anchored with the floor. On 18/07/2018: Corrected in previous follow-up inspection. During inspection racks were found anchored. On 17th Nov 2019: Corrected from previous inspection. During inspection, all non structural elements were found anchored and braced. On 25-Aug-2024: Corrected previously. On 23-Nov-2025: Previously corrected. On 04-Mar-2026: Previously corrected. | 25/02/2015 | Corrected
Initial Inspection |  | 4 | Lateral Load Resisting System is unclear in steel roofs located at Main Building, Washing Building Extension, Utility Building, Waste Shed, Boiler Shed. | Have a qualified structural engineer complete further analysis of the structure and develop a remediation plan if required. | We have done this | Jan 3 2016 | On 11/10/2015: The factory management appointed an engineering firm to do DEA and this issue has been covered under this DEA. But that has not got any approval from alliance till the time of inspection. On 14/03/2017: Factory was carried out DEA. DEA was submitted to Alliance which is under review. After DEA approval, factory is required to carry out remedial works as per approved DEA. On 28/11/2017: Factory lead brand Levis conducted a DEA by BRTC BUET. Factory consultant (Prudential Consultants) has also conducted a DEA under BUET's supervision. Factory submitted all the documents to Alliance on Sep 09, 2016. In 3rd RVV report Alliance marked this issue status as 'completed' with the comment "This issue cover under DEA". Hence this issue is considered as 'corrected'. On 18/07/2018: Corrected in previous follow-up inspection. On 16/05/2019: Corrected in previous follow up inspection. On 17th Nov 2019: Corrected from previous inspection. On 25-Aug-2024: Corrected previously. DEA of the Main Building and Washing Building was re-accepted by BUET on 28-May-2019. The DEA of the Utility Building was accepted by BUET on 22-Apr-2018. As per the CCVV on 20-Nov-2018, the boiler shed was accepted by Alliance. Factory has demolished the Waste shed. On 23-Nov-2025: Previously corrected. On 04-Mar-2026: Previously corrected. | 25/02/2015 | Corrected
Initial Inspection |  | 5 | Ponding at Washing Building Roof (3rd Floor) Ponding at Utility Building Roof near Cooling Towers | Under guidance from a qualified structural engineer, address all areas of needed maintenance by correcting the identified issues. | We have done this | Feb 25 2015 | On 11/10.2015: This issue has been done. On 14/03/2017: This issue has been corrected in the previous follow up. Factory has been completed remediation work regarding roof ponding issue. On 28/11/2017: This issue has been corrected previously. On 18/07/2018: Corrected in previous follow-up inspection. No water ponding was observed. On 16/05/2019: Corrected in previous follow up inspection. Water ponding was not observed on roof. On 17th Nov 2019: Corrected from previous inspection. Factory has provided drainage slope on roof slab and during inspection no water ponding was found. On 25-Aug-2024: Corrected previously. On 23-Nov-2025: Previously corrected. On 04-Mar-2026: Previously corrected. | 25/02/2015 | Corrected
Initial Inspection |  | 6 | Building Code not identified | Provide letter from EOR indicating building code used for design | We have done this | Jan 3 2016 | On 11/10.2015: The factory management appointed an engineering firm to do DEA and this issue has been covered under this DEA. But that has not got any approval from alliance till the time of inspection. On 14/03/2017: This issue has been covered under DEA. Factory management submitted DEA to Alliance and which is under review. On 28/11/2017: Factory lead brand Levis conducted a DEA by BRTC BUET. Factory consultant (Prudential Consultants) has also conducted a DEA under BUET's supervision. Factory submitted all the documents to Alliance on Sep 09, 2016. In 3rd RVV report Alliance marked this issue status as 'completed' with the comment "This issue cover under DEA". Hence this issue is considered as 'corrected'. On 18/07/2018: Corrected in previous follow-up inspection. On 16/05/2019: Corrected in previous follow up inspection. On 17th Nov 2019: Corrected from previous inspection. DEA of this factory has been reviewed and re-accepted from BUET on 28th May 2019. On 25-Aug-2024: Corrected previously. On 23-Nov-2025: Previously corrected. On 04-Mar-2026: Previously corrected. | 25/02/2015 | Corrected
Initial Inspection |  | 7 | Factory Representative has noted that Floor Load Plans are in process of being developed. | Continue developing Floor Load Plans. | We have done this | Jan 3 2016 | On 11/10.2015: Load plan was prepared as a part of DEA and loading plan was posted on floors but that was not approved from alliance. On 14/03/2017: A set of load plan was produced and included in DEA. DEA was submitted to Alliance which is under review. Factory was required to maintain safe load (42psf). Overloading observed in washing building. The factory is suggested to reduce the load as per allowable limit. On 28/11/2017: Factory lead brand Levis conducted a DEA by BRTC BUET. Factory consultant has also conducted a DEA under BUET's supervision. Factory submitted all the documents to Alliance. In their 3rd RVV report alliance marked this issue status as 'In progress' . During inspection load plans were posted and loading was below load plan limit. This issue will be corrected after alliance marks this issue as 'completed'. On 18/07/2018: Loading was found below the load plan. Load management program has been implemented by load restriction height marking/signage, posting load plan, maintaining load register and appointing load manager. On 16/05/2019: Corrected in previous follow up inspection. Load plan had been prepared as a part of DEA. During inspection load plan was found posted to each floor and overall loading was found below the allowable accepted loading limit. On 17th Nov 2019: Corrected from previous inspection. Load plan has been produced and re-accepted as a part of DEA. On 25-Aug-2024: Corrected previously. During load plan was found posted on floors of the Main Building, Washing Building and Utility Building. The floor loading was within allowable limit of accepted load plan (Main Building- Storage 157.7psf, production area 84 to 157.7psf & Dormitory 63 psf. Washing Building- storage 105 psf, production area 42 to 63 psf, dining and office area 63 psf. Utility Building- storage 63 psf, office & dinning area 63 psf and prayer area 105 psf). On 23-Nov-2025: Previously corrected. On 04-Mar-2026: Previously corrected. | 25/02/2015 | Corrected
Initial Inspection |  | 8 | Seismic and Wind requirements not indicated on drawings | Provide letter from EOR indicating seismic and wind criteria used for design | We have done this | Jan 3 2016 | On 11/10.2015: The factory management appointed an engineering firm to do DEA and this issue has been covered under this DEA. But that has not got any approval from alliance till the time of inspection. On 14/03/2017: This issue is required to be covered in DEA. Factory management has submitted DEA report to Alliance and it is under reviewed. On 28/11/2017: Factory lead brand Levis conducted a DEA by BRTC BUET. Factory consultant (Prudential Consultants) has also conducted a DEA under BUET's supervision. Factory submitted all the documents to Alliance on Sep 09, 2016. In 3rd RVV report Alliance marked this issue status as 'completed' with the comment "This issue cover under DEA". Hence this issue is considered as 'corrected'. On 18/07/2018: Corrected in previous follow-up inspection. On 16/05/2019: Corrected in previous follow up inspection. On 17th Nov 2019: Corrected from previous inspection. DEA of this factory has been reviewed and re-accepted from BUET on 28th May 2019. On 25-Aug-2024: Corrected previously. Corrected previously. DEA of the Main Building and Washing Building was re-accepted by BUET on 28-May-2019. The DEA of the Utility Building was accepted by BUET on 22-Apr-2018. As per the CCVV on 20-Nov-2018, the boiler shed, Security house-1 & 2, Waiting room, steel stair, connection bridge, Ansar shed and ETP was accepted by Alliance. Factory has demolished the Waste shed. On 23-Nov-2025: Previously corrected. On 04-Mar-2026: Previously corrected. | 25/02/2015 | Corrected
Initial Inspection |  | 9 | Wind loading and storm surge loading requirements not indicated on drawings | Provide letter from EOR indicating wind loading and surge loading requirements used for design | We have done this | Jan 3 2016 | On 11/10.2015: The factory management appointed an engineering firm to do DEA and this issue has been covered under this DEA. But that has not got any approval from alliance till the time of inspection. On 14/03/2017: This issue is required to be covered in DEA. Factory management has submitted DEA report to Alliance and it is under reviewed. On 28/11/2017: Factory lead brand Levis conducted a DEA by BRTC BUET. Factory consultant (Prudential Consultants) has also conducted a DEA under BUET's supervision. Factory submitted all the documents to Alliance on Sep 09, 2016. In 3rd RVV report Alliance marked this issue status as 'completed' with the comment "This issue cover under DEA". Hence this issue is considered as 'corrected'. On 18/07/2018: Corrected in previous follow-up inspection. On 16/05/2019: Corrected in previous follow up inspection. On 17th Nov 2019: Corrected from previous inspection. DEA of this factory has been reviewed and re-accepted from BUET on 28th May 2019. On 25-Aug-2024: Corrected previously. On 23-Nov-2025: Previously corrected. On 04-Mar-2026: Previously corrected. | 25/02/2015 | Corrected
Initial Inspection |  | 10 | No Factory Load Manager has beeen designated | Designate a representative as the Factory Load Manager. The Factory Owner shall ensure that at least one individual, the Factory Load Manager who is located onsite full time at the factory, is trained in calculating operational load characteristics of the specific factory. The Factory Load Manager shall serve as an ongoing resource to RMG vendors and be responsible to ensure that the factory operational loads do not at any time exceed the factory floor loading limits as described on the Floor Loading Plans. | We have done this | Feb 25 2015 | On 11/10.2015: Load manager has been appointed. On 14/03/2017: This issue has been corrected in the previous inspection. Factory management has appointed a load manager. On 28/11/2017: Corrected on previous follow-up. On 18/07/2018: Corrected in previous follow-up inspection. Factory has appointed a load manager. On 16/05/2019: Corrected in previous follow up inspection. Factory management had appointed load manager. On 17th Nov 2019: Corrected from previous inspection. Load manager has been appointed and he was present during inspection. On 25-Aug-2024: Corrected previously. On 23-Nov-2025: Previously corrected. On 04-Mar-2026: Previously corrected. | 25/02/2015 | Corrected
Initial Inspection |  | 11 | Load Plans have not been prepared. Factory Representative noted that Loads Plans are in the process of being developed. | Have a qualified structural engineer develop Floor Loading Plans per the requirements of Part 8 Section 8.20.5.3 | We have done this | Jan 3 2016 | On 11/10.2015: Load plan was prepared as a part of DEA and loading plan was posted on floors but that was not approved from alliance. On 14/03/2017: A set of load plan was produced and included in DEA. DEA was submitted to Alliance which is under review. Factory was required to maintain safe load (42psf). Overloading observed in washing building. The factory is suggested to reduce the load as per allowable limit. On 28/11/2017: Factory lead brand Levis conducted a DEA by BRTC BUET. Factory consultant (Prudential Consultants) has also conducted a DEA under BUET's supervision. Factory submitted all the documents to Alliance on Sep 09, 2016. In 3rd RVV report Alliance marked this issue status as 'completed' . During inspection all floor loading were found below load plan limit(63 psf) and load plans were posted. Hence this issue is corrected. Hence this issue is considered as 'corrected'. On 18/07/2018: Corrected in previous follow-up inspection. Loading was found below the load plan. Load management program has been implemented by load restriction height marking/signage, posting load plan, maintaining load register and appointing load manager. On 16/05/2019: Corrected in previous follow up inspection. Load plan had been prepared as a part of DEA. During inspection load plan was found posted to each floor and overall loading was found below the allowable accepted loading limit. On 17th Nov 2019: Corrected from previous inspection. Load plan has been produced and re-accepted as a part of DEA. On 25-Aug-2024: Corrected previously. During load plan was found posted on floors of the Main Building and Washing Building. The floor loading was within allowable limit of accepted load plan (Main Building- Storage 157.7psf, production area 84 to 157.7psf & Dormitory 63 psf. Washing Building- storage 105 psf, production area 42 to 63 psf, dining and office area 63 psf). On 23-Nov-2025: Previously corrected. On 04-Mar-2026: Previously corrected. | 25/02/2015 | Corrected
Initial Inspection |  | 12 | Floor Load Plans have not yet been developed | Have a qualified structural engineer prepare load plans including the information required in Section 8.20 of the Alliance Standard. | We have done this | Jan 3 2016 | On 11/10.2015: Load plan was prepared as a part of DEA and loading plan was posted on floors but that was not approved from alliance. On 14/03/2017: A set of load plan was produced and included in DEA. DEA was submitted to Alliance which is under review. Factory was required to maintain safe load (42psf). Overloading observed in washing building. The factory is suggested to reduce the load as per allowable limit. On 28/11/2017: This issue status is 'corrected' following Alliance 3rd RVV report. During inspection all floor loading were found below load plan limit(63 psf) and load plans were posted. On 18/07/2018: Corrected in previous follow-up inspection. Loading was found below the load plan. Load management program has been implemented by load restriction height marking/signage, posting load plan, maintaining load register and appointing load manager. On 16/05/2019: Corrected in previous follow up inspection. Load plan had been prepared as a part of DEA. During inspection load plan was found posted to each floor and overall loading was found below the allowable accepted loading limit. On 17th Nov 2019: Corrected from previous inspection. Load plan has been produced and re-accepted as a part of DEA. On 25-Aug-2024: Corrected previously. During load plan was found posted on floors of the Main Building, Washing Building and Utility Building. The floor loading was within allowable limit of accepted load plan (Main Building- Storage 157.7psf, production area 84 to 157.7psf & Dormitory 63 psf. Washing Building- storage 105 psf, production area 42 to 63 psf, dining and office area 63 psf. Utility Building- storage 63 psf, office & dinning area 63 psf and prayer area 105 psf). On 23-Nov-2025: Previously corrected. On 04-Mar-2026: Previously corrected. | 25/02/2015 | Corrected
Initial Inspection |  | 13 | Floor Load Plans have not yet been prepared | Provide signage or the appropriate markings at all areas used for storage to indicate the acceptable loading limits detailed in the Load Plan. | We have done this | Jan 3 2016 | On 11/10.2015: Load plan was prepared as a part of DEA and loading plan was posted on floors but that was not approved from alliance. On 14/03/2017: .A set of load plan was produced and included in DEA. DEA was submitted to Alliance which is under review. Factory was required to maintain safe load (42psf). Overloading observed in washing building. The factory is suggested to reduce the load as per allowable limit. Load marking and signage were missing in some area. On 28/11/2017: This issue status is 'corrected' following Alliance 3rd RVV report. During inspection all floor loading were found below load plan limit(63 psf) and load plans were posted. On 18/07/2018: Corrected in previous follow-up inspection. Loading was found below the load plan. Load management program has been implemented by load restriction height marking/signage, posting load plan, maintaining load register and appointing load manager. On 16/05/2019: Corrected in previous follow up inspection. Load plan had been prepared as a part of DEA. During inspection load plan was found posted to each floor and overall loading was found below the allowable accepted loading limit. In addition, load restriction height marking was also observed. On 17th Nov 2019: Corrected from previous inspection. On 25-Aug-2024: Corrected previously. During inspection, load limit marking was found at storage areas. On 23-Nov-2025: Previously corrected. On 04-Mar-2026: Previously corrected. | 25/02/2015 | Corrected
Initial Inspection |  | 14 | No certificates of occupancy were available for review | Provide Certificates of Occupancy for review. | We have done this | Mar 21 2016 | On 11/10.2015: The factory management applied for occupancy certificate. On 14/03/2017: This is not applicable for Alliance. On 28/11/2017: Corrected on previous follow-up. On 18/07/2018: Corrected in previous follow-up inspection. N/A On 16/05/2019: Corrected in previous follow up inspection. Not applicable. On 17th Nov 2019: Corrected from previous inspection. On 25-Aug-2024: Corrected previously. On 23-Nov-2025: Previously corrected. On 04-Mar-2026: Previously corrected. | 25/02/2015 | Corrected
Follow Up Inspection |  | 15 | New Findings-1: Observation on DEA report & Analysis file. | Factory is required to recheck the observations made on DEA report & analysis file. | We have done this | Dec 3 2018 | On 18/07/2018: After reviewing the DEA documents and the analysis file the following observations are made: 1. Several columns are found overstressed. performing the analysis file named ""2018-02-26_ETABS_DENIMACH_MAIN BUILDING_010115 (Final)_Combine Main"" 2. 125 mm brick wall encasement suggested for the two overstressed columns due to Euler force. No calculation/reference was provided for that scheme. 3. The evaluated concrete strength was used f'c=4.5 ksi, however, the strength was calculated 4.15 ksi as per ACI 562 & 214R. 4. For slab deflection in Washing Building " Replacing toilet partition & inside 125mm brick wall by fiber insulation board or any other lightweight board" was suggested, but no remediation drawing was provided. The factory is required to recheck the observations and revise the documents and submit to Alliance. On 16/05/2019: During inspection it was found that factory management had prepared revised DEA documents which is not reviewed from BUET yet. So, factory is required to submit revised DEA documents (Based on Accord findings) to BUET for further review. On 17th Nov 2019: DEA of this factory has been reviewed and re-accepted from BUET on 28th May 2019. On 25-Aug-2024: Corrected previously. DEA of the Main Building and Washing Building was re-accepted by BUET on 28-May-2019. On 23-Nov-2025: Previously corrected. On 04-Mar-2026: Previously corrected. | Within 6-Weeks | Corrected
Follow Up Inspection |  | 16 | New Findings-2: New structures were found in the factory premises. Mismatches in drawings and lack of lateral stability along the long direction for the Acid Wash shed and Drum Wastage Shed. | Building engineer is required to suggest the remediation to for lateral load path and submit the safety check report for the both structure. | We will ensure the timeline. | Oct 24 2024 | On 25-Aug-2024: During inspection, new structures, Acid wash shed (140 sqm) and Drum wastage shed (186 sqm) were found in the factory premises. Some mismatches in as-built drawings were found for both shed with site condition. Also, the lateral load transfer media was not available for the structures. Building engineer is required prepare accurate as-built drawing for the Acid wash shed and Drum wastage shed. Also suggest the lateral load transfer media for the both structures and submit the structural safety check report to RSC for further review. Additionally, six more ancillary structures were found in the same premises: Connecting bridge (257 sqm), New Boiler Building (300 sqm), Oil & Lubricant Room (11 sqm), Equalization Tank (849 sqm), Isolated Toilet-1 (9.8 sqm) and Isolated Toilet-2 (5.8 sqm). The New ETP (3523 sqm) was under construction during the CCVV on 20-Nov-2018. As-built drawings were available for these structures and found satisfactory with as-built conditions. Progress Status: On 04-Mar-2026: The factory prepared a safety check report for the single-storied steel Acid Wash Shed and Drum Wastage Shed, which was accepted by RSC on 15 January 2026. The factory has completed all remediation works in accordance with the acceptance, and the quality control certificate was available on-site. | (within 6 weeks) | Corrected
Special | Post Incident | 17 | New Finding-3 (Post-Incident Inspection): Unidentified cracks in the beam & plaster cracks on the façade (Washing Building) | The factory must engage a consultant to investigate the cracks. Any safety measures, if required as suggested by the consultant, must be taken to ensure safety. The consultant is required to evaluate the extent of the cracks and repair as per the recommendation of the report. |  | Jan 4 2026 | On 23-Nov-2025: Unidentified cracks in the beam & plaster cracks on the façade were observed. The factory must engage a consultant to investigate the cracks. Any safety measures, if required as suggested by the consultant, must be taken to ensure safety. The consultant is required to evaluate the extent of the cracks and repair as per the recommendation of the report. On 04-Mar-2026: The factory has submitted the post-seismic investigation report on the cracks, as per the last review comments the factory is required to submit the revised report by 11 March 2026. The factory is required to complete the remedial works as per the recommendation of the accepted investigation report. However the factory carried out remedial works on the cracks. Progress Status: 60% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 18 | New Finding-4: Missing cross truss along the short direction (Existing Boiler Shed, 1200 sqft, Construction 2014) | Building engineer is required to check the requirements of the cross truss of the roof structure of the safety check report, submit documents to RSC for review, and carry out the remedial works as per the recommendation. |  | Apr 19 2026 | On 04-Mar-2026: During the inspection, a missing cross truss along the short direction was found on the existing Boiler Shed. Building engineer is required to check the requirements of the cross truss of the roof structure of the safety check report, submit documents to RSC for review, and carry out the remedial works as per the recommendation. | (within 6 weeks) | In Progress

## Fire
Date
31-Mar-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Denimach, Kewa Mouja, Ward No. 5, Gorgoria Masterbari, Sreepur, Gazipur, Dhaka
Date of Inspection |  | 2013-02-12
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | (1) There are three large air circulation shafts in the Main Building used for ventilation of the production floors. Fans along the outside wall draw fresh air into the building and the air returns to the outside through the air circulation shafts. The shafts have operable windows at each floor to modulate the air flow. While this design provides good air circulation, in a fire condition these shafts will enable smoke to be drawn throughout the entire building. (2) There are two freight elevators in the main building, one located adjacent to Stair 1 (West Exit Stair) and one located adjacent to Stair 2 (East Exit Stair). The elevator shaft openings have sliding grilles between the elevator shaft and the floor at each level. (3) There is a vertical shaft with electrical service and plumbing that proceeds through the building. This shaft is not enclosed in a fire-rated enclousure. | Provide vertical opening protection for the three ventilation shafts in the Main Building by means of roll down shutters that cover each of the window openings in each ventilation shaft. These shutters should be mounted on the “occupied” side of the ventilation shafts (for ease of resetting) and would normally be in the “open” position. Upon activation of any fire detection device in the main building, the fire alarm control panel should release these shutters so that they will automatically close. Provide each of the elevators in the Main Building and the Washing Building with elevator doors at each floor level that provide a 2-hour fire protection rating. Provide 2-hour fire resistive rating for all vertical shafts (primarily plumbing and electrical shafts). The protection means can either be at each floor penetration or by the provision of a fire rated shaft enclosure. | We have done this | Mar 1 2016 | On 10/11/2018: Corrected. Note: Few Door were kept open by external source in toilet area. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Refer to issue# 53 | Dec 31 2014 | Corrected
Initial Inspection |  | 2 | Windows from the building create exposure to the exterior exit stairs. | Provide required fire rated construction 10 ft beyond the ends of the exterior stairs. Enclose any openings (windows, etc.) with required fire rated construction within that 10 ft wall section. | We have done this | Mar 15 2016 | On 22/05/2018: Corrected. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 3 | The exit stairs have a combined exit width of 285 inches (7239 mm). Based on the BNBC requirement of 8mm/person for stairs, the maximum permitted occupant load per floor is calculated to be 904 persons. The population count on the north side of the 6th floor was reported to be slightly more than 600 occupants. Adding the population on the balance of the floor would exceed the occupancy load limit of the BNBC. | Limit the population of each floor to 904. Alternately, construct additional exit stairs to accommodate the occupant load. | We have done this | Mar 1 2016 | On 22/05/2018: Corrected. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 4 | Stair 3 (North Exit Stair) has an obstruction at the 1st level to the ground floor where a stair from the daycare center reduces the available exit width by nearly one-half. | Rearrange the stair from the daycare center to allow people coming down from upper floors to have full use of the width of the stair (the facility reports that a new stair is already planned for the daycare center). | We have done this | Mar 1 2016 | On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 5 | All doors were unrated. | Remove all existing gates and doors in the means of egress. Install fire doors at the stairs that and are listed, approved, swinging, automatic-closing, in compatible fire rated frames with latching panic hardware. | We have done this | Mar 1 2016 | On 22/05/2018: Corrected as per previous follow up inspections. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 6 | There is a manually operated roll-down shutter between the production floor and the stair opening at each stair landing. | Remove all existing doors and gates in the means of egress. Install side-hinged doors with approved hardware that swing in the direction of egress. | We have done this | Mar 1 2016 | On 22/05/2018: Removed. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 7 | Stairs 1, 2, and 3 discharge into the interior of the building. | Enclose the exit stairs in the Main Building and the Washing Building on each level such that once an occupant enters the stair enclosure they remain in a fire rated enclosure until they reach an exit discharge directly to the outside. Install rated exit access corridors to connect stairs to exterior discharge. | We have done this | Mar 1 2016 | On 22/05/2018: Corrected. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 8 | Stairs 1, 2, and 3 discharge into the interior of the building. | Enclose the exit stairs in the Main Building and the Washing Building on each level such that once an occupant enters the stair enclosure they remain in a fire rated enclosure until they reach an exit discharge directly to the outside. Install rated exit access corridors to connect stairs to exterior discharge. | We have done this | Mar 1 2016 | On 22/05/2018: Corrected. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 9 | Wall penetrations are not protected with firestop systems. | Install listed firestop systems at every penetration through fire rated walls and assemblies. | We have done this | Mar 1 2016 | On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 10 | No sprinkler system was installed. It was reported that an automatic sprinkler system is planned to be provided for the raw materials and finished goods areas on the ground floor. | Install automatic fire sprinkler systems throughout the facility. Manufacturing areas and storage less than 12 feet high is classified Ordinary Hazard (Group 2). Sprinkler systems should be designed to deliver 0.20 gpm/ft2 over the most remote 1500 square feet. 250 gpm hose allowance. 90 minute water supply duration. | All work is complete, and we are now awaiting final verification. | Jun 1 2016 | On 06/05/2021: Factory asked for timeline extension which is not acceptable. On 4-10-2021: T&CVI found that, final verification required. See the detailed T&CVI report. On 21/06/2022: Installation has been done. Pending for final verification. On 27/09/2023: Final verification inspection found the SUPS not approved. See the detailed FVI report. On 27-Sep-2023 the RSC checked the FADS/SUPS systems and identified anomalies. The anomalies need to be remediated and reported by factory management. On 20-Jan-2025: The Final verification inspection found the SUPS requires another final verification inspection. See the detailed FVI report. RPO Comments on 12-May-2025 : The factory is now ready for FVV inspection. The systems will be checked in the next inspection. | Dec 31 2014 | Pending Verification
Initial Inspection |  | 11 | Floor penetrations are not protected with firestop systems. | Install listed firestop systems at every penetration through floors. | We have done this | Mar 1 2016 | On 22/05/2018: Sealed. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 12 | Exit stairs in the factory building are open to all levels, with no fire rated separation. | Protect all egress stairs with a shaft enclosure including 2-hour fire-rated construction. Install fire rated doors. | We have done this | Mar 1 2016 | On 22/05/2018: Corrected as per previous follow up inspections. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 13 | There is a manual fire alarm system in the main building. The system is activated by push buttons located at the entry to the stairs. It was reported that the existing fire alarm system is planned to be replaced with a new manual fire alarm system and automatic smoke detection system. | Install fire alarm system per NFPA 72. Include pull stations at all entrances to exit stairs, at ground floor exits, and at the entry points to enclosed storage rooms. Install strobes and horns for complete notification on all floors. Install smoke detectors that are part of the fire alarm system in locations required by Alliance standards. Provide contact points for releasing of automatic hold-open devices for egress stair doors and building ventilation windows. | All work is complete, and we are now awaiting final verification. | Jun 1 2016 | On 6/05/2021: Factory informed that this issue is resolved but documents for pre-T&C are pending review. Progress status will be changed to PV when factory is determined to be ready for pre-T&C by RSC engineers On 4-10-2021: T&CVI found that, the system is not approved. See the detailed T&CVI report. Comments by RCH on 20/3/22: Factory asked for timeline extension which is not acceptable On 21/06/2022: Modification work almost done. Pending for final T&C. On 27/09/2023: T&CVI found that the fire alarm and detection system not approved. See detailed T&CVI report. On 20-Jan-2025: The T&CVI found that the fire alarm and detection system require final verification inspection. See detailed T&CVI report. RPO Comments on 12-May-2025 : The factory is now ready for FVV inspection. The systems will be checked in the next inspection. | Dec 31 2014 | Pending Verification
Initial Inspection |  | 14 | Production floors lack cross aisles increasing travel distance. The Washing Building includes several large open work areas with only one means of egress and dead ends in excess of 120 feet. | Cross aisles need to be added in the production floors (especially on floors 3 – 6) to assure workers have direct access to an exit. There are several areas in the production line that require workers to go well past an exit stair before being able to turn to the exit. Provide a second means of egress in areas of the washing building that only have one. | We have done this. | Mar 20 2016 | On 22/05/2018: After completing the sprinkler system installation/activation (T&C) this issue will be corrected. Found 400ft. on GF store during inspection. On 10/11/2018: In Progress in ground floor store area. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 15 | The facility has its own fire pump and cistern for fire protection water supply. | Design and install a listed, approved fire pump to supply the calculated demand of the new sprinkler and class I standpipe system, per NFPA 20. | All work is complete, and we are now awaiting final verification. | Jun 1 2016 | On 25/07/2019 factory asked for timeline extension which is not acceptable . On 31/10/2019: System fully installed and it was functional during inspection. During documents review we found some mismatched where factory will work and submit to us for review. 06/05/2021: Factory asked for timeline extension which is not acceptable. On 4-10-2021: T&CVI found that, final verification required. See the detailed T&CVI report. On 21/06/2022: Pending for final T&C verification. On 27/09/2023: Final verification inspection found the SUPS not approved. See the detailed FVI report. On 27-Sep-2023 the RSC checked the FADS/SUPS systems and identified anomalies. The anomalies need to be remediated and reported by factory management. On 20-Jan-2025: The Final verification inspection found the SUPS requires another final verification inspection. See the detailed FVI report. RPO Comments on 12-May-2025 : The factory is now ready for FVV inspection. The systems will be checked in the next inspection. | Dec 31 2014 | Pending Verification
Initial Inspection |  | 16 | The site contains fire hose stations around the buildings as well as fire hose cabinets within the building on each floor. | Install a Class I standpipe system in the building with fire department valves at the floor landings in each stair. The standpipe will be part of the combined standpipe/sprinkler system supply. | All work is complete, and we are now awaiting final verification. | Jun 1 2016 | On 31/10/2019: It is an integrated part of fire fighting system. System fully installed and it was functional during inspection. During documents review we found some mismatched where factory will work and submit to us for review. 06/05/2021: Factory asked for timeline extension which is not acceptable. On 4-10-2021: T&CVI found that, final verification required. On 21/06/2022: Pending for final T&C verification. On 27/09/2023: Final verification inspection found the SUPS not approved. See the detailed FVI report. On 20-Jan-2025: The Final verification inspection found the SUPS requires another final verification inspection. See the detailed FVI report. RPO Comments on 12-May-2025 : The factory is now ready for FVV inspection. The systems will be checked in the next inspection. | Dec 31 2014 | Pending Verification
Initial Inspection |  | 17 | There is a manually operated roll-down shutter between the production floor and the stair opening at each stair landing. These shutters are kept in the open position during working hours. After work hours the shutters are closed and locked. | Remove all existing gates and doors from the stairs and exits including all locking devices. Install approved fire doors with compliant panic hardware that cannot be locked in the direction of egress under any conditions. | We have done this | Mar 1 2016 | On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 18 | There are numerous locations throughout the property where trash is not properly stored. Such areas include combustible materials in stair landing and under exit stairs. | Permanently remove all storage, trash, foreign material and foreign equipment out of the stairs. Implement a housekeeping program to keep the stairs and egress paths free of storage and impediments. | We have done this | Mar 1 2016 | On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 19 | There are numerous locations throughout the property where trash is not properly stored. Such areas include combustible materials in stair landings and under exit stairs. The discharge for Stair 2 (East Exit Stair) has electrical switchgear located under the stair. | Remove all impediments, obstructions, and stored materials from the means of egress. Keep all elements of the means of egress (exit path, aisles, stairs, corridors, etc.) continuously free and clear of all obstructions. Permanently remove electrical equipment and all other foreign equipment from the stairs. | We have done this | Mar 1 2016 | On 22/05/2018: Removed. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 20 | No occupant load signs are posted. | Post the occupant load for all assembly and production floor areas in a conspicuous space near the main exit or exit access doorway for the space. | We have done this | Mar 1 2016 | On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 21 | Fire doors and approved hardware were not installed. | Install approved fire doors with latching panic hardware. Provide re-entry to floor levels from the stairwells according to the standard. | We have done this | Mar 1 2016 | On 22/05/2018: Corrected as per previous follow up inspections. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected as per previous follow-up inspection. Note: Fire doors have been installed at all required exits. Door accessories were found non-functional due to lack of maintenance in few location. Factory shall ensure that all required hardware and accessories has been replaced immediately to ensure the proper separation. | Dec 31 2014 | Corrected
Initial Inspection |  | 22 | Storage areas and hazardous areas are open to rest of building. | Separate storage and hazardous areas from the rest of the building with 1-hour fire-rated construction. Install fire rated doors. | We have done this | Mar 1 2016 | On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 23 | No central reporting system was installed. | Arrange for direct connection of the fire alarm and detection system to a central station monitoring service or the Fire Service and Civil Defense. Assign a person to contact the fire department in the event of fire alarm activation until this connection is set up. Locate an annunciator to alert this person in a constantly attended location (such as a fire control room). | All work is complete, and we are now awaiting final verification. | Jun 1 2016 | On 4-10-2021: T&CVI found that, the system is not approved. See the detailed T&CVI report. Comments by RCH on 20/3/22: Factory asked for timeline extension which is not acceptable On 21/06/2022: Modification work almost done. On 27/09/2023: T&CVI found that the fire alarm and detection system not approved. See detailed T&CVI report. RPO Comments on 22-Dec-2024 : The factory is now ready for T&CVI (FADS) & FVV (SUPS) inspection. The systems will be checked in the next inspection. On 20-Jan-2025: The T&CVI found that the fire alarm and detection system require final verification inspection. See detailed T&CVI report. RPO Comments on 12-May-2025 : The factory is now ready for FVV inspection. The systems will be checked in the next inspection. | Dec 31 2104 | Pending Verification
Initial Inspection |  | 24 | Combustibles are stored under the cutting tables. | Remove all storage from under cutting tables and similar obstructions. | We have done this | Mar 1 2016 | On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 25 | Handrails are installed only on one side of stairs. | Provide handrails on both sides of each stairway. Mount handrails at a height between 30 in. and 44 in. | We have done this | Mar 1 2016 | On 22/05/2018: Corrected as per previous follow up inspections. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 26 | Some emergency lights were installed. | Install emergency lighting for all paths of egress. Illumination needs to be a minimum of 10 lux for all corridors, exit doors and stairways. Illumination for aisles needs to be a minimum of 2.5 lux. | We have done this | Mar 1 2016 | On 22/05/2018: Corrected as per previous follow up inspections. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 27 | Exterior discharge uses ramps that do not have handrails and the slope exceeds the maximum slope for discharge. | Provide handrails on both sides of all ramps. Revise slope of ramp to not exceed a slope of 1 in 12. | We have done this | Mar 1 2016 | On 22/05/2018: Corrected. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 28 | Lighted exit signs are installed only at the exits. | Provide continuously illuminated exit signs. Signs shall be placed at all required exits and along egress paths, especially where there is a change in direction for the path of travel. | We have done this | Apr 1 2016 | On 22/05/2018: Corrected. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 29 | Stair designation signs were not posted. | Install signage adjacent to each stair door indicating the stair name and the floor level in both English and Bengali. | We have done this | Jul 31 2015 | On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 30 | There are numerous locations throughout the property where trash is not properly stored. Such areas include: Combustible materials in stair landing and under exit stairs. Combustible materials in equipment repair areas and adjacent to production areas | Improve housekeeping policies. Properly dispose of trash. Store combustibles only in rated store rooms. Clear congested areas. | We have done this | Mar 1 2016 | On 22/05/2018: Corrected as per previous follow up inspections. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Dec 31 2014 | Corrected
Follow Up Inspection |  | 31 | New Finding: Office area in bonded ware house. | Remove all office from store room. | We have done this | Apr 3 2016 | On 22/05/2018: Corrected. Penetrations have been sealed. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 32 | New Finding: Unsealed penetrations and openings are located in exit stair enclosures. Location: Building-1 lift control room. | Seal all penetrations and openings in the wall of exit enclosure walls (full thickness of the wall) by fire rated materials to maintain the fire resistance rating. | This issue has been resolved. | Apr 3 2016 | On 22/05/2018: Sealed. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Issue re-opened. Roof top floor elevator shaft has been found open to the exit enclosure. Location: Building 1, Stair 3. RPO Comments on 16-Jul-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 33 | New Finding: Width of aisles is less than 0.9m (36-in.) Location: Building-1 finishing section, Iron section and washing section. | Aisles shall be provided with a minimum unobstructed clear-width of 0.9 m (36 in.). | We have done this | Apr 3 2016 | On 22/05/2018: Corrected as per previous follow up inspections. Shall be maintained properly as per standard all over the premises. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected as per previous follow-up inspection. | Within 1 month | Corrected
Follow Up Inspection |  | 34 | New Finding: Areas used for in-process storage of combustible materials are open to the surrounding occupancy. Location: (building-1 cutting section and building-2 washing section) are not | Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. or 3. Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | We have done this | Apr 3 2016 | On 22/05/2018: Corrected. Pile dimension area is maintaining. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 35 | New Finding: Chemical storage area is not separated by fire-rated construction having non rated door and unsealed penetrations and openings. Location: Washing Section. | Separate the chemical storage room by 2-hr fire rated construction. Seal all penetrations and protect the openings to maintain the required fire separations. Keep 16-points MSDS of all chemicals in the storage area. ** As per BNBC, chemical storage room will be Type-1 construction. | We have done this | Apr 3 2016 | On 22/05/2018: Corrected as per previous follow up inspections. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 36 | New Finding: Factory has newly created the mazinine floor which is greater than 30 percent avobe of actual floor area. Location: Washing Section. | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. | We have done this | Apr 3 2016 | On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 37 | New Finding: Boiler or furnace room is not properly separated by fire rated construction with other Occupancies. | 1. Boilers or other heat producing equipment shall be separated from other occupancies by a minimum 1-hr (2-hr for highrise building) fire rated construction (wall, floor, slab etc). Seal all penetrations and openings (door, window etc.) should be protected by 0.75-hr (45 min) fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. Or Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. | We have done this | Apr 3 2016 | On 22/05/2018: Corrected. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 38 | New Finding: Rooms used for combustible storage in ground floor are not separated by fire-rated construction. Location: Washing Section & building-1. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. | We have done this | Apr 3 2016 | On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 39 | New Finding: Kitchen room is not separated by fire rated construction. Location: Washing building, South side. | Provide a minimum 2-hr fire-rated construction | We have done this | Apr 3 2016 | On 22/05/2018: Corrected as per previous follow up inspections. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 40 | New Finding: Dining room is not separated by fire rated construction. Location: Washing building, South side. | Provide a minimum 2-hr fire-rated construction and direct excess to exit stair. | We have done this | Apr 3 2016 | On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 41 | New Finding: Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | We have done this | Apr 3 2016 | On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 42 | New Finding: Inspection, testing, and maintenance for the fire extinguisher system is not in accordance with NFPA 10 or as per Accord standard. | Inspect, test and maintain the potable fire extinguisher system, and keep written records on-site, in accordance with NFPA 10 or as per Accord standard. | We have done this | Apr 3 2016 | On 22/05/2018: Maintaining. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 43 | New Finding: The required standpipe system is not installed in accordance with the ACCORD standard. | Install a new standpipe system in accordance with ACCORD standard 5.4 and NFPA 14. A class III system shall be installed in buildings with the highest occupiable floor 10 m (33 ft.) above grade or more. A class I system shall be permitted in buildings protected throughout by an approved automatic sprinkler system. | All work is complete, and we are now awaiting final verification. | Jul 3 2016 | On 31/10/2019: System fully installed and it was functional during inspection. During documents review we found some mismatched where factory will work and submit to us for review. 06/05/2021: Factory asked for timeline extension which is not acceptable. On 21/06/2022: Pending for final T&C verification. On 27/09/2023: Final verification inspection found the SUPS not approved. See the detailed FVI report. On 20-Jan-2025: The Final verification inspection found the SUPS requires another final verification inspection. See the detailed FVI report. RPO Comments on 12-May-2025 : The factory is now ready for FVV inspection. The systems will be checked in the next inspection. | within 4 months | Pending Verification
Follow Up Inspection |  | 44 | New Finding ( 3rd Follow up): Electrical DB located in the exit stair of ground floor. | Electrical DB shall be separated from other occupancies by a minimum 2-hr fire rated construction (wall, floor, slab etc.). Seal all penetrations and openings (door, window etc.) should be protected by 1.5 -hr fire rated materials to maintain the fire separation if required. | This issue has been resolved. | Jun 14 2017 | On 10/11/2018: Corrected. Note: Horizontal BBT need to separate properly from stair 3. On 28/05/2019: Corrected. BBT has been separated from stair. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Issue re-opened. Electrical DB board has been found separated by fire rated access panel on the stair encloser but the horizontal cables has not been separated yet, Location- Stair-3 (B#1). Moreover, factory shall ensure the credibility of the installed gypsum board to separate the horizontal BBT on Stair- 2 of B#1 through proper listing labeling. RPO Comments on 16-Jul-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 month | Pending Verification
Follow Up Inspection |  | 45 | New Finding ( 3rd Follow up): The exterior exit stair using for Dinning room & Prayer room is not separated from the Cooling tower building. Location: Utility building 1st floor. | Exterior exit stairs shall be separated by minimum 1-hr fire-rated construction and The rating of the exterior wall shall extend 3.05 m (10 ft.) beyond the ends of the stair structure. Provide minimum .75-hr fire rated doors to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing, positive latching and that they are provided with fire exit (panic) hardware where serving production floors. | We have done this | Jun 14 2017 | On 22/05/2018: Corrected. On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Within 3 month | Corrected
Follow Up Inspection |  | 46 | New Finding ( 3rd Follow up): Collapsible doors have provided along means of egress of Cargo lift room. | Replace all collapsible/sliding/shutter type doors & gates by the side‐hinged swinging type doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | We have done this | Mar 20 2017 | On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 47 | New Finding (5th Follow Up): Inspection, testing, and maintenance for the fire detection system is not in accordance with NFPA 72. | Inspect, test and maintain the fire detection system, and keep written records on-site, in accordance with NFPA 72. | We have done this | Dec 19 2017 | On 19/11/2017: New Finding. On 22/05/2018: Corrected. Maintaining. On 10/11/2018: Corrected. On 28/05/2019: Corrected. Shall follow the table14.3.1 of NFPA-72. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 48 | New Finding (5th Follow Up): Inspection, testing, and maintenance of the automatic sprinkler system is not in accordance with NFPA 25. | Inspect, test and maintain the automatic sprinkler system, and keep written records on-site, in accordance with NFPA 25. | We have done this | Dec 19 2017 | On 28/05/2019: Maintaining for the existing system. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 49 | New Finding (5th Follow Up): Inspection, testing and maintenance of the fire pump system is not in accordance with NFPA 20. | Inspect, test and maintain the fire pump system and keep written records on-site, in accordance with NFPA 20 and ACCORD standards. | We have done this | Dec 19 2017 | On 28/05/2019: Maintaining for the existing system. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 50 | New Finding (5th Follow Up): Inspection, testing and maintenance of the standpipe system is not in accordance with NFPA 14. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 14 and ACCORD standards. | We have done this | Dec 19 2017 | On 10/11/2018: Corrected. On 28/05/2019: Corrected. On 31/10/2019: Corrected. On 21/06/2022: Corrected. On 27/09/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 51 | New finding (11th FUI): Fire evacuation maps is not posted at the entrance of required exit stair. Location:Building-1, Roof top floor | Fire evacuation maps shall be posted at the entrance to each required exit stair. | This issue has been resolved. | Oct 27 2023 | On 27/09/2023: New Finding. RPO Comments on 16-Jul-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 52 | New finding (11th FUI): Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. Location: Washing building (3rd floor), Boiler shed, New boiler building, Ansar shed, Drums shed, ETP building(1st Floor). | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | This issue has been resolved. | Oct 27 2023 | On 27/09/2023: New Finding. RPO Comments on 16-Jul-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 53 | New Findings (11th FUI): Floors are not separated from each others on the Atrium due to non functional hardware and accessories of the fire rated window. Magnetic holder has been found non functional on several location. Location: Building-1 | Atrium shall be separated from the adjacent spaces with fire resistive separation of at least 1-hr. [Section 3.7.4 of RSC Technical Guidelines (Standard) V1.0] Fire windows may be provided in fixed glazed openings when the window has a fire resistive rating of at least 0.75-hr and the area of the opening does not exceed 25 percent of the wall common to the atrium and the room into which the opening is provided. When fire rated window is installed, factory shall ensure that all the hardware and accessories of fire rated windows are functional properly so that the separation has been ensured. | This issue has been resolved. | Dec 27 2023 | On 27/09/2023: New Finding. RPO Comments on 16-Jul-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification

## Electrical
Date
31-Mar-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Denimach, Kewa Mouja, Ward No. 5, Gorgoria Masterbari, Sreepur, Gazipur, Dhaka
Date of Inspection |  | 2014-06-24
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Workers that operate and maintain the electrical system have not received electrical safety training. | Develop and implement an electrical safety program. Include key topics such as lock out tag out procedures, personal protective equipment requirements, etc. Reference NFPA 70e for example program requirements. |  | Jul 31 2015 | Corrected at 1st follow-up inspection. | Aug 20 2014 | Corrected
Initial Inspection |  | 2 | Distribution boards are metal enclosed without dead front construction. | Ensure distribution boards are metal enclosed with a dead front construction. |  | Dec 30 2015 | Corrected at 2nd follow-up inspection. | Jul 23 2014 | Corrected
Initial Inspection |  | 3 | Emergency power switchboards, distribution boards, and circuits are not properly identified. | Ensure proper identification of emergency power switchboards, distribution boards, and circuits. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Jul 23 2014 | Corrected
Initial Inspection |  | 4 | Combustible materials are stored within the substation room. There is a wooden table inside the LT Panel room. | Remove all combustible materials within the substation room. |  | Feb 25 2015 | Corrected at 1st follow-up inspection. | Jun 25 2014 | Corrected
Initial Inspection |  | 5 | Light fixtures without protective covers are installed in storage areas. | Ensure light fixtures without protective covers are not installed in storage areas or in any area where the Inspector of the Factories Rules (1.5.3.5) Part 53 disallows these fixtures. |  | Feb 25 2015 | Corrected at 1st follow-up inspection. | Jun 25 2014 | Corrected
Initial Inspection |  | 6 | Not all metal in the building is connected to the building earthing system. | Connect all metal in the building to the building earthing/grounding system such as metal rebar in concrete, metal frame of building, or metal water pipe. |  | Feb 25 2015 | Corrected at 1st follow-up inspection. | Aug 20 2014 | Corrected
Initial Inspection |  | 7 | It was not possible to verify the appropriate oil level of the transformer because it is located at an inaccessible height. | Verify and ensure that wet type transformer is not leaking and have appropriate oil levels. |  | Sep 30 2015 | Corrected at 1st follow-up inspection as Not applicable. | Aug 20 2014 | Corrected
Initial Inspection |  | 8 | Distribution boards are not provided with adequate clearance. | Provide clearance of at least 1 m (39 in) in front of distribution boards. |  | Feb 25 2015 | Corrected at 1st follow-up inspection. | Jul 23 2014 | Corrected
Initial Inspection |  | 9 | Distribution board is not installed in compliant location (access bared). | Install distribution boards in compliant locations so that operation is not hampered due to limited access. |  | Jul 31 2015 | Corrected at 1st follow-up inspection. | Aug 20 2014 | Corrected
Initial Inspection |  | 10 | Electrical cables are not sized according to capacity of circuit breakers. | Consult with a qualified Electrical Engineer and ensure electrical cables are sized according to capacity of circuit breakers. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Aug 20 2014 | Corrected
Initial Inspection |  | 11 | Multi looping of cables observed at circuit breakers within distribution boards. | Remove multi looping of cables at circuit breakers within distribution boards. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Aug 20 2014 | Corrected
Initial Inspection |  | 12 | Indications of overheating were observed at some locations during thermography. | Find out cause of overheating and take proper action including replacing cable or equipment where necessary. |  | Apr 10 2016 | On 14/03/2017: Corrected. Not found this time. | Jun 25 2014 | Corrected
Initial Inspection |  | 13 | Distribution boards are not provided with physical means to prevent the installation of more over current devices. | Ensure distribution boards provided with physical means to prevent the installation of more over current devices than that number for which the panel board was designed, rated, and listed following NFPA 70 section 408.54. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Aug 20 2014 | Corrected
Initial Inspection |  | 14 | Electrical cables are not properly identified. | Ensure the means of identification is obtained by separate colour coding, marking tape, tagging, or other approved means. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Aug 20 2014 | Corrected
Initial Inspection |  | 15 | Distribution boards do not have capacity information labels. | Provide capacity information labels (Maximum current rating, no of circuit breakers etc.) for distribution boards. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Aug 6 2014 | Corrected
Initial Inspection |  | 16 | No periodic safety inspections of the electrical system components are completed. | Establish a periodic inspection program to ensure the electrical systems are free from damage, debris, dirt, lint, etc. Maintain records concerning inspections and follow up actions. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Aug 20 2014 | Corrected
Initial Inspection |  | 17 | Power and telecommunication or antenna cables are not led in separately. | Lead telecommunication or antenna cables separately to the main point of service. Power and telecommunications cables must have separate entrance. |  | Dec 30 2015 | Telecommunication or antenna cables are not led in separate conduits. | Aug 20 2014 | Corrected
Initial Inspection |  | 18 | Thermo graphic scans of electrical equipment have not been completed. | Complete thermo graphic scans at least on a three year cycle. |  | Jan 31 2016 | Last thermo graphic inspection was conducted on December 02, 2015. Next inspection will be due on June 2016. | Aug 20 2014 | Corrected
Initial Inspection |  | 19 | Any report regarding the PCB content is not available on site therefore no confirmation can be obtained that the transformers do not contain harmful substances. | Consult with transformer manufacturing company to ensure that the transformer do not contain any harmful substance. For PCB containment report and consider replacing transformer that contain harmful substances such as PCBs. |  | Sep 30 2015 | Corrected at 1st follow-up inspection. | Aug 20 2014 | Corrected
Initial Inspection |  | 20 | Cable sockets are not provided for stranded conductors. | Provide cable sockets for stranded conductors having a nominal cross-sectional area 6mm2 or greater. And Conductors below 6 mm2 without cable sockets, all strands at the exposed ends are soldered together or are crimped using suitable sleeve or ferrules. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Aug 6 2014 | Corrected
Initial Inspection |  | 21 | Each circuit is not provided with a dedicated neutral. | Provide dedicated neutral for each circuit. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Aug 20 2014 | Corrected
Initial Inspection |  | 22 | There is no lightning protection system layout diagram to confirm that the air termination network of vertical conductors are appropriate. | Consult a qualified electrical engineer to prepare a proper lightning protection system layout diagram and ensure the air termination network of vertical conductors are appropriately spaced. |  | Apr 10 2017 | On 14/03/2017: Corrected. On 26/11/2018: Very few air terminals are found to be located at more than 2ft away from the edge. In the main building, the bonding connections are there but requires welded joint at few locations where existing joints are inappropriate. | Aug 6 2014 | Corrected
Initial Inspection |  | 23 | The lightning protection ground terminals are not bonded to the building or structure grounding. | Ensure the lightning protection ground terminals are bonded to the building or structure grounding as per Alliance Standards Part 10 Section 10.11 Lightning Protection. |  | Apr 10 2017 | On 14/03/2017: Corrected. | Aug 6 2014 | Corrected
Initial Inspection |  | 24 | There is no lightning protection system layout diagram to confirm that the number of down conductors appropriate. | Consult a qualified electrical engineer to prepare a lightning protection system layout diagram and ensure the number of down conductors appropriate based on building size. |  | Apr 30 2017 | On 14/03/2017: Corrected. | Aug 6 2014 | Corrected
Initial Inspection |  | 25 | Improper cable joints were found. | Ensure cable joints through porcelain or PVC connectors with PIB tape wound around joint. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Aug 20 2014 | Corrected
Initial Inspection |  | 26 | Improper insulation resistance measurement because the outgoing circuit breaker rating and the cable size is not mentioned. | Develop an Insulation Resistance Measurement Program that ensures deterioration of insulation resistance will be identified quickly. Testing should be in compliance with International Electrical Testing Association (NETA). |  | Jun 30 2015 | Corrected at 1st follow-up inspection. Last test was conducted on January 2015. Next test will be due on January 2017. | Aug 20 2014 | Corrected
Initial Inspection |  | 27 | Distribution boards are not clean. | Ensure distribution boards free of dirt. |  | Dec 31 2015 | Corrected at 2nd follow-up inspection. | Jul 23 2014 | Corrected
Initial Inspection |  | 28 | The distribution boards are not properly earthed. | Ensure distribution panel doors are earthed. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Aug 20 2014 | Corrected
Initial Inspection |  | 29 | Distribution boards have no clear identification markings. | As per BNBC section 2.11.5.4 ensure clear and permanent identification marks are painted in all distribution boards, switchboards, sub main boards and switches. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Jul 23 2014 | Corrected
Initial Inspection |  | 30 | No mechanical guards are provided for electrical equipment where necessary. | Provide mechanical guards for electrical equipment where necessary. |  | Dec 31 2015 | Corrected at 2nd follow-up inspection. | Jul 23 2014 | Corrected
Initial Inspection |  | 31 | Unterminated cables are found in distribution boards. | Ensure all electrical cable properly terminated at its point of termination. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Aug 20 2014 | Corrected
Initial Inspection |  | 32 | Electrical wiring is not properly supported. Location: Generator Room, Utility Building. | Provide adequate supports for electrical wiring and conduit. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Aug 20 2014 | Corrected
Initial Inspection |  | 33 | No signage indicating the prohibition of light fixtures without protective covers is installed at required locations. | Light fixtures without protective covers shall not be allowed in storage areas or in any area where the Inspector of the Factories Rules (1.6.3.7) Part 53 disallows these fixtures. Install signs posted in Bengali and English, indicating this prohibition at all entrances to these areas. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Jul 23 2014 | Corrected
Initial Inspection |  | 34 | Inspection, maintenance, and testing procedures of the IPS have not been completed and documented. | Establish an inspection testing, and maintenance program for the Instant Power Supply (IPS) and associated components. The program must based on the following: (1) Manufacturer's recommendations (2) Manufacturer's instruction manuals (3) Minimum Requirements of NFPA 111 Chapter 8 (4) Minimum Requirements of NFPA 70B Chapter 28. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Aug 20 2014 | Corrected
Initial Inspection |  | 35 | Required equipment and safety signage is not posted within the room. | Ensure required equipment and safety signage is posted within the room. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Jul 23 2014 | Corrected
Initial Inspection |  | 36 | Phase separators are not provided between terminals on circuit breakers. | Install phase separators between terminal connections at the noted locations. |  | Jun 30 2015 | Corrected at 1st follow-up inspection. | Aug 6 2014 | Corrected
Follow Up Inspection |  | 37 | New Finding: Light in store room / storage areas is uncovered. | Lights in store room / storage areas shall be covered. |  | May 10 2016 | On 14/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly. | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. |  | Apr 30 2017 | On 14/03/2017: Not corrected. Time extension is given till 30/04/2017. On 19/06/2017: Corrected. Oversized circuit breaker was not found during inspection period. | 2 Months | Corrected
Follow Up Inspection |  | 39 | New Finding: Safety program is initiated but has no influence. | Electrical safety training and awareness program for the electrical personal and workers needs be conducted frequently and recorded. After the training, there should be exam to evaluate the influence of the training program. |  | Apr 30 2017 | On 14/03/2017: Not corrected. Time extension is given till 30/04/2017. On 19/06/2017: Not corrected. On 19/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: Cable duct/ channels are filled with fluffs (Lint/dust). | Clean all the cable channels/ducts; then seal them for permanent (you may use checkered/ perforated plate at the bottom). But ensure that you have used proper sized cable for all of your electrical loads. |  | Apr 30 2017 | On 14/03/2017: Not corrected. Time extension is given till 30/04/2017. On 19/06/2017: Not corrected. On 19/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Air terminal is missing at some points, Air terminal installation at the outmost. Cross-run conductor exceed (150X50)' ft. mesh. | Missing Air Terminals shall be reinstalled. Cross-run conductor must not exceed (150X50)' ft. mesh. |  | Jul 31 2017 | On 19/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Renovation work doesn't reflect on SLD. | Electrical SLD must be updated properly; all the required information must be mentioned there; and it shall be updated when you do substantial amount of changes of your electrical system. |  | Jul 31 2017 | On 19/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Panel base plates are removed to allow cable entry. | Panel base plates must be installed, at all time, and cables entering panel must be firmly fixed with cable gland. |  | Jul 31 2017 | On 19/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. |  | Jul 31 2017 | On 19/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Lights in the store room / storage areas are uncovered/unprotected. | Lights in the store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. And a secure cabling shall be ensured. |  | Jul 31 2017 | On 19/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Haphazard wiring at the service room at utility building. | Need to arrange the wiring and fasten with supports where required. Cables shall not be laid on floor without supports. |  | Dec 20 2018 | On 06/05/2019: Not Corrected. Work in progress. On 31/10/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. |  | Dec 15 2019 | On 27/09/2023: Not Corrected. Still found in several places. On 27/03/2024: Not corrected. Progress has been observed. But still found in Main Building (SDB-1/2, MDB-4th Floor/CB-3), Wash Building (SDB-3.1/Busbar, SDB-9.1/CKT-38), Utility Building (Compressor DB, DB-12, LT panel) etc. Factory is working on this issue. RPO Comments on 22-Dec-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 22/10/2025: Corrected. Hotspot not found during inspection. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. |  | Dec 3 2023 | On 27/03/2024: Not corrected. Factory is preparing their as-built SLD to submit to RSC for review. On 22/10/2025: Not Corrected. SLD is undergoing a review process & Current status of SLD is Need Modifications. RPO Comments on 23-Feb-2026 : The design documents (SLD) have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design. | 2 Months | In Progress
Follow Up Inspection |  | 49 | New Finding: PVC pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. |  | Nov 3 2023 | On 27/03/2024: Not corrected. Progress has been observed. Factory remediated this issue from almost every storage area. But still found in Washing Building/2nd Floor/Laser section. Cable tray was observed here without any cover. Besides, some electrical installation, i.e. Power socket, breaker box was found adjacent to the materials On 22/10/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Distribution Board's top/bottom/front door is left open (typical issue). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. |  | Nov 3 2023 | On 27/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Grounded(neutral) conductor is used for equipment earthing. | A grounded conductor shall not be connected to normally non–current carrying metal parts of equipment, to the equipment grounding conductor(s), or be reconnected to ground on the load side of the service disconnecting means. |  | May 2 2024 | On 22/10/2025: Not Corrected. Found at few panels. RPO Comments on 23-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 52 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Ensure that any heat source (or steam line) is kept at least 0.9 meters away from any electrical installation. If unavoidable, the heat source must be covered with a suitable insulator. |  | Nov 22 2025 | RPO Comments on 23-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress

## Boiler
Date
31-Mar-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Denimach, Kewa Mouja, Ward No. 5, Gorgoria Masterbari, Sreepur, Gazipur, Dhaka
Date of Inspection |  | 2022-01-30
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 4805 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | We have done this work. Emergency Stop swich installed control panel and boiler room entrance door | Apr 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 4458 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | We have done this work. Emergency Stop swich installed control panel and boiler room entrance door | Apr 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 4804 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | We have done this work. Emergency Stop swich installed control panel and boiler room entrance door | Apr 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 6339 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | We have done this work. Emergency Stop swich installed control panel and boiler room entrance door | Apr 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 13632 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | We have done this work. Emergency Stop swich installed control panel and boiler room entrance door | Apr 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 4805 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can bevisualized and identified clearly. | We have done this work. Low Low water Level Marked properly. | Apr 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 4458 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have done this work. Low Low water Level Marked properly. | Apr 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 4804 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have done this work. Low Low water Level Marked properly. | Apr 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 6339 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have done this work. Low Low water Level Marked properly. | Apr 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 13632 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have done this work. Low Low water Level Marked properly. | Apr 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 13632 | Inconsistency was observed between the nameplate data and the CIoB provided certificate copy for the boiler regarding serial number | Information provided in the nameplate and in the CIoB provided certificate shall be consistent. Any alteration shall be approved from the CIoB and a copy to be preserved on site. | We are working on Boiler office to correction Name plate data as per CLoB provided certificate. | Apr 18 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 12 | BB 4805 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Necessary document are available for Boiler operation. | Apr 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 13 | BB 4458 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Necessary document are available for Boiler operation. | Apr 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 14 | BB 4804 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We are Woking on electrical Drawing and others Necessary document are available for Boiler operation. | Apr 18 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 15 | BB 6339 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Necessary document are available for Boiler operation as per Boiler Depatment . | Apr 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 16 | BB 4805 | Boiler Steam Header Safety Valve outlet line was not directed outside of the boiler room. | Steam Header Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | We have done this work. Boiler Steam Header Safety Valve outlet line was directed outside of the boiler room. | Mar 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 17 | BB 4458 | Boiler Steam Header Safety Valve outlet line was not directed outside of the boiler room. | Steam Header Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | We have done this work. Boiler Steam Header Safety Valve outlet line was directed outside of the boiler room. | Mar 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 18 | BB 4804 | Boiler Steam Header Safety Valve outlet line was not directed outside of the boiler room. | Steam Header Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | We have done this work. Boiler Steam Header Safety Valve outlet line was directed outside of the boiler room. | Mar 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 19 | BB 13632 | Boiler Steam Header Safety Valve outlet line was not directed outside of the boiler room. | Steam Header Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | We have done this work. Boiler Steam Header Safety Valve outlet line was directed outside of the boiler room. | Mar 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 20 | BB 4804 | A boiler with a height of 8 feet or more was observed with an inadequate platform and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet and a railing with a minimum height of 3.5 feet should be provided. | We have done this work. An .aduquate platform and railing have made for safely boiler operation. | Apr 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 21 | BB 13632 | Boiler body was found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | We have done this work.Boiler body insullation work has completed.. | Mar 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 22 | BB 13632 | Boiler exhaust gas pipeline inside the boiler room was found with improper insulation. | Proper insulation to boiler exhaust gas pipeline inside the boiler room causing heat exposure for personnel shall be provided. | We have done this Work. Properly insulation on Exhaust pipeline. | Mar 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 23 | BB 13632 | Valves were observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. | We Have done this work. Valves were removed between the boiler and the pressure controller. | Mar 4 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 24 | BB 4458 | Salt and scale formation was observed on the waterside on fire tubes (medium hard nonuniformly distributed with 1.5 to 2 mm thickness). | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | We have done this work. We are using chemical Removed Scale and salt continiously. | Mar 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 25 | BB 13632 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have done this work. The steam pressure limiter have installed. | Apr 18 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | Functional test inspection | 26 | BB 13632 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We have done this work. Now The Low Low Water (LLW) level tripping mechanism should be functional. | Feb 25 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 1 WEEKS | Pending Verification