## Structural
Date
30-Jun-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | EMON Fashion Ltd., 42,Mariyali , Joydebpur , Gazipur J2, Gazipur
Date of Inspection |  | 2018-06-07
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Discrepancies between provided drawing and on site condition. | Factory Engineer is required to prepare As –Built drawings reflecting the actual condition. | Corrected | Sep 18 2018 | On 20th-Jan-2019: As-built drawing has been produced and accepted from Accord on 13th Dec 2018. During inspection no discrepancy was found between as-built drawing and as-built condition. On 12th June 2019: Corrected from previous inspection. As-built drawing has been produced and accepted from Accord on 13th Dec 2018. On 24-Sep-2023: Corrected previously. On 01-Feb-2024: This issue was corrected from previous inspection. On 17-Oct-2024: Corrected previously. The as-built drawing of the RMG Building was accepted from ACCORD on 13-Dec-2018. On 16-Feb-2026: Previously corrected. | Within 06 Week | Corrected
Initial Inspection |  | 2 | Water ponding/clogging on roof slab. | Factory is required to provide proper drainage system and water proofing on roof slab. | Corrected | Sep 18 2018 | On 20th-Jan-2019: During inspection it was observed that water proofing work was ongoing. Factory is required to complete the water proofing work. On 12th June 2019: During inspection it was observed that factory has provided proper drainage system and water proofing on roof slab. No water ponding was found. On 24-Sep-2023: Corrected previously. During inspection, water proofing was observed and no standing water was found. On 01-Feb-2024: This issue was corrected from previous inspection. On 17-Oct-2024: Corrected previously. During inspection, the roof drainage system was found to have improved & no water clogging was found on the roof of the RMG Building. On 16-Feb-2026: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 3 | Lack of documentation and lateral stability for Office building. | Factory Engineer to review design, loads, columns and footings stresses. | Corrected | Sep 18 2018 | On 20th-Jan-2019: Factory has decided to demolish the structure and provided a written document regarding this issue. On 12th June 2019: Corrected from previous inspection. Factory has demolished Office building. On 24-Sep-2023: Corrected previously. The office building has already been demolished. On 01-Feb-2024: This issue was corrected from previous inspection. On 17-Oct-2024: Corrected previously. The factory demolished the Office Building. On 16-Feb-2026: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 4 | Lack of documentation and lateral stability for Office building. | Verify in-situ concrete strength and aggregate type by taken min. 4 nos. 100mm dia. core samples from ground floor columns. | Corrected | Sep 18 2018 | On 20th-Jan-2019: Factory has decided to demolish the structure and provided a written document regarding this issue. On 12th June 2019: Corrected from previous inspection. Factory has demolished Office building. On 24-Sep-2023: Corrected previously. The office building has already been demolished. On 01-Feb-2024: This issue was corrected from previous inspection. On 17-Oct-2024: Corrected previously. The factory demolished the Office Building. On 16-Feb-2026: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 5 | Lack of documentation and lateral stability for Office building. | The Detailed Engineering Assessment to be completed. | Corrected | Sep 18 2018 | On 20th-Jan-2019: Factory has decided to demolish the structure and provided a written document regarding this issue. On 12th June 2019: Corrected from previous inspection. Factory has demolished Office building. On 24-Sep-2023: Corrected previously. The office building has already been demolished. On 01-Feb-2024: This issue was corrected from previous inspection. On 17-Oct-2024: Corrected previously. The factory demolished the Office Building. On 16-Feb-2026: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 6 | Lack of documentation and lateral stability for Office building. | Produce and actively manage a loading plan for all floor plates within the factory, giving consideration to floor, column and foundation capacity. | Corrected | Sep 18 2018 | On 20th-Jan-2019: During inspection, the office building was found vacant. On 12th June 2019: Corrected from previous inspection. Factory has demolished Office building. On 24-Sep-2023: Corrected previously. During inspection, the office building was found demolished. On 01-Feb-2024: This issue was corrected from previous inspection. On 17-Oct-2024: Corrected previously. The factory demolished the Office Building. On 16-Feb-2026: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 7 | Lack of documentation and lateral stability for Office building. | Complete implementation of any remedial works deemed necessary by the DEA. | Corrected | Feb 7 2019 | On 20th-Jan-2019: During inspection it was observed that demolition work was on-going. On 12th June 2019: During inspection Office building was found demolished. On 24-Sep-2023: Corrected previously. The office building has already been demolished. On 01-Feb-2024: This issue was corrected from previous inspection. On 17-Oct-2024: Corrected previously. The factory demolished the Office Building. On 16-Feb-2026: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 8 | Lack of documentation and lateral stability for Office building. | Continue to implement loading plan. | Corrected | Feb 7 2019 | On 20th-Jan-2019: During inspection, the office building was found vacant. On 12th June 2019: Corrected from previous inspection. Factory has demolished Office building. On 24-Sep-2023: Corrected previously. The office building has already been demolished. On 01-Feb-2024: This issue was corrected from previous inspection. On 17-Oct-2024: Corrected previously. The factory demolished the Office Building. On 16-Feb-2026: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 9 | Non engineer shed to be replaced (Utility-1, Shed-1). | Demolish the non engineered shed. | Corrected | Sep 18 2018 | On 20th-Jan-2019: During inspection it was observed that factory has demolished all the ancillary sheds. (Factory has demolished the sheds of south side and will send pictorial evidence after demolishing the sheds at north side near main gate) On 12th June 2019: Corrected from previous inspection. During inspection those sheds were found demolished. On 24-Sep-2023: Corrected previously. On 01-Feb-2024: This issue was corrected from previous inspection. On 17-Oct-2024: Corrected previously. The factory demolished the Utility-1 & Shed-1. On 16-Feb-2026: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 10 | Non engineer shed to be replaced (Utility-1, Shed-1). | Replace the non engineered structure by an engineered structure. | Corrected | Feb 7 2019 | On 20th-Jan-2019: Factory has no plan to construct new shed for utility purpose. During inspection it was observed that factory has shifted all utility usage to a new 4 storied RC building. On 12th June 2019: Corrected from previous inspection. Factory has demolished the sheds and shifted operations to another building. On 24-Sep-2023: Corrected previously. During inspection, these sheds were found demolished. Operations from these sheds has been shifted to another building. On 01-Feb-2024: This issue was corrected from previous inspection. On 17-Oct-2024: Corrected previously. The factory demolished the Utility-1 & Shed-1. On 16-Feb-2026: Previously corrected. | (within 6-months) | Corrected
Follow Up Inspection |  | 11 | New findign-01: Non structural racking system and plastic water tanks on roof of RMG building are not adequately anchored or braced to resist earthquake forces. | Building engineer is required to provide adequate anchoring or bracing to the non structural elements including plastic water tank and racking system to resist eartquake force. | Corrected | Nov 5 2023 | On 24-Sep-2023: During inspection, non structural racking system and plastic water tanks on roof of RMG building were found unbraced. Building engineer is required to identify all the laterally unbraced non structural elements and provide adequate anchoring or bracing to withstand the lateral force. On 01-Feb-2024: Factory has anchored the racks and braced the PVC water tanks at roof. On 17-Oct-2024: Corrected previously. During inspection, all non-structural racking system & plastic water tanks were found anchored to the RMG Building. On 16-Feb-2026: Previously corrected. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 12 | New finding-02: Damage of column cover due to trolley impact at RMG building. | The building engineer is required to repair the damaged cover of columns and install barriers around the columns to prevent heavy trolley impact. | Corrected | Nov 5 2023 | On 24-Sep-2023: During inspection, damage of column cover found due to trolley impact at RMG building. The factory engineer is required to repair the damaged cover of columns and install barriers around the columns to prevent heavy trolley impact. On 01-Feb-2024: Factory has repaired the damaged columns and provided barrier to avoid further damage due to trolly impact. On 17-Oct-2024: Corrected previously. The factory provided the steel barrier around the column to prevent trolley impact. On 16-Feb-2026: Previously corrected. | (within 6 weeks) | Corrected

## Fire
Date
30-Jun-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | EMON Fashion Ltd., 42,Mariyali , Joydebpur , Gazipur J2, Gazipur
Date of Inspection |  | 2018-06-07
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Fire rated construction The exit stairs are not separated from [work areas, other spaces] on each floor by fire rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire rated doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors.If fire rated doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system.Once fire doors are installed, every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets ACCORD standard 6.8.3.1 | Corrected | Dec 30 2018 | On 16/09/2018: Extension of timeline is accepted. Extended timeline is valid till 30/12/2018. On 30/4/2019: Fire door installation almost done and interfacing work with FACP is going on. On 28/12/2020: Corrected. On 28/02/2022: Corrected. On 24/09/2023: Corrected. On 09-Jul-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 2 | Fire door Interfacing Installed fire rated doors of utility riser room and exit stairs were kept open without interfacing with the addressable FACP through some external sources. | If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. | Facility has ensured that all fire door are functional properly. Also our dedicated fire team is working and monitoring this regularly. | Jul 11 2018 | On 16/09/2018: Extension of timeline is not accepted. Extended timeline is valid till 07/11/2018. On 30/4/2019: Fire door installation almost done and interfacing work with FACP is going on. Some penetration has been observed. On 28/12/2020: Penetration sealed with non listed material. Penetration sealer shall be listed. On 28/02/2022: Fire door of Utility riser room doesn't close properly. Penetration was observed at ground floor. Penetration sealed by gypsum board, installation work must be as per UL prescribed procedure. On 24/09/2023: Fire rated doors were not closing properly on 5th floor both stairs. On 09-Jul-2024: Corrected. Fire doors interfacing with FACP and door accessories functionality have been verified during inspection and found functional and satisfactory. | Within 3 months | Corrected
Initial Inspection |  | 3 | Fire rated construction The boiler, generator, transformer and air compressor room is not separated by fire rated construction (openings, non-rated doors, penetrations). Location: Utility shed | Separate the boiler, generator, transformer and air compressor room by a minimum 2-hr fire rated construction. Seal and/or protected all openings to maintain fire separations. | Corrected | Dec 30 2018 | On 16/09/2018: Extension of timeline is accepted. Extended timeline is valid till 30/12/2018. On 30/4/2019: Corrected. On 28/12/2020: Corrected. On 28/02/2022: Corrected. On 24/09/2023: Corrected. On 09-Jul-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | Storage Areas Areas used for in-process storage of combustible materials are open to the surrounding occupancy. | Provide dedicated storage rooms separated by minimum 1- hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m | Corrected | Jul 11 2018 | On 16/09/2018: Extension of timeline is not accepted. Extended timeline is valid till 07/11/2018. On 30/4/2019: Corrected. On 28/12/2020: Corrected. On 28/02/2022: Referred to the issue no-22. On 24/09/2023: Corrected. On 09-Jul-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 5 | Fire Rated construction Rooms used for storage of combustible materials are not separated from the surrounding occupancy/areas. Location: Finish good store on 1st floor, dedicated store with knitting section on ground floor. | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour construction. | Corrected | Dec 30 2018 | On 16/09/2018: Extension of timeline is accepted. Extended timeline is valid till 30/12/2018. On 30/4/2019: Fire door installation almost done and interfacing work with FACP is going on. On 28/12/2020: In storage area penetration was observed with production floor area. On 28/02/2022: During inspection, penetration was observed in the 5th floor office along with the storage area. Penetration were not properly sealed at ground floor storage area. On 24/09/2023: Corrected based on site conditions. On 09-Jul-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 6 | Storage in Dining Area Storage located in the dining area. | Remove storage from the dining area. | Corrected | Oct 8 2018 | On 16/09/2018: Extension of timeline is not accepted. Extended timeline is valid till 10/08/2018. On 30/4/2019: Corrected. Removed. On 28/12/2020: Corrected. On 28/02/2022: Corrected. On 24/09/2023: Corrected. On 09-Jul-2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 7 | Lockage Egress Doors Egress doors/gates with locking features not complying with NFPA101 are provided at [ building exits, exit stairs, along egress routes, exit discharge] | Remove locking features from all egress doors/gates.If locks are required for security reasons, utilize specialized door locking features complying with NFPA101. | Corrected | Aug 14 2018 | On 16/09/2018: This issue will be verified during follow up inspection On 30/4/2019: Corrected. On 28/12/2020: Corrected. On 28/02/2022: Corrected. On 24/09/2023: Corrected. On 09-Jul-2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 8 | No Handrails Handrails are not provided on both sides of each exit stairs on all floors. Having handrails on one side of said staircase, may pose as a falling hazard during evacuation. | Provide handrails on both sides of the exit stair. New handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in.) | Corrected | Jul 11 2018 | On 16/09/2018: Extension of timeline is accepted. Extended timeline is valid till 07/11/2018. On 30/4/2019: Corrected On 28/12/2020: Corrected. On 28/02/2022: Corrected. On 24/09/2023: Corrected. On 09-Jul-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 9 | Storage in Egress Path Storage was located in the egress path and in the exit stair. | Keep egress path and stair clear of storage. | Corrected | Aug 14 2018 | On 16/09/2018: This issue will be verified during follow up inspection On 30/4/2019: Corrected On 28/12/2020: Corrected. On 28/02/2022: Corrected. On 24/09/2023: Corrected. On 09-Jul-2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 10 | Unusable discharge path The exit discharge path of south-east and north-east exit stairs are totally unusable. Exit stair found blocked. | Make a road / egress path for smooth discharge of occupants. Means of egress shall be maintained continuously free and clear of all obstructions. | Corrected | Aug 14 2018 | On 16/09/2018: This issue will be verified during follow up inspection On 30/4/2019: Corrected. On 28/12/2020: Corrected. On 28/02/2022: Corrected. On 24/09/2023: Corrected. On 09-Jul-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 11 | Antiquated Fire Detection System The fire detection system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. Location: RMG, office building and other sheds. | Replace the fire detection system with a new, listed addressable fire detection system in accordance with NFPA 72. | Corrected | Jun 30 2019 | On 28/12/2020: Factory is waiting for T&C VI. On 12/1/2021 (T&CVI): Approved. For details follow the full T&C report. On 28/02/2022: Corrected as per last T&CVI Report. See detailed on T&CVI Report (12/01/2021). On 24/09/2023: Corrected by T&CVI on 12/01/2021. On 09-Jul-2024: Previously corrected by T&CVI in 12-Jan-2023. FACP has been observed in normal operational condition. Detector was not provided in several newly modified areas on printing section colour mixing room & chemical mixing room (5th floor), CAD display room (4th floor) and Heat seal section (2nd floor). Reportedly, factory will install required detectors following standard in the newly modified areas, update the drawing, calculation and documents and keep available at site. It will be verified in the next follow-up inspection. | Design within 4months, Installwithin 9 months | Corrected
Initial Inspection |  | 12 | Fire Detection ITM Inspection, testing, and maintenance for the fire detection system is not inaccordance with NFPA 72. | Inspect, test and maintain the fire detection system, and keep written records on-site, in accordance with NFPA 72. | Corrected | Jul 11 2018 | On 16/09/2018: Extension of timeline is not accepted. Extended timeline is valid till 07/11/2018. On 30/4/2019:It is an integrated part of fire alarm system . On 28/12/2020: It is an integrated part of fire alarm system. On 12/1/2021 (T&CVI): Approved. For details follow the full T&C report. On 28/02/2022: Corrected. On 24/09/2023: Corrected. On 09-Jul-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 13 | Standpipe System The existing RMG building has an occupied floor greater than 10 meter (33 feet) and is not provided with standpipe protection. | Install a new class III standpipe system & fire department connection in accordance with NFPA 14. A class I system shall be permitted in buildings protected throughout by an automatic sprinkler system. | Corrected | Jul 5 2019 | On 28/12/2020: Factory is waiting for T&C VI. On 12/1/2021 (T&CVI): Approved. For details follow the full T&C report. On 28/02/2022: Corrected as per last T&CVI Report. See detailed on T&CVI Report (12/01/2021). On 24/09/2023: Corrected by T&CVI on 12/01/2021. Note: Class 1 piping was not fire rated enclosure at stair-S-E. On 09-Jul-2024: Corrected by T&CVI in 12-Jan-2023. | Design within 3 months, Install within 6 months | Corrected
Initial Inspection |  | 14 | Standpipe ITM Inspection, testing and maintenance of the standpipe system is not in accordance with NFPA 14. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 14 and ACCORD standards. | Corrected | Jul 5 2019 | On 16/09/2018: Extension of timeline is not accepted. Extended timeline is valid till 07/05/2019. On 30/4/2019:It is an integrated part of stand pipe system. On 28/12/2020: It is an integrated part of stand pipe system. On 12/1/2021 (T&CVI): Approved. For details follow the full T&C report. On 28/02/2022: Corrected. On 24/09/2023: Corrected. On 09-Jul-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 15 | Inadequate Lighting Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected | Jul 11 2018 | On 16/09/2018: Extension of timeline is not accepted. Extended timeline is valid till 07/11/2018. On 30/4/2019: Corrected. On 28/12/2020: Corrected. On 28/02/2022: Corrected. On 24/09/2023: Corrected. On 09-Jul-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 16 | On/Off Switch Manual on-off switch is provided for [emergency lighting / exit signage] units. | Remove manual on/off switches from [emergency lighting /exit signage] units to prevent them from being switched off | Corrected | Jul 9 2018 | On 16/09/2018: This issue will be verified during follow up inspection On 30/4/2019: Corrected. On 28/12/2020: Corrected. On 28/02/2022: Corrected. On 24/09/2023: Corrected. On 09-Jul-2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 17 | Non-Working Exit Signs Exit signage not illuminated (burned out, broken, etc.). | Regularly inspect all exit signage and replace/install lights as needed to illuminate signs | Corrected | Jul 9 2018 | On 16/09/2018: This issue will be verified during follow up inspection On 30/4/2019: Corrected. On 28/12/2020: Corrected. On 28/02/2022: Corrected. On 24/09/2023: Corrected. On 09-Jul-2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 18 | Emergency Lighting ITM Inspection, testing, and maintenance for the emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the emergency lighting system in the accordance with The ACCORD standard. Keep written recordson-site. | Corrected | Nov 30 2018 | On 16/09/2018: Extension of timeline is accepted. Extended timeline is valid till 30/11/2018. On 30/4/2019: Corrected. On 28/12/2020: Corrected. On 28/02/2022: Corrected. On 24/09/2023: Corrected. On 09-Jul-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 19 | Fire Extinguishers ITM Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10 and ACCORD standards. | Corrected | Jul 11 2018 | On 16/09/2018: Extension of timeline is accepted. Extended timeline is valid till 07/11/2018. On 30/4/2019: Corrected. On 28/12/2020: Corrected. On 28/02/2022: Corrected. On 24/09/2023: Corrected. On 09-Jul-2024: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 20 | New Finding (2nd followup): Dining area is not separated from other occupancies with fire rated assemblies | Re-locate the dining area or separate the dining area from other occupancies with fire rated construction | Corrected at the site, waiting for verification: The facility has separated the Dining area from the office area with fire-rated construction by installing a 3-hour fire-rated door. Also, the facility has reduced the dining capacity to below 300. | Mar 28 2021 | On 28/12/2020: New Findings. On 28/02/2022: Dining has been relocated to another shed which area are not separated from chemical & salt store. On 24/09/2023: Corrected because dining area has been relocated to lab building. On 09-Jul-2024: Issue re-opened. Dining area (500 seating capacity, E3 occupancy) has been relocated to 5th floor of main production building and separated from Office areas (F1 occupancy) by 2-hr fire rated construction (Fire door). While as per BNBC 2006 part-3 Table 3.2.1 a minimum of 3-hr fire rated construction barrier is required to separate E3 from F1. RPO Comments: On 20-May-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Follow Up Inspection |  | 21 | New Finding (3rd followup): Penetrations through floor/ceiling assemblies are found unsealed. Location: Toilet slubs (All Floor)/ North and south side. | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling or thickness required to maintain desired rating ) assemblies by listed fire stop materials to maintain the required fire resistance rating of 3-hr. | Corrected at the site, waiting for verification: The facility has sealed all penetrations in the toilet area with a required fire-rated stop collar. | May 28 2022 | On 28/02/2022: New Findings. On 24/09/2023: It is same as it was before. On 09-Jul-2024: Listed collar has been installed on 3rd and 4th floor toilet blocks. Penetration sealing work is ongoing on other floors. RPO Comments: On 20-May-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Follow Up Inspection |  | 22 | Areas used for in-process storage of combustible materials are open to the surrounding occupancy which are not separated by fire rated construction. Location: 1st & 4th floor. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Or, Where separate storage rooms are not feasible, Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Corrected | May 28 2022 | On 28/02/2022: New Findings. On 24/09/2023: Area used for in-process storage of combustible materials were found exceed limit on 4th floor. On 09-Jul-2024: Corrected. Process storage were found maintained as per recommendation and observed within permitted limit. | Within 3 months | Corrected
Follow Up Inspection |  | 23 | New Finding (5th FUI): Room used for storage of combustible materials are not separated from the surrounding occupancy/areas by fire rated construction. Location: Finished Goods Godown, 5th Floor. | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour construction. If store rooms (H2) are located with assembly occupancies (E3, E4) it shall be separeted by minimum 3 hour fire rated construction as per BNBC 2006 part 3 table 3.2.1. | Corrected at the site, waiting for verification: The facility has separated the storage from the surrounding occupancy with the required construction at the finished goods godown-5th floor. | Sep 9 2024 | On 09-Jul-2024: New Finding. RPO Comments: On 20-May-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 months | Pending Verification
Follow Up Inspection |  | 24 | New Finding (5th FUI): Travel distance exceeds the maximum allowable limit where only a single means of egress is provided. Location: Accessories Store (4th floor), Bonded warehouse at (Ground floor). | The number of means of egress from any floor, story or portion thereof shall not be less than 2 except where a single exit is permitted following Table 6.6.2, a single means of egress is permitted by 6.6.5 or where a greater number is required by 6.6.3. (RSC Technical Guidelines v1 (Standard)). | Corrected at the site, waiting for verification: To maintain the travel distance, the facility has installed the required secondary exit door at the Accessories store (4th floor) & Bonded Warehouse (ground floor). | Sep 9 2024 | On 09-Jul-2024: New Finding. RPO Comments: On 20-May-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 months | Pending Verification
Follow Up Inspection |  | 25 | New Finding (5th FUI): Storage rooms discharge directly into the exit stair enclosure. Location: 1st floor (Gray Fabric Store). | Openings from exit enclosure to storage spaces shall be provided with a vestibule with fire rated construction and openings. Provide a 1.5-hr. fire rated door on the exit stair side and a 1-hr. fire rated door on the storage room side as per 6.14.3 - RSC Technical Guidelines Standard V1.0. The minimum width for vestibules shall not be less than 1.1m and length 1.8m. Ensure that the fire rating of the vestibule construction matches that of the exit stair enclosure. | Corrected at the site, waiting for verification: The facility has removed the goods from the mentioned storage area on the 1st floor (Gray Fabric Store). Now the facility is being used this area as a sewing floor and an idle sewing machines area. | Oct 9 2024 | On 09-Jul-2024: New Finding. RPO Comments: On 20-May-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification

## Electrical
Date
30-Jun-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | EMON Fashion Ltd., 42,Mariyali , Joydebpur , Gazipur J2, Gazipur
Date of Inspection |  | 2018-06-07
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by Accord. Electrical SLD shall be updated properly when electrical system is modified. | Corrected | Oct 30 2018 | On 17/09/2018: Extension till 30/10/2018 from 07/10/2018 is accepted by Accord. On 30/04/2019: Not Corrected. On 28/12/2020: Not Corrected. SLD is not as built. Cable(phase, earthing) size mismatches with SLD in few locations. On 18-01-2022: Not Corrected. As built SLD has been prepared. Factory is working to implement it. On 24/09/2023: Not Corrected. Factory got SLD "Accepted" from RSC on 05-Sep-2023. Progress observed in field. Still found some mismatch with field & SLD. On 04/04/2024: Corrected. | 02 Months | Corrected
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not installed where the risk index equal or greater than 40 (According to BNBC). | Factory has to design Lightning Protection System (LPS) for the whole factory (where the Risk index is equal or greater than 40). Once LPS is designed properly, installation shall be done accordingly. | Corrected | Nov 30 2018 | On 17/09/2018: Extension till 30/11/2018 from 07/11/2018 is accepted by Accord. On 30/04/2019: Corrected. | 03 Months | Corrected
Initial Inspection |  | 3 | Insulation resistance record (cable information) doesn't match with field. | Field information shall be reflected in the record and significantly lower sized cables' record shall be avoided. | Corrected | Oct 30 2018 | On 17/09/2018: Extension till 30/10/2018 from 07/10/2018 is accepted by Accord. On 30/04/2019: Corrected. | 02 Months | Corrected
Initial Inspection |  | 4 | Earth Pit resistance test record doesn't match with field. | Adequate number of earth pits shall be ensured (if it's lower in numbers) and record shall be made accordingly. | Corrected | Oct 30 2018 | On 17/09/2018: Extension till 30/10/2018 from 07/10/2018 is accepted by Accord. On 30/04/2019: Corrected. | 02 Months | Corrected
Initial Inspection |  | 5 | Programmed schedule for periodical inspection & testing of electrical equipment is not proper. | An electrical maintenance program shall be prepared which will include inspections and testing of the electrical systems (preventive and proactive). | Corrected | Oct 30 2018 | On 17/09/2018: Extension till 30/10/2018 from 07/09/2018 is accepted by Accord. On 30/04/2019: Corrected. | 01 Month | Corrected
Initial Inspection |  | 6 | No LOTO (Lock-Out-Tag-Out) policy is introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. | Corrected | Nov 30 2018 | On 17/09/2018: Extension till 30/11/2018 from 07/10/2018 is accepted by Accord. On 30/04/2019: Corrected. | 02 Months | Corrected
Initial Inspection |  | 7 | Uninsulated electrical tools are used by maintenance personnel in the factory. | For maintenance purposes, all the electrical tools shall be properly insulated, and these insulations shall be checked periodically. | Corrected | Jul 9 2018 | On 30/04/2019: Corrected. | 01 Month | Corrected
Initial Inspection |  | 8 | 11kV power cable dropping from overhead line is not properly supported with pole and unprotected at the bottom of pole. | 11kV distribution power cable shall be fixed with pole properly and protected at the bottom avoiding any kind of physical injury. | Corrected | Jul 10 2018 | On 30/04/2019: Corrected. | 02 Months | Corrected
Initial Inspection |  | 9 | HT switchgear is not provided for incoming supply from grid. | HT switchgear shall be installed for the protection of incoming supply from grid. | Corrected | Oct 30 2018 | On 30/04/2019: Corrected. | 02 Months | Corrected
Initial Inspection |  | 10 | Inadequate working space around transformer performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) shall be maintained. | Corrected | Nov 30 2018 | On 30/04/2019: Corrected. | 03 Months | Corrected
Initial Inspection |  | 11 | Oil level in transformer conservator oil tank is below minimum level. | Minimum oil level in transformer conservator oil tank shall be maintained, and it shall be checked periodically. | Corrected | Jul 10 2018 | On 30/04/2019: Corrected. Oil cooled transformer does not exist now in the factory. | 02 Months | Corrected
Initial Inspection |  | 12 | Transformer Silica gel is discolored. | Silica gel shall be changed; or reuse can be done, if color regains after sundry. | Corrected | Jul 10 2018 | On 30/04/2019: Corrected. Oil cooled transformer does not exist now in the factory. | 02 Months | Corrected
Initial Inspection |  | 13 | Lint and dust deposited on and around the transformer. | Transformer top and around it shall be kept neat and clean. | Corrected | Jul 10 2018 | On 30/04/2019: Corrected. Oil cooled transformer does not exist now in the factory. | 02 Months | Corrected
Initial Inspection |  | 14 | 11kV power cables laid on substation room floor which makes obstacle in the working area. | HT cables shall be rerouted avoiding obstacles in the working areas of electrical installations. | Corrected | Jul 10 2018 | On 30/04/2019: Corrected. | 02 Months | Corrected
Initial Inspection |  | 15 | Cable trench is found wet or filled with water. | Cable trench shall be kept always dry and shall be covered by checkered plate. | Corrected | Oct 30 2018 | On 30/04/2019: Corrected. | 01 Month | Corrected
Initial Inspection |  | 16 | Generator output cables (laid on floor) are not protected and supported. | Service cables from generator shall be supported at its own breaker's terminal and with cable tray. | Corrected | Oct 30 2018 | On 30/04/2019: Corrected. | 02 Months | Corrected
Initial Inspection |  | 17 | Equipment earth cable (for generator) size is inadequate. | At least two separate earth pits shall be ensured for generator; The earth cable size shall be determined according to BNBC or Adiabatic method (considering related factors). Number of earth pits shall be determined by the size of connected earth cable. | Corrected | Oct 30 2018 | On 30/04/2019: Not Corrected. On 28/12/2020: Corrected. | 02 Months | Corrected
Initial Inspection |  | 18 | Lead acid battery terminals are left open. | Lead acid battery terminals shall be covered/capped, and rust shall be checked and cleaned. | Corrected | Jul 9 2018 | On 30/04/2019: Corrected. | 01 Month | Corrected
Initial Inspection |  | 19 | Distribution boards have no clear identification markings. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. | Corrected | Oct 30 2018 | On 30/04/2019: Corrected. | 01 Month | Corrected
Initial Inspection |  | 20 | Inadequate working space around (or in front of) board/panels and access to the board/panels is obstacles. | At least 1.07 meter (or equal to the width of board/panel, whichever is higher) working clearance shall be maintained in front of each electrical board/panel. | Corrected | Oct 30 2018 | On 30/04/2019: Corrected. | 02 Months | Corrected
Initial Inspection |  | 21 | Electrical power cables and circuit breakers are not identified properly. | Proper identification shall be done on power cables, circuit breakers used in the system according to SLD. | Corrected | Jul 10 2018 | On 30/04/2019: Not Corrected. On 28/12/2020: Corrected. | 02 Months | Corrected
Initial Inspection |  | 22 | Panel doors are not connected with earth. | All metal installation which a part of electrical system shall be connected to earth to avoid electrical shock or electrocution. | Corrected | Jul 9 2018 | On 30/04/2019: Corrected. | 01 Month | Corrected
Initial Inspection |  | 23 | Panel base plates are removed to allow cable entry. | Panel base plates shall be installed, at all time, and cables entering panel shall be firmly fixed with cable gland. | Corrected | Jul 10 2018 | On 30/04/2019: Corrected. | 02 Months | Corrected
Initial Inspection |  | 24 | Electrical distribution box/panels are full of fluffs (lint/dirt). | Each electrical distribution board/panel shall be properly sealed to avoid ingression of fluffs; but an adequate ventilation system shall also be ensured. | Corrected | Jul 9 2018 | On 30/04/2019: Corrected. | 01 Month | Corrected
Initial Inspection |  | 25 | Power cables entering or exiting from Distribution board/panel are not properly fixed. | Power cables entering or exiting from distribution board/panel shall be fixed through Panel base/top plate using proper sized cable glands (metal/PVC). | Corrected | Jul 10 2018 | On 30/04/2019: Corrected. | 02 Months | Corrected
Initial Inspection |  | 26 | Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, shall be made following proper guidance. | Corrected | Jul 10 2018 | On 30/04/2019: Corrected. | 02 Months | Corrected
Initial Inspection |  | 27 | MCCBs are not adjusted per load demand. | All the MCCBs shall be adjusted per connected load current; if adjustment is not possible, replacement will be the only way. | Corrected | Jul 10 2018 | On 30/04/2019: Not Corrected. On 28/12/2020: Corrected. | 02 Months | Corrected
Initial Inspection |  | 28 | Circuit is drawn from bus bar without any protective means. | Each electrical circuit shall be drawn from distribution board busbar using a proper type protection arrangement (MCCB/MCB). | Corrected | Nov 30 2018 | On 30/04/2019: Corrected. | 02 Months | Corrected
Initial Inspection |  | 29 | Earth lead cable/Earth Continuity Conductor size is inadequate/undersize. | Earth lead cable/ Earth Continuity Conductor (ECC) shall be determined according to BNBC or Adiabatic method (considering CB's response time, fault current & type of earth conductor other factors). | Corrected | Nov 30 2018 | On 30/04/2019: Not Corrected. On 28/12/2020: Corrected. | 02 Months | Corrected
Initial Inspection |  | 30 | Multiple cables (came from different electrical consumers) terminated at same terminals. | Each electrical circuit shall be terminated at single terminals. | Corrected | Jul 10 2018 | On 30/04/2019: Corrected. | 02 Months | Corrected
Initial Inspection |  | 31 | Hot Spots were observed at several points. | Hot spots shall be eliminated from entire electrical system and shall be always carried forward. | Corrected | Aug 21 2018 | On 30/04/2019: Corrected. No hot spots have been found. | 02 Weeks | Corrected
Initial Inspection |  | 32 | MCCB/MCB is installed without any enclosure. | Each MCCB/MCB shall be enclosed by proper type material. the material shall not be more than 18 SWG graded. | Corrected | Jul 9 2018 | On 30/04/2019: Corrected. | 01 Month | Corrected
Initial Inspection |  | 33 | Cables are hanging without (proper) support and protection. | Cable tray/ladder shall be used to support cables at anywhere to keep cable out of tension. Outdoor arrangement shall be covered. | Corrected | Sep 30 2018 | On 30/04/2019: Corrected. | 03 Months | Corrected
Initial Inspection |  | 34 | Cables passing through wall/ floor slab are not protected at the entry/exit point(s). | Cables passing through permanent wall/floor slab shall be protected. Floor to floor openings shall be sealed by proper type materials (consult with fire expert). | Corrected | Jul 10 2018 | On 30/04/2019: Corrected. | 02 Months | Corrected
Initial Inspection |  | 35 | Combustible material attached with power cable. | Power cable shall be free from combustible material. | Corrected | Jul 9 2018 | On 30/04/2019: Corrected. | 01 Month | Corrected
Follow Up Inspection |  | 36 | New Finding: Exhaust fan body and metal enclosure has no earth connection. | Ensure earth collection for exhaust fan motor frame and metal enclosures. | Corrected | Feb 7 2021 | On 18/01/2022: Corrected. | 01 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Field information has no/less reflection in existing SLD. | As-built Electrical Single Line Diagram (SLD) must be prepared by a qualified engineer, including all essential details of the electrical system. This diagram must be reviewed and approved by the RSC. The accepted SLD needs to be implemented at the factory. All cables, all circuits, all terminals, all equipment are required to be identified as per the accepted Single line diagram. | Corrected at the site, waiting for verification: The factory has revised the SLD and submitted it to RSC, and it has already been accepted. | Mar 1 2026 | RPO Comments: On 20-May-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 38 | New Finding: Hot spots have been observed at some points. | Hot spots throughout the entire electrical system must be eliminated to ensure safety and prevent potential equipment failures or hazards and reduce downtime and repair costs. | Corrected at the site, waiting for verification: The factory has eliminated all hot spots. | Mar 1 2026 | RPO Comments: On 20-May-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 39 | New Finding: Uncovered & perforated type cable tray used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Corrected at the site, waiting for verification: The factory has completed all wiring in the storage area in accordance with the RSC guidelines. | Mar 1 2026 | RPO Comments: On 20-May-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification

## Boiler
Date
30-Jun-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | EMON Fashion Ltd., 42,Mariyali , Joydebpur , Gazipur J2, Gazipur
Date of Inspection |  | 2022-08-22
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 5815 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. |  | Jul 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Not Corrected. The Boiler is in temporary shutdown condition. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 2 | BB 11195 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | Completed. The facility has installed the required emergency stop push switches in the mentioned Boiler area. | Jul 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Corrected | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 3 | BB 13007 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. |  | Jul 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Not Corrected. The Boiler is in temporary shutdown condition. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 4 | BB 5815 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. |  | Jul 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Not Corrected. The Boiler is in temporary shutdown condition. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 5 | BB 11195 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Completed. The Low Low Water Level (LLWL) has been marked beside the gauge glass so that the water level can be visualized and identified clearly. | Jul 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Corrected | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 6 | BB 13007 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. |  | Jul 30 2025 | Comments on 07-Jul-2025: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within 20-Jul-2025. On 4-May-2026: Not Corrected. The Boiler is in temporary shutdown condition. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 7 | BB 11195 | Necessary technical documents (manufacturing drawings, Piping & Instrumentation diagram, data sheets of mountings, accessories & feed water pump, boiler maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report, and water treatment report) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Completed. Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning ocuments, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report are available and attached with the pcitorial evidence file. | Jul 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Corrected. manufacturing drawings, Piping & Instrumentation diagram, data sheets of mountings, accessories & feed water pump, boiler maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report, and water treatment report were available and reviewed. | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 8 | BB 5815 | Nameplates for safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. |  | Jun 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Not Corrected. The Boiler is in temporary shutdown condition. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 9 | BB 5815 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. |  | Jun 15 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Not Corrected. The Boiler is in temporary shutdown condition. | 2 WEEKS | In Progress
Initial Inspection | External visual inspection | 10 | BB 11195 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | Completed. Fuel line in boiler room sealed off to prevent fuel leakage. | Jun 15 2025 | Comments on 07-Jul-2025: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within 20-Jul-2025. On 4-May-2026: Corrected | 2 WEEKS | Corrected
Initial Inspection | External visual inspection | 11 | BB 13007 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. |  | Jun 30 2025 | Comments on 07-Jul-2025: As per the pictorial evidence, the issue is not remediated yet. The remediation work shall be done following guidelines provided and applicable standard within 20-Jul-2025. Uninsulated portion at the side of the steam header should also be insulated properly. On 4-May-2026: Not Corrected. The Boiler is in temporary shutdown condition. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 12 | BB 5815 | Steam header Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. |  | Jun 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Not Corrected. The Boiler is in temporary shutdown condition. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 13 | BB 11195 | Steam header Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | Boiler Safety Valve outlet line is directly outside of the boiler room. | Jun 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Corrected | 1 MONTH | Corrected
Initial Inspection | External visual inspection | 14 | BB 13007 | Steam header Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. |  | Jun 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Not Corrected. The Boiler is in temporary shutdown condition. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 15 | BB 13007 | Necessary technical documents (except manufacturing calculations, boiler operational logbook) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. |  | Jul 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Not Corrected. The Boiler is in temporary shutdown condition. Documents were not available. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 16 | BB 5815 | Water leakage was observed inside the boiler room. | Boiler and its surrounding shall be free from storage, obstruction and free from slipping hazard for proper monitoring by boiler operator and other relevant maintenance technicians. |  | Jul 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Not Corrected. The Boiler is in temporary shutdown condition. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 17 | BB 11195 | Water leakage was observed inside the boiler room. | Boiler and its surrounding shall be free from storage, obstruction and free from slipping hazard for proper monitoring by boiler operator and other relevant maintenance technicians. | Completed. Boiler room is free from storage & obustractions & hazards. | Jul 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Corrected. Water leakage issue inside the boiler room was resolved. | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 18 | BB 5815 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. |  | Jul 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Not Corrected. The Boiler is in temporary shutdown condition. Documents were not available. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 19 | BB 11195 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder - that does not pose fall hazard - should be provided. | Completed. Facility has installed the platform with the lader as per the mentioned measurement. | Jul 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Corrected | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 20 | BB 13007 | Boiler body was found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. |  | Jun 30 2025 | Comments on 07-Jul-2025: As per the pictorial evidence, the issue is not remediated yet. The remediation work shall be done following guidelines provided and applicable standard within 20-Jul-2025. The remediation work by the factory can be a temporary solution. To ensure a safe workplace for the staffs in the boiler room, proper insulation is required. On 4-May-2026: Not Corrected. The Boiler is in temporary shutdown condition. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 21 | BB 11195 | Discharge of safety valve was not free from danger of scalding. | Safety valve outlet line shall not affect emergency discharge path or discharge of safety valve shall be free from danger of scalding. | Completed. Safety valve outlet line emergency discharge path is free from danger of scalding. | Jun 30 2025 | Comments on 07-Jul-2025: The remediation work will be verified during the next follow-up inspection. On 4-May-2026: Corrected | 1 MONTH | Corrected
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 22 | BB 11195 | Salt and thin scale formation was observed on the waterside. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | Completed. Facility has properly cleaned the boiler. Also facility keep the water quality verified record. | Jun 30 2025 | On 15-Apr-2026: Corrected. Descaling was performed on 26-Mar-26, and upon inspection, the boiler waterside was observed to be clean. | 1 MONTH | Corrected