## Structural
Date
12-Apr-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Helicon Ltd, Plot # 127, Dhaka EPZ (Old Area), Ganakbari, Savar, Dhaka, Dhaka
Date of Inspection |  | 2014-05-11
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Column stresses (if building is extended to 6 storeys). | If factory is to be extended to 6 storeys Factory Engineer to review columns stresses in all columns using a model based design check to loading set out in BNBC-2006. Factory Engineer to verify insitu concrete strength by taking 100mm diameter cores from 4 columns . | Completed. The DEA documents of Helicon Ltd (Accord ID: 10718) have been reviewed & accepted by the Accord Bangladesh on 23 June 2016. The DEA process and report have been reviewed in accordance with ACCORD Standards and Helicon can proceed with extension work with additional stories as per drawing design accepted by ACCORD. Accord Structural 3rd followup audit and DEA verification conducted on 30 March,2017. But during verification some discrepancy was found with provided drawings. According to Accord standard, we have submitted revised DEA and accepted by Accord on 23 May,2017. | Mar 2 2016 | On 07/03/2015: In our inspection, no sign of further extension were made. On 10/02/2016: Previous timeline: 28 Sep, 2014 Final timeline: 02 March, 2016 During inspection, the building was found to be extended up to 4 storied. In that case the factory is advised to submit DEA as per BNBC provision. Factory will submit it within 02 March, 2016. Core test already done by factory. It should be included along with other test reports in the DEA. Load exceeds 130 psf in some parts in 2nd floor. Factory authority is advised to remove excess loads within 17 Feb, 2016. On 30/03/2017: This issue has been covered in DEA. DEA of the factory was accepted from Accord on 23rd June 2016. During verification, some discrepancy was found with provided drawings. Factory is being informed already by mail with a discrepancy report. On 11/07/2017: After DEA verification, DEA documents have been reviewed and conditionally re-accepted by ACCORD on 23-May-2017. On 25/02/2018: Corrected from previous follow up inspection. DEA of the factory was carried out considering 6-stories which was re-accepted by ACCORD on 23rd May 2017. On 16-Jan-2024: Corrected from previous inspection. This issue had been covered under DEA which was accepted by ACCORD on 23-May-2017. Also, core test report was available on site during inspection. On 29-Mar-2026: Previously corrected. During the inspection, single-storied ancillary structures Boiler Room, Security Room, and RMS Room were found. The as-built drawings were available on-site and found satisfactory. | within 6-months | Corrected
Initial Inspection |  | 2 | Cracking in non structural masonry walls. | Factory Engineer to monitor cracking in masonry walls over an extended period (min 12 months) and advise on any remedial structural work required. | Completed. Our Engineer (Structural engineering firm Advance engineering) has investigated the recurrent cracking are exists only in the render and as per his advice, we have taken corrective action and completed the crack issue and also monitoring on cracks and there is no newly cracks observed. | Mar 10 2016 | On 07/03/2015: In our inspection, we found the cracks were repaired but seems to reappearing and our advice would be to monitor the cracks for another 6 months and to take measure accordingly. On 10/02/2016: Some cracks are repaired by plastering. But some still exists. The factory authority is advised to investigate the reason of recurrent cracks and take proper measures to prevent them within 10 March,2016. On 30/03/2017: Factory has repaired some cracks by plastering. But during inspection, cracks found in many locations which are not repaired. The factory authority is advised to investigate the reason of recurrent cracks and take proper measures to prevent them. On 11/07/2017: During inspection, cracks were not found in non-structural masonry walls. Factory has repaired the cracks by cement mortar and maintained a register book for the observation of crack status. However, this issue requires continuous observation and will be corrected if no cracks were observed in the next 6 months. On 25/02/2018: Factory Engineer has repaired the cracks by cement mortar and maintained a register book for the observation of crack status. No further crack is observed during this inspection On 16-Jan-2024: Corrected from previous inspection. Cracks were found repaired and factory maintained a register book regarding cracks. During inspection, no visible cracks were found. On 29-Mar-2026: Previously corrected. | within 6-months | Corrected
Initial Inspection |  | 3 | Cracking in Ground Floor Slab. | Factory Engineer to monitor settlement of the ground floor slab and note if any settlement occurs in foundations to the main structural elements. | Completed: Our Engineer (Structural engineering firm Advance engineering) has checked this issue with foundation adequacy and along with DEA report. The crack was caused by differential settlement. As per advise of our Engineer, we have done the repairing work. Our structural engineer has monitored the settlement of the ground floor slab and there is no any settlement occurred/observed in foundations to the main structural elements. | Mar 2 2016 | On 10/02/2016: Crack has been repaired. The factory is advised to check foundation adequacy along with DEA report if it was caused by differential settlement or not. Factory authority said they will submit DEA within 02 March, 2016. On 30/03/2017: A settlement test has been carried out by factory consultant. As per recommendation, it is certified that, the building is quite safe and sound to bear the functional load of the building. On 11/07/2017: Found corrected from previous inspection. On 25/02/2018: Corrected from previous follow up inspection. crackings are not observed during inspection. No further crack is found during this inspection. On 16-Jan-2024: Corrected from previous inspection. As per investigation report cracks were not occurred in main structural elements. During inspection, no visible cracks were found. On 29-Mar-2026: Previously corrected. | within 6-months | Corrected
Initial Inspection |  | 4 | Cracking in beams. | Factory Engineer to investigate if the cracking is structural or exists only in the render. | Work In progress. Our Engineer (Structural engineering firm Advance engineering) has investigated the recurrent cracking are exists only in the render and as per his advice we will complete the crack issue within 15 July, 2017. Also we are monitoring on cracks and there is no newly cracks observed. | Mar 10 2016 | On 07/03/2015: Some of the beam cracks has been repaired. Some has not been repaired yet. On 10/02/2016: Factory management has repaired most of the cracks by plastering. But some still exists. The factory is advised to investigate the reason of recurrent cracking on structural elements and take proper measures to prevent them 10 March, 2016. On 30/03/2017: Cracks in beam weren't investigated by factory engineer or consultant. Some of the beam cracks has been repaired. Some has not been repaired yet. On 11/07/2017: Factory engineer has produced investigation report for floor beam crack and it was observed that the cracking was non-structural. In addition, factory has repaired the cracks by cement mortar. On 25/02/2018: Corrected in previous follow up inspection. Factory engineer produced investigation report which ensured crackings were non-structural. In addition, factory has repaired the cracks by cement mortar. On 16-Jan-2024: Corrected from previous inspection. As per investigation report cracks were found non-structural. During inspection, no visible cracks were found. On 29-Mar-2026: Previously corrected. | within 6-months | Corrected
Follow Up Inspection |  | 5 | New Finding: Beam stress and slab stress under the newly installed two overhead water tanks | Factory engineer is advised to carry out the adequacy check under the overhead water tanks. | Corrected: At present, the water tank has been moved and placed temporarily on a 4 legged steel with the support of cross beam. Our Engineer (Structural engineering firm Advance engineering) has checked the adequacy of the slab and beam on which water tanks are placed and the supporting documents of adequacy checks has been submitted to Accord on 09 Feb, 2016. Also note that Accord has reviewed & accepted/ approved DEA documents of Helicon Ltd. dated on June 23, 2016 and we will make permanent water tank as per proposed/approved drawing during construction work of vertical extension of our factory building. As per DEA, Our Structural engineer have shifted the subject discussion water tank in considerable place on roof top on 04 February,2018. | Mar 10 2016 | On 07/03/2015: Structural team from ACCORD found two 3000 liters water tanks resting on roof slab. Factory engineer is advised to check the adequacy of the slab and beam on which water tanks are resting. On 10/02/2016: The water tank has been moved and placed on to a 4 legged steel slab. The supporting documents of adequacy checks has been submitted by the factory on 09 Feb., 2016 which is under review. ACCORD will review it within 10 March,16. On 30/03/2017: The water tank has not been moved as per accepted load plan. Factory is advise to replace the water tank ae per accepted load plan. On 11/07/2017: Overhead water tanks were not shifted yet as per instruction since construction work is going on. Factory is required to replace the water tanks as per posted load plan as soon as possible. On 25/02/2018: Beam-column adequacy has been checked in DEA. Also, a allowable floor loading plan has prepared. OHPWT are shifted to the locations as shown in floor load plan. On 16-Jan-2024: Corrected from previous inspection. (see item no. 9) On 29-Mar-2026: Previously corrected. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 6 | New Finding: A long crack extending from one beam to another beam in 2nd floor. | Factory engineer to investigate the cause and remedy of the crack. | Completed. Our Engineer (Structural engineering firm Advance engineering) has investigated the long crack extending from one beam to another beam in 2nd floor and as per his advise, we have done the remediation action. | Mar 10 2016 | On 07/03/2015: In our inspection, we removed some of the plaster covering and found the crack propagating through the concrete. Factory Engineer is to investigate and carry out proper remediation within 18 March, 2015. On 10/02/2016: Factory management has repaired the crack by plastering. The factory is advised to investigate the reason of recurrent cracks on structural elements and take proper measures to prevent them within 10 March, 16. On 30/03/2017: Crack has been investigated and repaired with suitable method as per investigation report. On 11/07/2017: Found corrected from previous inspection. On 25/02/2018: Corrected from previous follow up inspection. No further cracks are observed in beams. On 16-Jan-2024: Corrected from previous inspection. During inspection no visible cracks were found. On 29-Mar-2026: Previously corrected. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 7 | New Finding: Drawing does not show any opening in the 2nd floor slab. | Factory engineer to carry out structural investigation the slab having the opening. | Completed. Our Engineer (Structural engineering firm Advance engineering) has investigated the slab having the opening in 2nd floor and as per his advise, we have closed the opening in the 2nd floor slab. | Aug 8 2015 | On 07/03/2015: We found an opening in the 2nd floor slab which is not shown in the original drawing. This opening has several cracks around it. We advised factory engineer to investigate and carry out remediation action as soon as possible. On 10/02/2016: The slab opening has been sealed off by the factory management. On 30/03/2017: Corrected in previous follow up inspection. The slab opening has been sealed off. On 11/07/2017: This issue remains corrected. On 25/02/2018: Corrected from previous follow up inspection. The opening of slab are observed sealed. On 16-Jan-2024: Corrected from previous inspection. On 29-Mar-2026: Previously corrected. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 8 | New findings (On 30/03/2017) Damaged column at GF due to installation of washing machine | Remove the discharge pipe of washing machine and repair the damaged column with suitable method. | Completed. Our Engineer (Structural engineer firm Advance engineer) has investigated the damage column. According to consultancies , we have already removed the discharge pipe of washing machine and repair the damaged column with the opinion of consultancy method. | Apr 27 2017 | On 30/03/2017: Remove the discharge pipe of washing machine and repair the damaged column with suitable method. On 11/07/2017: Factory has removed the discharge pipe of washing machine and repaired the damaged column with suitable method. In addition, factory has produced remediation report regarding this issue. On 25/02/2018: Corrected form previous follow up inspection. The column is observed repaired. On 16-Jan-2024: Corrected from previous inspection. During inspection, column was found repaired. On 29-Mar-2026: Previously corrected. | Immediately | Corrected
Follow Up Inspection |  | 9 | New findings-5: Proposed roof shed (Dining). | The building engineer is required to carry out the remedial works as per the accepted EA (if any). | Completed: We have resubmitted updated EA to RSC structural engineer and RSC structural engineer Re-Acceptance of Engineering Assessment documents of Helicon Ltd [ID: 10718] on 22/09/2024. | Aug 1 2024 | On 16-Jan-2024: The factory has submitted the EA considering the proposed roof shed. The factory is required to carry out the remedial works as per the accepted EA (if any). On 29-Mar-2026: The EA of the existing six-storied RC Building and proposed steel roof shed was accepted by RSC dated 22-September-2024. The proposed dining shed has not yet been constructed. However, the factory has completed the retrofitting work for the existing six-storied RC Building. The retrofitting steel plate (6mm and 15mm) test report was not available on-site. The factory is required collect the retrofitting plate test reports and keep it on-site which will be checked in the next inspection. Also, complete the proposed roof shed construction as the re-accepted design-drawing. Progress Status: 75%. | within 6-months | In Progress

## Fire
Date
12-Apr-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Helicon Ltd, Plot # 127, Dhaka EPZ (Old Area), Ganakbari, Savar, Dhaka, Dhaka
Date of Inspection |  | 2014-06-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Areas used for combustible storage at 1st and 2nd floors are not fire-rated separated from factory floors. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. |  | Dec 1 2016 | On 05-01-2017: Corrected. On 30/03/2017: Corrected. On 11/07/2017: Completed On 17/10/2017: Corrected. On 11/03/2018: Corrected. On 22/10/2018: Corrected. On 28/09/2020: Please see issue no. 26. On 20/05/2024: Corrected. | 3 Months | Corrected
Initial Inspection |  | 2 | Areas used for combustible storage at the ground floor are not separated by fire-rated construction. | Provide 1-hour fire-rated walls up to structure and 0.75 hour fire-rated openings. |  | Apr 25 2016 | On 30/03/2017: Corrected. On 11/07/2017: Separated. Fire doors are not interfaced with fire alarm system. If the factory wants to keep open the doors, needs to interface them with fire alarm system. On 17/10/2017: Corrected. On 11/03/2018: Corrected as per previous follow up. On 22/10/2018: Corrected. On 28/09/2020: Corrected. On 20/05/2024: Corrected. | 3 Months | Corrected
Initial Inspection |  | 3 | Areas used for combustible storage are not separated by fire rated construction. Ground, 1st and 2nd floors have areas used for storage without proper separation. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. |  | Jun 30 2016 | 02-11-2016: Not corrected. More fire doors need to be installed in Ground floor to correct this issue. On 05-01-2017: Works have been started. On 30/03/2017: L/C has been opened for fire rated doors. On 17/10/2017: Corrected. On 11/03/2018: Corrected as per previous follow up. On 22/10/2018: Corrected. On 28/09/2020: Please see issue no. 26. On 20/05/2024: Corrected. | 3 Months | Corrected
Initial Inspection |  | 4 | The exit stairs are not separated from work areas on each floor by fire-rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. |  | Dec 20 2015 | On 05-01-2017: Corrected. On 30/03/2017: Corrected. If factory wants to keep fire rated door open, they will install electromagnetic door holder and interface with FACP. On 17/10/2017: Issue has been reopened on point no 22. On 22/10/2018: Corrected. On 28/09/2020: Please see issue no. 22. On 20/05/2024: Corrected. | 3 Months | Corrected
Initial Inspection |  | 5 | Egress gates with locking features are provided at building exits, exit stairs, along egress routes and exit discharge. Lockable collapsible gates we're provide at most exits, gates were open and unlocked during the inspection. | Remove locking features from all egress gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. |  | Dec 1 2016 | On 30/03/2017: Corrected. On 17/10/2017: Corrected. On 11/03/2018: Corrected. On 22/10/2018: Corrected. On 28/09/2020: Corrected. Removed. On 20/05/2024: Corrected. | Immediately | Corrected
Initial Inspection |  | 6 | Storage was located in the west exit stair. | Remove all storage from exit stairs and egress paths. |  | Nov 10 2014 | On 30/03/2017: Corrected. On 17/10/2017: Corrected. On 11/03/2018: Corrected. On 22/10/2018: Corrected. On 28/09/2020: Corrected. Removed. On 20/05/2024: Corrected. | Immediately | Corrected
Initial Inspection |  | 7 | Collapsible gates are provided at most building exits, exit stairs, along egress routes and exit discharge. | Replace all collapsible gates along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. |  | Dec 15 2014 | On 30/03/2017: Corrected. On 17/10/2017: Corrected. On 11/03/2018: Corrected . On 22/10/2018: Corrected. On 28/09/2020: Corrected. Replaced. On 20/05/2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 8 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | Completed. We have installed automatic CFDS in the facilities which is right now in operation. | Jun 30 2016 | On 17/10/2017: Yet L/C has not been opened. On 11/03/2018: Same condition found. L/C yet not opened. On 22/10/2018: Installation has been almost completed. Factory shall apply for T&C. On 20/05/2019: FAT&C observations (not limited to): Detector missing in several location, spacing not comply with NFPA 72, plastic cover not removed from some detector, battery size and voltage drop calculation shall be proper, as built design not match with actual site layout (mostly at 5th floor) and not legible, all exhaust fan is not interfaced with FACP, wiring of fire alarm device found exposed, Cable not protected from physical damage at upper ceiling area & device connection wiring. All the deficiencies shall be remediated as soon as possible and system shall comply with NFPA 72. On 28/09/2020: Factory has applied for T&C. Please see details in pre-T&C report. On 07/09/2021 (Completed on 20/09/2021): T&CVI found that the system is corrected. See detailed T&CVI report. On 20/05/2024: Corrected. System was found active and functional. FACP was in normal condition. | Design within 4 months, install within 9 months | Corrected
Initial Inspection |  | 9 | Inspection, testing, and maintenance for the fire alarm system was not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | Corrected: We have completed the Installation work of Fire Detection and Alarm System and we are maintaining Inspection, testing, and maintenance in accordance with NFPA 72. Also applied and submitted T&C documents to Accord Bangladesh on 04 November,2018.Now we are waiting for T&C inspection schedule. | Jun 30 2016 | On 17/10/2017: Integrated part of fire alarm system. On 11/03/2018: Integrated part of FA system On 22/10/2018: Integrated part of fire alarm system. On 20/05/2019: Corrected. On 28/09/2020: Corrected as per previous follow up. On 20/05/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 10 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Replace the single-station smoke alarms with automatic smoke detectors tied into the fire alarm system in accordance with NFPA 72. | Completed. We have installed automatic CFDS in the facilities which is right now in operation. | Jun 30 2016 | On 17/10/2017: Integrated part of fire alarm system. On 11/03/2018: Integrated part of fire alarm system. On 22/10/2018: Integrated part of fire alarm system. On 20/05/2019: Refer to issue 8 for T&C comment. On 28/09/2020: Integrated part of fire alarm system. On 07/09/2021 (Completed on 20/09/2021): T&CVI found that the system is corrected. See detailed T&CVI report. On 20/05/2024: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 11 | Inspection, testing, and maintenance records for the emergency lighting system were not in accordance of the ACCORD standards. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. |  | Jan 31 2016 | On 30/03/2017: Corrected. On 11/07/2017: Completed On 17/10/2017: Corrected. On 11/03/2018: Corrected. On 22/10/2018: Corrected. On 28/09/2020: Corrected. Maintaining. On 20/05/2024: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 12 | New Finding: The existing factory building with an occupiable floor greater than 10 m (33 ft.) above the finished grade is not protected with an approved standpipe system. | Provide a standpipe system throughout the building in accordance with NFPA 14. | Completed. We have installed standpipe system in the facility and its fully operational. | Jul 12 2016 | On 11/03/2018: Same condition found. L/C yet not opened. On 22/10/2018: Installation has been almost completed. Factory shall apply for T&C. On 20/05/2019: T&C observations (not limited to): Hydraulic calculation shall be proper, No installation completion record and T&C report from contractor, undersize reservoir, The distance between the bottom of the strainer and the bottom of the wet pit not meet standard, total head calculation could not be done, water level detector is missing, auto fill mechanism not provided for UGWR. All the deficiencies shall be remediated as soon as possible as per NFPA 13, 14, 20 and 22 prior to acceptance test again. On 28/09/2020: Factory has applied for T&C. Please see details in pre-T&C report. On 07/09/2021 (Completed on 20/09/2021): T&CVI found that final verification is required. See detailed T&CVI report. On 14/06/2022: Final VI found that after modification of the fire pump system, it is required again for final verification inspection on-site. See detailed Final VI Report. On 28/08/2023: Corrected. Final verification inspection (FVI) found that the standpipe system is approved. See detailed in the FVI report. On 20/05/2024: Corrected. System was found active and functional. | Design within 2 months, install within 4 months | Corrected
Follow Up Inspection |  | 13 | New Finding: Inspection, testing, and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers, and keep written records on-site, in accordance with NFPA 10. |  | Apr 24 2016 | On 05-01-2017: Corrected. On 30/03/2017: Corrected. On 11/07/2017: Completed On 17/10/2017: Corrected. On 11/03/2018: Corrected. On 22/10/2018: Corrected. On 28/09/2020: Corrected as per previous follow up. On 20/05/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 14 | New Finding: Exit stair is discharge the occupants inside the building. Location: Stair 3 (North-east stair) ground floor. | 1. Modify stair to discharge directly outside. Or 2. Provide 2-hr fire-rated exit passageway leading directly outside (vestibules to separate any storage/ production areas). Or 3. Provide sprinkler protection for discharge floor in accordance with NFPA 13. |  | Apr 25 2016 | On 30/03/2017: Corrected as per last follow-up inspection. On 11/07/2017: Comments same as before. On 17/10/2017: Corrected. On 11/03/2018: Corrected as per previous follow up. On 22/10/2018: Corrected. On 28/09/2020: Corrected as per previous follow up. On 20/05/2024: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 15 | New Finding: Cargo lift shaft and electrical/ utility riser shafts are not separated by proper fire rated construction on each floor (openings, non-rated doors, penetrations). | Provide a minimum 2-hr fire rated elevator shaft to separate it from each floor. Seal and/or protect all openings to maintain fire separations. |  | Jun 30 2016 | On 05-01-2017: Corrected as per previous follow up. On 30/03/2017: Corrected as per last follow-up inspection. Note - Factory has to installed fire rated door in lift in ground floor. On 11/07/2017: Separated. On 17/10/2017: Corrected. On 11/03/2018: Corrected as per previous follow up. On 22/10/2018: Corrected. On 28/09/2020: Corrected. On 20/05/2024: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 16 | New Finding (4th follow-up): Exit passageway is not separated by fire rated construction. Ground floor. | Separate the exit passageway (ceiling, floor, wall etc.) by 2- hr. fire-resistance rated construction and shall terminate at an exit discharge. |  | Aug 20 2016 | On 30/03/2017: In progress. On 11/07/2017: Rooms (store) & exit stars related to exit passageway have been separated by fire rated construction. On 17/10/2017: Corrected. On 11/03/2018: Corrected as per previous follow up. On 22/10/2018: Corrected. On 28/09/2020: Corrected as per previous follow up. On 20/05/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 17 | New Finding (5th Follow-up): Unsealed penetrations and openings are located in exit stair enclosures. (Ground Floor) (This issue also related to issue no. 4 & 14 ) | Seal all penetrations and openings in the wall of exit enclosure walls (full thickness of the wall) by fire rated materials to maintain the fire resistance rating. And Provide 1-hr rated fire door if openings are required for exit. |  | Dec 2 2016 | On 30/03/2017: Corrected. On 11/07/2017: Separated. On 17/10/2017: Corrected. On 11/03/2018: Corrected as per previous follow up. On 22/10/2018: Corrected. On 28/09/2020: Corrected as per previous follow up. On 20/05/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 18 | New Finding (5th Follow-up): Chemical storage area is not separated by fire-rated construction having non rated door and unsealed penetrations and openings. (Ground Floor) | Separate the chemical storage room by 2-hr fire rated construction. Seal all penetrations and protect the openings to maintain the required fire separations. Keep 16-points MSDS of all chemicals in the storage area. |  | Dec 2 2016 | On 30/03/2017: Corrected as per last follow-up inspection. On 11/07/2017: Separated On 17/10/2017: Corrected. On 11/03/2018: Corrected . On 22/10/2018: Corrected. On 28/09/2020: Corrected. On 20/05/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 19 | New Finding (5th Follow-up): The exit discharge path is less than 10 ft. wide and is not separated from the building interior. | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft. to provide a minimum 1-hr fire separation. |  | Dec 2 2016 | On 30/03/2017: Corrected. On 11/07/2017: Completed On 17/10/2017: Corrected. On 11/03/2018: Corrected . On 22/10/2018: Corrected. On 28/09/2020: Corrected as per previous follow up. On 20/05/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 20 | New Finding (5th Follow-up): Occupant load at 1st floor is 736 which exceeds the exit capacity of the 562 person. (1st Floor) | Reduce the occupant load to 562 Or Provide another stair (width minimum 1.4 m for current occupant load) with a capacity to meet the current occupant load. |  | Nov 20 2016 | On 30/03/2017: Corrected. On 11/07/2017: Reduced On 17/10/2017: Corrected. On 11/03/2018: Corrected . On 22/10/2018: Corrected. On 28/09/2020: Corrected. Reduced. On 20/05/2024: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 21 | New Finding (5th Follow-up): Manual on-off switch is provided for exit signage. | Remove manual on/off switches from exit signage units to prevent them from being switched off. |  | Nov 20 2016 | On 30/03/2017: Corrected. On 11/07/2017: Removed/deactivated On 17/10/2017: Corrected. On 11/03/2018: Corrected . On 22/10/2018: Corrected. On 28/09/2020: Corrected. Removed. On 20/05/2024: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 22 | New Finding (9th Follow-up): The exit stairs are not separated from work areas on each floor by fire-rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | Completed. We have installed fire doors at accounts room to separate stair from the discharge | Dec 18 2018 | On 17/10/2017: New finding. On 11/03/2018: Yet not finished. Fire door need to save the exit from passage way. On 22/10/2018: Interfacing of fire doors shall be confirmed in T&C. On 20/05/2019: Not completed. Some unprotected openings and penetrations found at stair enclosures wall and which is prohibited. Stair-1 discharge the occupant at ground floor exit passageway which also not separated from found floor various occupancy except storage. On 28/09/2020: Not corrected. Exit stair-1 discharge on ground floor and shall be separated properly from office rooms. On 20/05/2024: Corrected. Separated. | Within 2 month | Corrected
Follow Up Inspection |  | 23 | NEW FINDING (11 March, 2018): Dining and prayer room are not separated from production floor. | Remove the dining area; or, Separate the dining area from adjoining work area by 2 hours fire rated construction | Completed. Dining room is separated from Carpenter , Maintenance & Iron pattern room by providing fire doors. | Jun 11 2018 | NEW FINDING On 22/10/2018: Remedial work has not been done properly, Shall be provided with direct exit. On 20/05/2019: Separation is not completed. Moreover at least two direct safe exit is required from dining and prayer areas. On 28/09/2020: Still dining room not separated from Carpenter, Maintenance & Iron pattern room. On 20/05/2024: Corrected. Separated. | Within 3 Months | Corrected
Follow Up Inspection |  | 24 | New Finding: Compressor room is not properly separated by fire rated construction with other Occupancies/Areas at ground floor. | Compressor room shall be separated from other occupancies by a minimum 1-hr (2-hr for high-rise building) fire rated construction (wall, floor, slab etc.). Seal all penetrations and openings (door, window etc.) shall be protected by 0.75-hr (45 min) fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. Or Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. | Completed. We have separated compressor room from production floor by providing fire door | Jun 20 2019 | On 28/09/2020: Compressor room not separated from work area on ground floor. On 20/05/2024: Corrected. Separated. | Within 1 month | Corrected
Follow Up Inspection |  | 25 | New Finding: Width of aisles is less than 0.9m (36-in.) also some aisles are remain obstructed by storage or other obstruction. | Aisles shall be provided with a minimum unobstructed clear-width of 0.9 m (36 in.). Means of egress shall be maintained continuously free and clear of all obstructions/storage. Or Keep egress paths and stairs clear of storage. | Corrected: We have done the renovation works, revised the floor layout and also reorganized work stations & goods/materials. Now, no obstruction means of all egress by storage and new layout system continuously free and clear of all obstructions/storage and also maintained clear-width of 0.9 m (36 in.) | Jun 20 2019 | On 28/09/2020: Corrected. Provided. On 20/05/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 26 | New Finding: Areas used for in-process storage of combustible materials are open to the surrounding occupancy. | Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. or 3. Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Completed. We have separated accessories store from production floor by providing fire door at 1st floor. | Jun 20 2019 | On 28/09/2020: Accessories store not separated from production area on 1st floor. On 20/05/2024: Corrected. Separated. | Within 1 month | Corrected
Follow Up Inspection |  | 27 | New Finding: Headroom height at egress aisles is less than 2.03 m (6 ft 8 in) at top floors hanger area. | All means of egress shall have a minimum ceiling height of 2.3 m (7 ft 6 in.) with projections from the ceiling not less than 2.03 m (6 ft 8 in.) | Completed. Since the hanger is customized system, we have removed hanger ensuring 6 ft height | Jun 20 2019 | On 28/09/2020: During follow up inspection hanger height was found (6 ft) less than 2.03m in pressing area on 5th floor. On 20/05/2024: Corrected. Hanger removed from the said location. | Within 1 month | Corrected
Follow Up Inspection |  | 28 | New Finding: Exit sign not provided at some exits and some are not illuminated (damage/burnt out etc). | Lighted exit signs shall be placed at entrance to an exit. Additional exit signs shall be placed throughout the facility anywhere the continuation of the egress is not obvious. Lighted exit signs shall be provided with either battery backup or uninterruptable power supply systems and shall be continuously illuminated. | Corrected: We have placed and confirmed lighted exit signs at entrance to all exit. And we have confirmed additional exit signs throughout the facility anywhere the continuation of the egress is not obvious. And we have lighted exit signs with battery backup and uninterruptable power supply systems which continuously illuminated. | Jun 20 2019 | On 28/09/2020: Corrected. Provided. On 20/05/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 29 | New Finding (14th FUI): Room used for combustible storage (Newly constructed-'Fabric & accessories store' room) is not separated by fire rated construction from the surrounding occupancy. Location: 4th floor-Jacquard Section). | Separate the storage room by a minimum 1- hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | Completed: We have removed all combustible storage (Newly constructed-'Fabric & accessories store' room) from 4th floor and instrolled jacquard/knitting machine as per floor plan. Now no combustible storage in the 4th floor. | Aug 20 2024 | On 20/05/2024: New Finding. RPO Comments: On 18-MAY-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification

## Electrical
Date
12-Apr-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Helicon Ltd, Plot # 127, Dhaka EPZ (Old Area), Ganakbari, Savar, Savar, Dhaka
Date of Inspection |  | 2014-06-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | HT cable coiled near the transformer. | Excess length of existing HT cables coiled near transformer must be protected and laid safely. |  | Nov 10 2014 | On 07/03/15: Corrected | 3 Months | Corrected
Initial Inspection |  | 2 | 11kV cable entering electrical room is not protected. | All cables passing through permanent wall must be protected in steel pipes and remaining holes around the pipe must be sealed. |  | Oct 18 2014 | On 07/03/15: Corrected | 3 Months | Corrected
Initial Inspection |  | 3 | HT cable laid on, along with LT cables not separated. | Terminate the HT cable and LT cables separately on a cable tray/ladder and provide covers made of non-combustible material preferably metal to protect the cables’ insulation from physical damage as well as prevent entering debris, dust and lint. |  | Sep 30 2015 | On 12/01/16: Corrected. | 3 Months | Corrected
Initial Inspection |  | 4 | Silica gel in transformer breather, deteriorated. | Replace silica gel and must include in routine maintenance to check and maintain. |  | Aug 15 2015 | On 12/01/16: Corrected. | 1 Month | Corrected
Initial Inspection |  | 5 | Upper arcing horns on HV bushing are insulated by insulation tapes. | Arcing horns must not be insulated and should be properly aligned. |  | Aug 15 2015 | On 12/01/16: Corrected. | 3 Months | Corrected
Initial Inspection |  | 6 | Transformer neutral earth connected together with equipment earth. | Two separate earth connection & one separate and distinct Neutral connection must be provided for Transformer & Generator. These body must have earth connection with half of phase conductor/follow manufacturer recommendation. |  | Feb 29 2016 | On 24/04/16: Corrected | 3 Months | Corrected
Initial Inspection |  | 7 | Transformer guarded with wire mesh fencing. | Construct a separate room for the transformer by constructing barrier (brick) walls (fire rated wall) up to the ceiling; the minimum area of the transformer room should be 10-13 sq. m (according to BNBC 2006, Section-2.6.3). |  | Feb 29 2016 | On 24/04/16: Corrected | 3 Months | Corrected
Initial Inspection |  | 8 | Excessive lint/dust deposits on transformer. | Establish a cleaning program to keep neat and clean the substation room. To clean the transformer, shut down the main line and clean the exterior of the transformer. |  | Feb 20 2016 | On 24/04/16: Corrected | 1 Month | Corrected
Initial Inspection |  | 9 | Transformer placed on transport wheels. | Transformer must be permanently placed on foundation and wheel must be removed. |  | Aug 7 2014 | On 07/03/15: Corrected | 3 Months | Corrected
Initial Inspection |  | 10 | Transformer soak pit not constructed. | Construct soak pit around the transformer. |  | Oct 20 2014 | On 07/03/15: Corrected | 3 Months | Corrected
Initial Inspection |  | 11 | Combustible materials used in Generator room. | Remove excess reserved fuel and other combustible items stored in the generator. |  | Aug 5 2014 | On 07/03/15: Corrected | 1 Month | Corrected
Initial Inspection |  | 12 | Generator frame earth looped. | Connect generator earth directly to main earth strips without loop. |  | Aug 7 2014 | On 07/03/15: Corrected | 1 Month | Corrected
Initial Inspection |  | 13 | Oil accumulation in generator enclosure. | Generator and enclosure compartment must be always clean. |  | Aug 5 2014 | On 07/03/15: Corrected | 1 Month | Corrected
Initial Inspection |  | 14 | Generator enclosure/housing installed without foundation bolts. | Generator housing must be mounted firmly on its foundation with foundation bolts. |  | Oct 20 2014 | On 07/03/15: Corrected | 6 Months | Corrected
Initial Inspection |  | 15 | Excessive dusts deposit in Control Panel. | Control panel must be cleaned as part of regular maintenance and all openings in panel must be closed. |  | Aug 5 2014 | On 07/03/15: Corrected | 1 Month | Corrected
Initial Inspection |  | 16 | Gland holes in cable base plates left open. | Gland holes not used for cable entry must be sealed with blanking plates or plugs. |  | Oct 26 2014 | On 07/03/15: Corrected | 1 Month | Corrected
Initial Inspection |  | 17 | Panel base plates removed to allow cable entry. | Make circular hole at the base plate and provide cable gland according to the respective cable size for cable entry and exit so that the cables are not stressed on the sharp edges of the hole of panels. Provide covers (of non-combustible material) if any additional gap remains after installing cable glands. |  | Feb 29 2016 | On 24/04/16: Corrected | 3 Months | Corrected
Initial Inspection |  | 18 | Panel doors not connected to earth. | Provide earth connection for body and doors of metallic distribution boards using green cables preferably braid so that the metallic door remains at zero potential all the time. |  | Aug 1 2014 | On 07/03/15: Corrected | 1 Month | Corrected
Initial Inspection |  | 19 | LT panels installed without foundation bolts. | PFI panel must be mounted firmly on its foundation with foundation bolts. |  | Oct 20 2014 | On 07/03/15: Corrected | 6 Months | Corrected
Initial Inspection |  | 20 | Cables terminating at panel, not supported. | Cables must be protected from external damages and must be laid/ supported on cable trays. It is recommended to lay cable in covered trenches, under floor level or covered cable-ducts installed on floor. |  | Feb 29 2016 | On 24/04/16: Corrected | 3 Months | Corrected
Initial Inspection |  | 21 | Wires laid in cable trench are not protected. | Provide covers on the trench made of non-combustible material preferably concrete slab to protect the cables’ insulation from physical damage as well as prevent entering debris, dust and lint. |  | Aug 15 2015 | On 12/01/16: Corrected. | 3 Months | Corrected
Initial Inspection |  | 22 | Main cables delivering power from electrical room to factory floors are not supported on trays / raceways throughout their length. | Cables must be supported on trays / raceways / risers and protected against possible physical stress/damages throughout its length. |  | Sep 30 2015 | On 12/01/16: Corrected. | 6 Months | Corrected
Initial Inspection |  | 23 | LT cables laid on concrete floor. | Cables must be supported on cable trays and riser or must be laid in trench. |  | May 30 2016 | On 24/04/16: Not Corrected. New committed timeline : May 30, 2016. On 20/07/2016: Not Corrected. 02/11/2016: Corrected. | 6 Months | Corrected
Initial Inspection |  | 24 | Excessive lint/dusts deposit in cable trenches. | Clean the trench regularly and cover it. |  | Feb 29 2016 | On 12/01/16: Though this issue was corrected at Accord 1st follow-up, but observed again 2nd follow-up. New committed time line is given till 29th February, 16. On 24/04/16: Corrected. | 3 Months | Corrected
Initial Inspection |  | 25 | Wire/cable joints in wiring systems are not properly done and not protected adequately. | Wire and cable joints in wiring system must be avoided. Unavoidable joints must be tightly connected and protected. Heat shrink tubes may be used for cables. |  | Feb 29 2016 | On 24/04/16: Corrected | 1 Month | Corrected
Initial Inspection |  | 26 | Wirings exposed and not supported. | Wires and cables must be arranged and fixed on supports (tray/ladder) and protected if necessary, with metal sheets of adequate strength. |  | Feb 29 2016 | On 24/04/16: Corrected | 3 Months | Corrected
Initial Inspection |  | 27 | Wiring passing through walls are not protected. | Wirings passing through permanent walls must be protected with rigid conduits/pipes and remaining gaps must be sealed with fire rated materials. |  | Oct 20 2014 | On 07/03/15: Corrected | 3 Months | Corrected
Initial Inspection |  | 28 | Wire and cable terminated without cable lug or thimble. | Wire and cable termination must use thimble or cable lugs of proper size. |  | Oct 20 2014 | On 07/03/15: Corrected | 1 Month | Corrected
Initial Inspection |  | 29 | Wires inside panels not arranged. | Wires inside panel must be arranged and firmly fixed to prevent intentionally touching other live parts. |  | Aug 15 2015 | On 12/01/16: Corrected. | 1 Month | Corrected
Initial Inspection |  | 30 | Wiring in PVC flexible conduits are not supported. | Wiring in PVC conduit must be supported throughout its length. Most of the flexible PVC conduits used are not appropriate to substitute to wiring support and protection. |  | Oct 20 2014 | On 07/03/15: Corrected | 1 Month | Corrected
Initial Inspection |  | 31 | PFI panel installed without foundation bolts. | PFI panel must be mounted firmly on its foundation with foundation bolts. |  | Oct 20 2014 | On 07/03/15: Corrected | 3 Months | Corrected
Initial Inspection |  | 32 | Wiring and cables installed in boiler room are not protected. | Provide steel pipe for routing the cables inside the boiler room. Ensure the pipe is placed at a distance from the steam pipe and boiler so that heat does get transferred to the wiring steel pipe. |  | Aug 15 2015 | On 12/01/16: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: Cable channel near to heat source. | Ensure minimum 900mm distance between heat source and electrical wiring or provide adequate heat proof insulation. |  | Feb 29 2016 | On 24/04/16: Corrected | 3 Months | Corrected
Follow Up Inspection |  | 34 | New Finding: Multiple cables terminated at MCCB terminals/ Bus bar. | Terminate each power cable at single terminal and use proper sized cable lug. Multiple cables termination is allowed if all are soldered properly and powering to a single circuit. |  | Feb 29 2016 | On 24/04/16: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 35 | New Finding: Phase barrier/separator has not installed. | Put purposely made phase separator (rubber type) between two phases; also terminate cables by proper sized cable lugs and cover cable lugs by heat shrink. |  | Feb 29 2016 | On 24/04/16: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 36 | New Finding: MCCBs are not adjusted accordingly. | Adjust all the MCCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. |  | May 30 2016 | On 12/01/16: This issue is still open, final time extension for closing this issue is 29-02-16. On 24/04/16: Not Corrected. New committed timeline: May 30, 2016. On 20/07/2016: Not Corrected. On 02/11/2016: Not Corrected. On 05/01/2017: Corrected | 3 Months | Corrected
Follow Up Inspection |  | 37 | New Finding: Power cables are bent excessively. | Avoid power cable bending in electrical system; in unavoidable case bend cables without any stress but not less than 135 degree. |  | May 30 2016 | On 20/07/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 38 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/ undersize. | Resize earth lead cable/ECC for LT panel/MDB/DB; follow BNBC 2006 Part 8 chapter 2 section 2.8 for sizing your earthing cables (Usually ECC should be equal to the half of the respective phase cable). |  | Sep 30 2015 | On 12/01/16: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 39 | New Finding: Unterminated wires inside panel board. | Provide end cap or remove unterminated wires from panel board. |  | Aug 11 2015 | On 12/01/16: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 40 | New Finding: Compressor not fixed at base. | Fix the compressor at base with foundation bolt. |  | Aug 16 2015 | On 12/01/16: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Uncovered light at storage area. | Provide explosion proof cover on lighting fixture at storage area. |  | Aug 8 2015 | On 12/01/16: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 42 | New Finding: Hot spot observed during inspection. Thermo graphic scanning of the entire electrical system has not been tested and recorded. | Thermal inspection is needed to be conducted and recorded bi-annually. Record/Ask for the calibration certificate of the scanner. And corrective the issues raise from scanning. |  | Feb 20 2016 | On 24/04/16: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 43 | New Finding: Lightning Protection System(LPS) has not installed yet. | Calculate the risk index for lightning and if required design and install LPS for your factory. |  | May 30 2016 | On 12/01/16: This issue is still open, final time extension for closing this issue is 29-02-16. On 24/04/16: Not Corrected. New committed timeline: May 30, 2016. On 20/07/2016:Not Corrected. 02/11/2016:Not corrected. On 05/01/2017:Not Corrected. On 30/03/2017:Not corrected On 11/07/2017:Not corrected. On 17/10/2017:Not Corrected. 4th & 5th Floor is under construction. On 11/03/201:Not Corrected On 22/10/2018:Not corrected. Cross sectional area of main conductor is 43mm2 which is inadequate and the connection between junction box and earth electrode are also inadequate. On 28/04/2019: Corrected. | 4 Months | Corrected
Follow Up Inspection |  | 44 | New Finding: Electrical Single Line Diagram (SLD) has inadequate information which has no effectiveness. | Prepare SLD more informative and mention all the modification there as present in the factory thus anyone can understand it. |  | May 30 2016 | On 12/01/16: This issue is still open, final time extension for closing this issue is 29-02-16. On 24/04/16: Not Corrected. New committed timeline: May 30, 2016. On July-20,2016 Not Corrected. 02/11/2016: Not Corrected. On 05/01/2017: Corrected | 3 Months | Corrected
Follow Up Inspection |  | 45 | New Finding: Earth pits are not identifiable. Earth Pit resistance record is unavailable. | Identify each earth pit and mark it for periodic maintenance purpose. Record earth pit resistance for all the earth pit and do once in a year. |  | May 30 2016 | On 20/07/2016: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 46 | New Finding: Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | Hang this instruction near all electrical equipment (LT panel, MDB, FDB, DB, SDB) on a visible location. |  | Feb 29 2016 | On 24/04/16: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 47 | New Finding: Electric safety training program is not initiated/ conducted. | Electrical safety training and awareness program for the electrical personal and workers must be initiated and recorded. |  | Feb 29 2016 | On 24/04/16: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 48 | New Finding: Inadequate working clearance around the generator/s. | Working clearance around each generator should be 1.07m. If multiple generators are installed then the gap between two generators must be equal to the width of bigger generator. |  | May 13 2016 | On 24/04/16: Corrected | 3 Months | Corrected
Follow Up Inspection |  | 49 | New Finding: Panel/Distribution boxes are not readily accessible. | This panel/ distribution board is too low to operate quickly. Take necessary initiative thus every panel/ distribution board can be easily accessible. |  | Apr 13 2016 | On 24/04/16: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 50 | New Finding: Phases are imbalanced. | In three phase outgoing circuits all the phases shall be balanced. Calculate each phase's load and redistribute loads to make phases balanced. |  | Mar 13 2016 | On 24/04/16: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Indicator light is mounted without control device. | Indicator light should be connected with control device such as fuse or MCB. |  | Mar 13 2016 | On 24/04/16: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Cable tray is overloaded with excessive cables; eventually top cover has of no use. | Replace cable tray by wider one; or use additional cable tray to distribute cables thus 20-25% tray area are kept free (if you cover it). |  | Mar 13 2016 | On 24/04/16: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: Insulation resistance test of electrical cables is not accurate. | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off). |  | May 30 2016 | On 20/07/2016: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: Inadequate working space around panels and access to the panel is inconvenient. | Ensure at least 1 meter (or equal to the width of board, whichever is higher) working clearance in front of each panel. |  | May 30 2016 | On 20/07/2016: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding: Hot spot observed during inspection. | Thermal inspection is needed to be conducted and recorded bi-annually. Record/Ask for the calibration certificate of the scanner. And corrective the issues raise from scanning. |  | Aug 27 2016 | 02/11/2016: Not found any hot spot. | 1 Month | Corrected
Follow Up Inspection |  | 56 | New Finding: Inadequate working clearance around the transformer. | Working clearance around each transformer shall be 1.07m. If multiple transformers are installed then the gap between two transformers must not be less than 1 m. |  | Dec 31 2018 | On 28/04/2019: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 57 | New Finding: Safety program is initiated but has no influence. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. After the training, there should be exam to evaluate the influence of the training program. | Completed. Electrical safety training and awareness program have been conducted for the electrical persons. | Nov 10 2020 | On 07-Sep-2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: Electrical power cables are not identified properly. | Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables used in the system according to SLD. | Completed. We have provided proper identification for the cable, now its properly identified. | Oct 20 2021 | On 05/12/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. | We have submitted the updated electrical SLD to RSC and get approval on 11/07/2024. Now we are working as per approved SLD. We will complete the work withing 30/09/2024. | Feb 15 2024 | On 23/06/2024: Not corrected. Factory received SLD review feedback from RSC on 04 April 2024 with a status of "Need Modification". Factory has started modification work and will resubmit SLD to RSC promptly for approval. RPO Comments: On 11-SEP-2024 the design documents (SLD) have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design . | 2 Months | In Progress

## Boiler
Date
12-Apr-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Helicon Ltd, Plot # 127, Dhaka EPZ (Old Area), Ganakbari, Savar, Dhaka, Dhaka
Date of Inspection |  | 2022-05-10
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 9710 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have disposed the Boiler 9710 which effective from 2 November 2022 and there is no existence this boiler in Helicon Ltd. | Jan 19 2026 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 11100 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have installed emergency push switch outside of boiler room | Jan 19 2026 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 9710 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have disposed the Boiler 9710 which effective from 2 November 2022 and there is no existence this boiler in Helicon Ltd. | Jan 19 2026 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 11100 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Low Low Water Level (LLWL) is marked marked properly on water level gauge glass system. | Jan 19 2026 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 13325 | Necessary technical documents (manufacturing calculations, Piping and Instrumentation diagram, commissioning documents, data sheets of mountings, book, operation and maintenance manual, water treatment design and calculation) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We have arranged necessary technical documents to verify boiler design and operation parameters. | Jan 19 2026 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 13325 | Valves were observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. | We have removed the valve between the boiler and the pressure controller. | Dec 4 2025 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 13325 | Inconsistency was observed between the nameplate data, maker’s stamp and the CIoB provided certificate copy for the boiler regarding Maker’s Number. | Information provided in the nameplate and in the CIoB provided certificate shall be consistent. Any alteration shall be approved from the CIoB and a copy to be preserved on site. | Information provided in nameplate and in the CIoB provided certificate is consistent.Manufacturer acknowledge the same. | Jan 19 2026 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 13325 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | Proper insulation has been fixed. | Dec 19 2025 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 13325 | Drainage arrangement was not installed for one or more safety valves. | Drainage arrangement must be installed for all safety valves as per manufacturer published guideline or at the lowest point of outlet line. | Drainage arrangement has been installed for all safety valves as per manufacturer published guideline | Jan 19 2026 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 13325 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | Fuel/Gas line openings in boiler room has been sealed off | Dec 4 2025 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 13325 | The boiler air vent line was not directed to the outside of the boiler room. | The boiler vent line should be directed outside of the boiler room with proper support. | Completed this work: The boiler vent line in boiler room has been sealed off. A new vent line has now been installed and redirected outside the boiler room. The line is securely supported to ensure safe discharge and full compliance with applicable safety standards. | Dec 19 2025 | Comments on 03-Dec-2025: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. Moreover, the boiler air vent line should not be sealed, it should be directed outside the boiler room. RPO Comments: On 28-JAN-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 12 | BB 11100 | Valves were observed between the boiler and the water level limiter sensor. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. Any modification shall be consulted with the manufacturer. | Valves has been removed between the boiler and the water level limiter sensor. | Nov 26 2025 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | External visual inspection | 13 | BB 13325 | Drainage arrangement was not installed for one or more safety valves. | Drainage arrangement must be installed for all safety valves as per manufacturer published guideline or at the lowest point of outlet line. | Drainage arrangement has been installed for all safety valves as per manufacturer published guideline | Jan 19 2026 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 14 | BB 13325 | Salt and scale formation was observed on the waterside on furnace, tube and shell. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | Feed and boiler water quality and conditioning has been verified and monitored and boiler is properly cleaned. | Dec 19 2025 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 15 | BB 13325 | The inside of the boiler was found corroded due to inadequate water treatment. | Feed water must be externally or internally treated. The boiler operator should blow down regularly as per the manufacturer’s recommendation. Rapid boiling should be avoided. Shell and end plate thicknesses must be within the allowable limit specified by the manufacturer. | We are treating the boiler water as per manufacturere guideline and we have measured the Shell and end plate thicknesses and found in acceptable limit | Dec 19 2025 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 16 | BB 11100 | The boiler room did not have an adequate drainage system for spilt liquids. | An appropriate drainage system for the boiler room directed outside shall be provided. | We have developed the drainage system directed to outside of boiler room | Feb 19 2025 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 3 MONTHS | Pending Verification
Initial Inspection | Functional test inspection | 17 | BB 13325 | There was no acoustic or optical alarm when the limiter was activated. | An acoustic with optical alarm should be installed. | An acoustic with optical alarm has been istalled. | Dec 19 2025 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 18 | BB 11100 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | Steam Pressure Limiter has been installed | Dec 19 2025 | Comments on 03-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification