## Structural
Date
16-Apr-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | INTERLOOP BD LTD, 86,SOYDANA, NATIONAL UNIVERSITY, Gazipur
Date of Inspection |  | 2014-03-18
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Overloading of 5th floor during construction due to piles of waste materials and bricks | Remove any waste materials not required for construction and move to ground level. | We are removing the construction material from 5th floor.But we can clear it within 30th August-15. | Sep 30 2015 | On 1-Apr-2015: As Construction work is not finished yet, some stocks have been present there but most of the waste materials were found to be removed. On 19-Jul-2016: No construction and wastage materials was appeared during inspection. On 31-October-2019: Corrected in previous follow up inspection. During inspection construction and wastage material was not found on 5th floor. On 05-Oct-2020: Corrected from previous inspection. Factory has removed construction and wastage material were not found on 5th floor. On 18-Aug-2024: Corrected previously. | Immediate | Corrected
Initial Inspection |  | 2 | Overloading of 5th floor during construction due to piles of waste materials and bricks | Spread out remaining necessary construction equipment so as not to exceed design loads. | Done | May 15 2014 | On 1-Apr-2015: During the inspection, It was seen that the waste materials to be used for construction have almost been removed. As Construction work is not finished yet, some stocks have been present there in spreaded condition. On 19-Jul-2016: No construction and wastage materials was appeared during inspection. On 31-October-2019: Corrected in previous follow up inspection. During inspection construction and wastage material was not found on 5th floor. On 05-Oct-2020: Corrected from previous inspection. Factory has distributed live load as per accepted load plan limit (40 psf) at 5th floor. On 18-Aug-2024: Corrected previously. Wastage and construction materials were removed. During inspection, floor loading was found within the accepted load plan (60 psf at storage & dining area and 40 psf for all other areas). | Immediate | Corrected
Initial Inspection |  | 3 | Overloading of 5th floor during construction due to piles of waste materials and bricks | During construction ensure that workers do not store waste or other materials in piles on the slab. Waste should be removed immediately as it develops. | Done | Jun 15 2014 | On 1-Apr-2015: As Construction work is not finished yet, some stocks have been present there in spreaded condition. Waste materials were kept in spreaded condition. On 19-Jul-2016: No construction and wastage materials was appeared during inspection. On 31-October-2019: Corrected in previous follow up inspection. During inspection construction and wastage material was not found on 5th floor. On 05-Oct-2020: Corrected from previous inspection. construction and wastage material was not found on 5th floor. On 18-Aug-2024: Corrected previously. Wastage and construction materials had been removed. | Within 6 weeks | Corrected
Initial Inspection |  | 4 | Overloading of 5th floor during construction due to piles of waste materials and bricks | Implement and adhere to a loading plan across the whole structure. | We already got DEA acceptance from ACCORD on 14-Jan-2020. We also post the Live Load Plan in every floor. | Sep 30 2015 | On 1-Apr-2015: No load plan was found to be used during construction work. But construction work is going to end soon. DEA submitted on 24th March, 2015 does not contain any load plan to be maintained during construction work. On 19-Jul-2016: Live load was found within 42 psf during inspection. Factory is advised to marks the maximum stack height considering load capacity in storage areas and ensure that worker understand the marking. On 31-October-2019: Load plan had been prepared as a part of DEA but not accepted yet. During inspection load plan was found posted to each floor and overall loading was found below 42 psf. Load height marking was found also. Factory management had submitted revised DEA report to ACCORD on 07-November-2019 which is under review. On 05-Oct-2020: DEA of this factory was accepted on 14th January 2020 from Accord. During inspection accepted load plan was found posted at every floor and load was found bellow the load plan limit (60 psf at 1st floor storage area and 40 psf for all other areas) On 18-Aug-2024: Corrected previously. During inspection accepted load plan was found posted and floor loading was found below the allowable limit (60 psf at storage & dining area and 40 psf for all other areas). | Within 6 weeks | Corrected
Initial Inspection |  | 5 | Overloading of 5th floor during construction due to piles of waste materials and bricks | Ensure that future storage loads do not exceed design loads. | We already provide the load mark to control the live load & to keep the live load within design limit. | Sep 30 2015 | On 1-Apr-2015: Factory verbally promised not to make any storage for future construction as construction work is going to be finished very soon. On 19-Jul-2016: Factory has submitted the load plan along with DEA and it is currently under ACCORD review. On 31-October-2019: Load plan had been prepared as a part of DEA but not accepted yet. During inspection load plan was found posted to each floor and overall loading was found below 42 psf. Load height marking was found also. Factory management had submitted revised DEA report to ACCORD on 07-November-2019 which is under review. On 05-Oct-2020: DEA of this factory was accepted on 14th January 2020 from Accord. During inspection accepted load plan was found posted at every floor and load was found bellow the load plan limit (60 psf at 1st floor storage area and 40 psf for all other areas) On 18-Aug-2024: Corrected previously. During inspection accepted load plan was found posted and floor loading was found bellow the allowable limit (60 psf at storage & dining area and 40 psf for all other areas). | Within 6 months | Corrected
Initial Inspection |  | 6 | Uncontrolled loading at 1st and 3rd floor levels leading to potential issues of overloading. | With the assistance of in-house engineer, establish a maximum storage height to remain within design load of 3kN/m2. | We already provide the load mark to control the live load & to keep the live load within design limit. | Dec 31 2015 | On 1-Apr-2015: 3rd floor loading has been found to be within permissible load. But 1st floor loading on the south portion has been found to be very high. As per the factory, these two floors do not belong to the factory and they have been facing trouble to work according to the report. On 19-Jul-2016: Live load was found within 42 psf during inspection. Factory is advised to marks the maximum stack height considering load capacity in storage areas and ensure that worker. On 31-October-2019: Load plan had been prepared as a part of DEA but not accepted yet. During inspection load plan was found posted to each floor and overall loading was found below 42 psf. Load height marking was found also. Factory management had submitted revised DEA report to ACCORD on 07-November-2019 which is under review. On 05-Oct-2020: DEA of this factory was accepted on 14th January 2020 from Accord. During inspection load height marking was found at storage areas and load was found bellow the load plan limit (60 psf at 1st floor storage area and 40 psf for all other areas) On 18-Aug-2024: Corrected previously. During inspection accepted load plan was found posted and floor loading was found below the allowable limit (60 psf at storage & dining area and 40 psf for all other areas). Load height marking was found in the storage areas. | Within 6 weeks | Corrected
Initial Inspection |  | 7 | Uncontrolled loading at 1st and 3rd floor levels leading to potential issues of overloading. | Reduce all storage to established height. | We already provide the load mark to control the live load & to keep the live load within design limit. | Dec 31 2015 | On 1-Apr-2015: 3rd floor loading has been found to be within permissible load. But 1st floor loading on the south portion has been found to be very high. As per the factory, these two floors do not belong to the factory and they have been facing trouble to work according to the report. On 19-Jul-2016: Live load was found within 42 psf during inspection. No height marking was observed in storage area. Factory is advised to marks the maximum stack height considering load capacity in storage areas and ensure that worker. On 31-October-2019: Load plan had been prepared as a part of DEA but not accepted yet. During inspection load plan was found posted to each floor and overall loading was found below 42 psf. Load height marking was found also. Factory management had submitted revised DEA report to ACCORD on 07-November-2019 which is under review. On 05-Oct-2020: During inspection load height marking was found at storage areas and load was found bellow the load plan limit (60 psf at 1st floor storage area and 40 psf for all other areas) On 18-Aug-2024: Corrected previously. During inspection accepted load plan was found posted and floor loading was found below the allowable limit (60 psf at storage & dining area and 40 psf for all other areas). Load height marking was found in the storage areas. | Within 6 weeks | Corrected
Initial Inspection |  | 8 | Uncontrolled loading at 1st and 3rd floor levels leading to potential issues of overloading. | Apply the same rules established in the loading plan (set out in item 2) to all floors of the building, regardless of tenant. | We already provide the load mark to control the live load & to keep the live load within design limit. | Dec 31 2015 | On 1-Apr-2015: 3rd floor loading has been found to be within permissible load. But 1st floor loading on the south portion has been found to be very high. As per the factory, these two floors do not belong to the factory and they have been facing trouble to work according to the report. Submitted DEA does not contain any load plan. On 19-Jul-2016: Live load was found within 42 psf during inspection. No height marking was observed in storage area. Factory is advised to marks the maximum stack height considering load capacity in storage areas and ensure that worker. On 31-October-2019: Load plan had been prepared as a part of DEA but not accepted yet. During inspection load plan was found posted to each floor and overall loading was found below 42 psf. Load height marking was found also. Factory management had submitted revised DEA report to ACCORD on 07-November-2019 which is under review. On 05-Oct-2020: DEA of this factory was accepted on 14th January 2020 from Accord. During inspection accepted load plan was found posted at every floor and load was found bellow the load plan limit (60 psf at 1st floor storage area and 40 psf for all other areas) On 18-Aug-2024: Corrected previously. During inspection accepted load plan was found posted and floor loading was found below the allowable limit (60 psf at storage & dining area and 40 psf for all other areas). Load height marking was found in the storage areas. | Within 6 months | Corrected
Initial Inspection |  | 9 | Steel walkway exists between the factory and the adjacent building, with no drawings or design to support its construction. | Carry out structural design to check the capacity of the walkway for access loading. | Steel Walkway occupied other factory .Building owner strong commitment to us as soon as possible will reduce walkway. So we need small more time. | Jun 15 2014 | On 1-Apr-2015: ACCORD team found that access door has been closed with brickworks. But steel walkway was found in connected state with RC building during the inspection. And Submitted DEA does not include any check for steel walkway. On 19-Jul-2016: Factory does not use the walkway between the factory and the adjacent building by closed the door with brickwork. On 31-October-2019: Corrected in previous follow up inspection. Factory management had removed the walkway and closed the doors by brickwork. On 05-Oct-2020: Corrected from previous inspection. Steel walkway has been removed and closed now. On 18-Aug-2024: Corrected previously. Steel walkway had been removed. | Within 6 weeks | Corrected
Initial Inspection |  | 10 | Steel walkway exists between the factory and the adjacent building, with no drawings or design to support its construction. | Check connections between walkway and concrete buildings. | Now there is no steel walkway between the factory and adjacent building. | Mar 30 2015 | On 1-Apr-2015: DEA has been submitted on 24th March, 2015. But Submitted DEA does not contain the check for connections. Steel walkway was found to be existed although factory confirmed not to use the walkway anymore. On 19-Jul-2016: During inspection it was found that the adjacent building is used the walkway as storage. Factory has a plan to demolish it within one week. On 31-October-2019: Factory management had removed the walkway and closed the doors by brickwork. On 05-Oct-2020: Corrected from previous inspection. Steel walkway has been removed and closed now. On 18-Aug-2024: Corrected previously. Steel walkway had been removed. | Within 6 weeks | Corrected
Initial Inspection |  | 11 | Steel walkway exists between the factory and the adjacent building, with no drawings or design to support its construction. | Do not carry out further structural works without first carrying out thorough structural design and gaining local authority permission. | We will do not carry out further structural works without first carrying out thorough structural design and gaining local authority permission. | Mar 30 2015 | On 1-Apr-2015: ACCORD team found that steel stair door has been closed with brickworks. Steel walkway was found to be existed although factory confirmed not to use the walkway anymore. On 19-Jul-2016: During inspection it was found that the adjacent building is used the walkway as storage. Factory has a plan to demolish it within one week. On 31-October-2019: Factory management had removed the walkway and closed the doors by brickwork. On 05-Oct-2020: Corrected from previous inspection. Steel walkway has been removed and closed now. On 18-Aug-2024: Corrected previously. Steel walkway had been removed. | Within 6 months | Corrected
Initial Inspection |  | 12 | No clear lateral stability system is in place; this requires further detailed analysis. | Carry out a detailed structural assessment to determine the capacity of the existing structure, particularly against lateral loads. | We already got DEA acceptance from ACCORD on 14-Jan-2020. | Aug 30 2015 | On 1-Apr-2015: DEA has been submitted on 24th March, 2015. On 19-Jul-2016: Revise DEA has been submitted to ACCORD. On 31-October-2019: This issue is required to be covered in DEA report. Factory management had submitted revised DEA report to ACCORD on 07-November-2019 which is under review. On 05-Oct-2020: DEA has been reviewed and accepted from Accord on 14th January 2020. During DEA verification inspection all as-built and retrofitting drawings were found matched with onsite condition. Core locations were verified during onsite review inspection earlier. On 18-Aug-2024: Corrected previously. | Within 6 weeks | Corrected
Initial Inspection |  | 13 | No clear lateral stability system is in place; this requires further detailed analysis. | Implement any changes recommended by the detailed engineering assessment. | We already got DEA acceptance from ACCORD on 14-Jan-2020. | Aug 30 2015 | On 1-Apr-2015: DEA has been submitted on 24th March, 2015. On 19-Jul-2016: Revise DEA has been submitted to ACCORD. On 31-October-2019: Factory management had submitted revised DEA report to ACCORD on 07-November-2019 which is under review. So after getting acceptance from ACCORD factory will go for remedial work if recommended in DEA. On 05-Oct-2020: Factory has completed all required retrofitting works as per accepted drawing. Retrofitting completing certificate was also provided by the consultant. Material test reports were sent by mail after inspections. On 18-Aug-2024: Corrected previously. | Within 6 months | Corrected
Initial Inspection |  | 14 | Waterproofing layer and perimeter wall to be applied at roof level as part of the on-going construction works. | Apply a waterproof membrane across the full area of roof level. | We will apply a waterproof membrane across the full area of roof level within 31.12.15 | Dec 31 2015 | On 1-Apr-2015: Construction work is going on. Factory will apply the water-proofing layer soon. On 19-Jul-2016: Waterproof membrane has applied across the full area of the roof. On 31-October-2019: Corrected in previous follow up inspection. During inspection waterproofing membrane was found on roof top. On 05-Oct-2020: Corrected from previous inspection. Factory has provided water proofing layer on roof slab to drain out water. On 18-Aug-2024: Corrected previously. | Within 6 months | Corrected
Initial Inspection |  | 15 | Waterproofing layer and perimeter wall to be applied at roof level as part of the on-going construction works. | Construct a perimeter wall to a height of 1m, as detailed in building licence drawing. | We already Constructed a perimeter wall to a height of 1m, as detailed in building licence drawing. | Dec 31 2015 | On 1-Apr-2015: Light weight Guard Rails was found to be installed along perimeter. On 19-Jul-2016: Steel railing has constructed on the perimeter of the roof due to protect the falling hazard. On 31-October-2019: Corrected in previous follow up inspection. During inspection steel railing was found constructed at roof top. On 05-Oct-2020: Corrected from previous inspection. Factory has provided railing to prevent falling hazard. On 18-Aug-2024: Corrected previously. | Within 6 months | Corrected
Follow Up Inspection |  | 16 | Underground fire pump room and water reservoir below the plinth of the factory Building. | The Building engineer is required to check the capacity of RC wall and foundation of underground fire pump room & water reservoir. Also prepare load plan for suspended ground floor slab based on the floor loading capacity. | We have submitted releted documents to RSC concern engeineer for review dated on 17th July 2025. Also we send a mail for requested to arrange a meeting with RSC Enginner dated on 11th August 2025. | Oct 15 2024 | On 18-Aug-2024: During the inspection, an underground fire pump & water reservoir were found below the plinth of the factory building. The construction work was done, after the DEA acceptance on 14 Jan 2020. The Building engineer is required to check the capacity of RC wall and foundation of underground fire pump room & water reservoir. Also prepare load plan for suspended ground floor slab based on the floor loading capacity. Submit all the required documents to RSC by 15 Oct 2024. RPO Comments: On 16-Aug-2025, the design & documents are currently under RSC’s review. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 17 | Non-structural elements (water tanks and storage racks) were found unbraced. | Building engineer is required to provide adequate anchored/braced to avoid falling hazard during earthquake. | Done | Oct 15 2024 | On 18-Aug-2024: During the inspection, non-structural elements (water tanks on roof and storage racks on different floors) were found unbraced. Building engineer is required to provide adequate anchored/braced to avoid falling hazard during earthquake. RPO Comments: On 16-Aug-2025, the design & documents are currently under RSC’s review. | (within 6 weeks) | In Progress

## Fire
Date
16-Apr-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | INTERLOOP BD LTD, 86,SOYDANA, NATIONAL UNIVERSITY, Gazipur
Date of Inspection |  | 2014-03-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The boiler room located on the ground floor is not separated by fire-rated construction openings, non-rated doors, penetrations all present | Separate the boiler room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | We have done this | Jan 15 2016 | On 19-07-2016: Corrected. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Within 03 months | Corrected
Initial Inspection |  | 2 | The Generator and boiler room is located on the ground floor and is not separated by fire-rated construction openings, non-rated doors, penetrations all present | Separate the Generator room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | We have done this | Apr 5 2016 | On 19-07-2016: In progress. Generator room has been separated and has access from building exterior. Boiler room fire door re-arrangement work is in progress to avoid obstruction on egress aisles. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Within 03 months | Corrected
Initial Inspection |  | 3 | The Ground floor has areas used for combustible storage which are not adequately separated by fire-rated construction. | Provided dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Done | Apr 15 2016 | On 09/10/2016: Fire rated door has been installed. Factory has to interface fire rated door with FACP. Dining room is not separated yet. On 08/12/2016: Interfacing of fire rated door has not been done properly with FACP. On 28/11/2021: Corrected. Fire door installation and interfacing with FACP had been done. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Within 03 months | Corrected
Initial Inspection |  | 4 | The exit stairs are not separated from work areas other spaces on each floor by fire-rated construction. The second floor stairwell currently allows access to the adjoining building with no adequate rated fire separation | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | All exit stairs & adjoining building are separated from work areas by UL listed 1.5 hr Fire Door & fire Rated Construction . | Apr 15 2016 | On 09/10/2016: Fire rated door has been installed in all exit stairs. Factory has to interface all fire rated door with FACP. On 08/12/2016: Fire rated door has not been installed in office room. Interfacing of fire rated door has not been done properly with FACP. On 28/11/2021: Corrected. Fire door installation and interfacing with FACP had been done On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Within 03 months | Corrected
Initial Inspection |  | 5 | Unsealed penetrations and openings are located in the fire-rated floor/ceiling assemblies. | Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor level. Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation. | We have done this | Jan 5 2016 | On 28-03-2016: Completed On 19-07-2016: Corrected. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Within 03 months | Corrected
Initial Inspection |  | 6 | Unsealed penetrations and openings are located in exit stair enclosures | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | We have done this | Apr 5 2016 | On 28-03-2016: Still few unsealed penetrations has been found to exit stair. On 19-07-2016: Corrected. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Within 03 months | Corrected
Initial Inspection |  | 7 | Egress doors/gates are with locking features are provided at all building exits, exit stairs, along egress routes and the main discharge. All gates/doors were open and unlocked during the inspection. | Remove locking features from all egress doors / gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | We have done this | Mar 31 2016 | On 28-03-2016: The factory has removed all non compliant doors having non compliant locking features along egress routes except from main exit at ground level. On 19-07-2016: Corrected. Found same as previous follow-up. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 8 | Collapsible gates and sliding doors are provided at all building exits, exit stairs and along egress routes | Replace all gates / sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | We have done this | Jan 15 2016 | On 28-03-2016: Completed. Sewing direction of pocket doors should be to egress travel/outward. On 19-07-2016: Corrected. Found same as previous follow-up. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Within 01 month | Corrected
Initial Inspection |  | 9 | The day-care room does not have direct access to an exit stair on the ground floor | Relocate day-care room to ground floor with maximum travel distance of 9m (30 ft). | We have done this | Jan 5 2016 | On 28-03-2016: Completed On 19-07-2016: Corrected. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 10 | Exit stairs discharge inside the building open to production floor and storage space due to non rated fire doors in place | Provide 2-hr fire-rated exit passageway leading directly outside (vestibules to separate any storage areas). | We have done this | Apr 15 2016 | On 28-03-2016: The factory has separated the exit discharge area by fire rated construction (wall & door). The factory have to submit documents related to listing of all door assemblies, after that this issue will be solved. On 19-07-2016: Corrected. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 11 | Fire Protection The fire alarm system is antiquated, not a listed system, and dose not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | we have install UL/ LPCB Listed addressable fire Alarm System . | Apr 30 2016 | On 09/10/2016: Installation of fire alarm system has been completed. Factory will send test and commission request to Accord. On 08/12/2016: Installation of fire alarm system has been completed. Factory will send test and commission request to Accord. On 20/1/2020(J-H T&C): T&CVI found that final verification required. For details follow the full report. On 28/11/2021: Installation has been done. Pre T&C is on going. On 06/03/2023: T&CVI found that the fire alarm system is approved. See detail in the T&CVI report. On 04-Sep-25: Corrected. FACP was found functional and normal condition during inspection. Note: The fire alarm sound was not synchronized on the 4th floor. | Design within 4 months, install within 9 months | Corrected
Initial Inspection |  | 12 | Fire Protection Inspection, testing, and maintenance records for the fire alarm system were not available | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | We have done this | Jan 5 2016 | On 28-03-2016: Completed On 19-07-2016: Corrected. Found same as previous follow-up. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 13 | Fire Protection The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Replace the single-station smoke alarms with automatic smoke detectors tied into the fire alarm system. Configure the fire alarm system to initiate occupant notification upon activation of any two smoke detectors in addition to the manual fire alarm stations. | We removed Single Station Smoke alarm System & we have install UL/ LPCB Listed Automatic addressable fire Alarm System . | Apr 30 2016 | On 09/10/2016: It is an integrated part of fire alarm system. On 08/12/2016: It is an integrated part of fire alarm system. On 20/1/2020(J-H T&C): T&CVI found that final verification required. For details follow the full report. On 28/11/2021: Installation has been done. Pre T&C is on going. On 06/03/2023: T&CVI found that the fire alarm system is approved. See detail in the T&CVI report. On 04-Sep-25: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 14 | Emergency lighting did not function in test mode throughout factory floors bulbs burned out or broken | Regularly test the emergency lighting system on each floor and replace/repair lights as needed. | We have done this | Jan 5 2016 | On 28-03-2016: Completed On 19-07-2016: Corrected. Found same as previous follow-up. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 15 | Exit Signage not adequate throughout factory | Provide exit signs above all exits to the exterior and all doors to the exit stairs. | We have done this | Jan 10 2016 | On 28-03-2016: Completed On 19-07-2016: Corrected. Found same as previous follow-up. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 16 | New Finding in 1st follow up: Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes of all floors. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | We have done this | Jan 5 2016 | On 28-03-2016: Completed On 19-07-2016: Corrected. Found same as previous follow-up. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 17 | New Finding in 1st follow up: Inspection, testing, and maintenance for the emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | We have Inspected, tested and maintained the emergency lighting system in the accordance with The ACCORD standard & also keeping written records on-site. | Jan 5 2016 | On 28-03-2016: Completed On 19-07-2016: Corrected. Found same as previous follow-up. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Issue re-opened. No written record of ITM was found onsite during the inspection. On 04-Sep-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 18 | New Finding in 1st follow up: IPS, electrical Panel board located in the ground floor's both north and south exit stairs. | Keep egress path and stairs clear of storage | We have done this | Jan 5 2016 | On 28-03-2016: Completed On 19-07-2016: Corrected. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 19 | New Finding in 1st follow up: Flammable storage area (gas cylinder) is not separated by fire-rated construction (openings, non-rated doors, penetrations). | Separate the hazardous materials / flammable liquid storage room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | Facility management has already purchased the require fire rated door and door is in housed 26.2.2026. Saturday on 28.2.2026 the door will be fixed for proper separation cylinder room at ground floor. | Jan 20 2016 | On 28-03-2016: Completed On 19-07-2016: Corrected. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Issue re-opened. LPG cylinders and high-pressure CNG pipeline & appliances were found without fire separation. On 04-Sep-25: The factory submitted the proposed design for a separate room for LPG cylinders to the RSC on 03 September 2025. The LPG cylinders, high-pressure CNG pipeline, and associated appliances have been removed from the main building. Work on constructing the separated room has commenced; however, it is still in progress and not yet completed. RPO Comments: On 02-mar-2026, The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Follow Up Inspection |  | 20 | New Finding in 1st follow up: The building has occupied floor greater than 10 meter (33 feet) and is not provided with Class-I standpipe system as per NFPA14 throughout the building. | Provide Class-I standpipe system as per NFPA14 throughout the building | We have install UL Listed Fire Pump & Class-iii System Standpipe As per NFPA -14 & 20 | Apr 30 2016 | On 19-07-2016: In progress. ACCORD has reviewed stand pipe system drawing submitted by factory. Factory reported that they are in process of opening LC for importing components. On 09/10/2016: L/C has not been opened for fire protection system. On 08/12/2016: L/C has not been opened for fire protection system. On 28/11/2021: Installation has been done. Pre T&C is on going. On 06/03/2023: T&CVI found that the system requires final verification inspection. See detail in the T&CVI report. On 17/01/2024: The Final Verification Inspection has been conducted and the system is approved. See the details in FVI report. On 04-Sep-25: Corrected. | Design within 2 months, install within 6 months | Corrected
Follow Up Inspection |  | 21 | New Finding in 2nd follow up : Parapets or guards are not according to the standard height. | Provide parapets or guards with a minimum height of 1067mm (42 inch.). | We have done this | Feb 5 2016 | On 28-03-2016: Completed On 19-07-2016: Corrected. Found same as previous follow-up. On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 22 | New Finding in 2nd follow up : Manual on-off switch is provided for emergency lightings/exit signage units. | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. | We have done this | Apr 5 2016 | On 28-03-2016: The factory has started the work and will be completed within committed timeline. On 19-07-2016: Partially corrected. Manual on-off switch was seen with few emergency exit signage. On 09/10/2016: Not Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 23 | New Finding (4th follow-up): Unsealed penetrations and openings are located in the fire-rated floor/ceiling assemblies between 3rd, 4th & 5th floor around steam pipeline. | Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor level. Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation. | We have done this | Aug 19 2016 | On 19-07-2016: New Finding On 09/10/2016: Not Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 24 | New Finding (4th follow-up): Unsealed penetrations and openings are located in exit stair enclosures (exit stair-2) | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | We have done this | Aug 19 2016 | On 19-07-2016: New Finding On 09/10/2016: Corrected. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 25 | New Finding (4th Follow-up): Dinning space is not separated from production floor and storage area | Remove dinning space from this location or, alternatively provide minimum 3-hour fire rated separation | We are very much concern about the workers safety. We will be relocated the packing section and confirm the workers safety first. We will share drawing design area measurement within the April 20, 2026 with you. Also physical work/separation work will be completed within the May, 15, 2026. We are humble requesting to you, please conceder the time for smooth relocation. | Aug 19 2016 | On 19-07-2016: New Finding. On 09/10/2016: Civil work is going on. Fire rated door has not been installed yet. On 08/12/2016: Corrected. On 28/11/2021: Corrected. On 06/03/2023: Corrected. On 04-Sep-25: Issue has been reopened. Dining (E4-180) area is not separated from packing area (G2) and medical (D1) with fire rated assemblies. Location: 1st Floor of Main production Building. RPO Comments: On 02-mar-2026, The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 month | In Progress
Follow Up Inspection |  | 26 | New finding (9th Follow-up) : Exit sign is not provided at exit. Location: Bonded Wearhouse on ground floor. | Illuminated exit signs shall be placed at entrance to an exit. Additional exit signs shall be placed throughout the facility anywhere the continuation of the egress is not obvious. Illuminated exit signs shall be provided with either battery backup or uninterruptable power supply systems and shall be continuously illuminated | We have installed exit sign in placed with uninterruptable power supply systems that shall be continuously illuminated. | Apr 21 2023 | On 06/03/2023: New finding. On 04-Sep-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 27 | New finding (9th Follow-up) : Inspection, testing, and maintenance for the Standpipe system is not in accordance with NFPA 14, 25 or as per RSC standard. | Inspect, test and maintain the standpipe system in accordance with NFPA 14, 25 or as per RSC standard and keep written records on-site | We have Inspected, tested and maintained the emergency lighting system as per RSC standard & also keeping written records on-site. | Apr 21 2023 | On 06/03/2023: New finding. On 17/01/2024: The Final Verification Inspection has been conducted and the system is approved. See the details in FVI report. On 04-Sep-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 28 | New finding (9th Follow-up) : Inspection, testing, and maintenance for the fire pump is not in accordance with NFPA 20, 25 or as per RSC standard. | Inspect, test and maintain the fire pump in accordance with NFPA 20, 25 or as per RSC standard and keep written records on-site. | We have Inspected, tested and maintained the system as per RSC standard & also keeping written records on-site. | Apr 21 2023 | On 06/03/2023: New finding. On 17/01/2024: The Final Verification Inspection has been conducted and the system is approved. See the details in FVI report. On 04-Sep-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 29 | New finding (9th Follow-up): Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10 and RSC standards. | We have Inspected, tested and maintained the system as per RSC standard & also keeping written records on-site. | Apr 21 2023 | On 06/03/2023: New finding. On 04-Sep-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 30 | New finding (10th Follow-up): Electrical cable is passing through the exit enclosure. Location: Ground Floor Stair 2 of Main production Building. | No other penetration into and through the exit enclosure except for fire alarm equipment electrical raceway, required exit doors, sprinkler piping, standpipes, and electrical conduit serving the exit enclosure is permitted in accordance with section 6.14.4 of RSC Technical Guidelines (Standard)¹ V1.0. So, relocate the electrical wires/raceways to somewhere else avoiding the exit enclosure, and seal the created unprotected openings with a minimum of 1.5 hours listed/certified fire-rated materials. Installation shall be as per manufacturer published installation guideline and the certification authority guideline to ensure the fire-rating. Or seal the penetration by 2-hr masonry construction. | The facility has removed Electrical Cable from passing through the exit enclosure and Installed outside as per fire rated materials. | Dec 4 2025 | On 04-Sep-25: New finding. RPO Comments: 01-Jan-2026, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Follow Up Inspection |  | 31 | Directional signs are not provided where direction of the path of travel to an exit has changed. Location: Bonded warehouse, ground Floor, Main production Building. | Illuminated directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.11.3. | Illuminated directional signs have been installed at all required locations | Oct 4 2025 | On 04-Sep-25: New finding. RPO Comments: 01-Jan-2026, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification

## Electrical
Date
16-Apr-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | INTERLOOP BD LTD, 86,SOYDANA, NATIONAL UNIVERSITY, Gazipur
Date of Inspection |  | 2014-03-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Excessive dust was found inside of the changeover switch panel. | Disconnect the panel from the electrical service & clean interior components of the panel to remove all dust and debris. Seal/block all openings(kept unused at cable entry point or other)within the enclosure to prevent dust and debris from entering inside. | We have done this | Jul 30 2014 | On 01/04/2015: Corrected. | Within 1 Month | Corrected
Initial Inspection |  | 2 | MCCB mounted on wooden board without enclosure. | Remove the wooden board and install the MCCB into an enclosure made of galvanized plain sheet (metallic) of minimum thickness 20 SWG in order to reduce the risk of spreading fire due to short circuit. | We have done this | Sep 30 2014 | On 01/04/2015: Corrected. | Within 3 Months | Corrected
Initial Inspection |  | 3 | Lint/dust was found inside the cable duct. | Clean the dust inside the cable-duct and provide cover for the cable-duct to prevent the further accumulation of dust inside the duct. | We have done this | Sep 30 2014 | On 01/04/2015: Corrected. | Within 3 Months | Corrected
Initial Inspection |  | 4 | 1.Multiple cables connected at a point on the bus-bar. 2. Lug was found punched improperly during termination. | 1. Connect all the cable individually on bus-bar. 2. Use proper crimping tool or hydraulic puncher to punch the cable-socket/lug during termination the lug, PIB tape and then PVC cable- sleeve shall be used instead of using only PVC/electric-tape. | We have done this | Jun 30 2015 | On 01/04/2015: Not corrected. Extension has been given till 31.05.15 to close this issue. On 05/01/2016: Corrected. | Within 1 Month | Corrected
Initial Inspection |  | 5 | Damaged flexible conduit goes under the table without proper support. | Wiring for connections to machines shall be carried in steel pipes or cable tray running in concrete or over the floor. Where steel pipe/tray cannot be used, industrial graded flexible pipes shall be used with proper support. See standard details in Accord Standard 10.3.2.4. | We have done this | Sep 30 2014 | On 01/04/2015: Corrected. | Within 3 Months | Corrected
Initial Inspection |  | 6 | Cables are connected to the panel without providing any support (without gland fixation). | Block the opening in base plate or cable-entry-openings & keep the provision for gland fixation for incoming and outgoing cables shall be connected in the panel through the glands. | We have done this | Feb 15 2016 | On 01/04/2015: Not corrected. Extension has been given till 31.05.15 to close this issue. On 05/01/2016: Not corrected. The arrangement done by the factory is inadequate. New committed timeline is given till February 15, 2016. On 28/03/2016: Corrected. | Within 3 Months | Corrected
Initial Inspection |  | 7 | Cable is run in the ceiling at an angle. | Cables shall be run either horizontally or vertically (not at an angle). | We have done this | Jun 30 2015 | On 01/04/2015: Not corrected. Extension has been given till 31.05.15 to close this issue. On 05/01/2016: Corrected. All wiring have been done in acceptable way. | Within 3 Months | Corrected
Initial Inspection |  | 8 | Earth wire of SDB door is not installed. | Provide earthing connections for all panels door in the factory (with flexible copper braids preferably). | We have done this | Jun 30 2015 | On 01/04/2015: Not corrected. Extension has been given till 31.05.15 to close this issue. On 05/01/2016: Corrected. | Within 1 Month | Corrected
Initial Inspection |  | 9 | Wire is jointed inside panel and the wire is terminated without providing any cable-socket. | Terminate all the cable providing copper cable socket/lug on bus-bar individually with using proper crimping tools for punching the lug/connector. | We have done this | Feb 15 2016 | On 01/04/2015: Not corrected. Extension has been given till 31.05.15 to close this issue. On 05/01/2016: Not corrected. The arrangement done by the factory is inadequate. Many cable joints are found in cable duct and few in DB panels. New committed timeline is given till February 15, 2016. On 28/03/2016: Corrected. | Within 1 Month | Corrected
Initial Inspection |  | 10 | Burning sign was observed at the termination point of MCB, which might be induced from the loose connection. | Replace the burnt MCBs and make sure all the termination are tight. Arrange a periodic inspection and thermal scan for identifying the loose connection and overloading which may induce unexpected heat-rise. | We have done this | Jul 30 2014 | On 01/04/2015: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 11 | New Finding: Cables are hanging without support. Cable terminals may be in tension. | Use cable tray/ladder to support cables at any where to keep cable out of tension. | We have done this | Feb 15 2016 | On 05/01/2016: Not corrected. New committed timeline is given till February 15, 2016. On 28/03/2016: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 12 | New Finding: Generator output supply terminal box open. | Cable terminating at the generator box must be fixed bottom plate with cable gland. | We have done this | Aug 30 2015 | On 05/01/2016: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 13 | New Finding: Distribution Panel and Water pump installed under stairways. | The distribution panel and water pump should not be installed under the stairways. It shall be located in a confined place with entrance control mechanism where only authorized personnel can have access. | We have done this | Jun 30 2015 | On 05/01/2016: Corrected. No pump or distribution panel are found under stairways. | Within 3 Months | Corrected
Follow Up Inspection |  | 14 | New Finding: Inadequate working space around panels and access to the panel is inconvenient. | Ensure at least 1 meter (or equal to the width of board, whichever is higher) working clearance in front of each panel. | We have done this | Jun 30 2015 | On 05/01/2016: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 15 | New Finding: Sub station / Generator room has inadequate illumination. | Ensure adequate illumination in the sub station room thus any maintenance can be done comfortably (150 lux should be maintained). | We have done this | Jun 30 2015 | On 05/01/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 16 | New Finding: Cable duct/channels / trench are filled with fluffs (lint/dust). | Clean all the cable channels/ducts; then seal them for permanent (you may use checkered/perforated plate at the bottom). But ensure that you have used proper sized cable for all of your electrical loads. | We have done this | Jun 30 2015 | On 05/01/2016: Corrected. Cable ducts are covered. | Within 3 Months | Corrected
Follow Up Inspection |  | 17 | New Finding: Cables passing through wall/floor slab are not protected at the entry/exit point(s). | Cables passing through permanent wall/floor slab must be protected. Seal the opening by fire rated material protecting power cables thus no smoke can pass through this. | We have done this | Jun 30 2015 | On 05/01/2016: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 18 | New Finding: Cables in service are joined (splicing) between terminations. | Existing cables with joints must be spliced using butt splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. | We have done this | Jun 30 2015 | On 05/01/2016: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 19 | New Finding: Generator frame is not earthed by 2 separate and distinct earth. | Generator must be connected to earth securely at least two points. | We have done this | Feb 15 2016 | On 05/01/2016: Not corrected. New committed timeline is given till February 15, 2016. On 28/03/2016: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 20 | New Finding: Batteries are kept on floor. | Use non-flammable case/shelf to store battery | We have done this | Jun 30 2015 | On 05/01/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 21 | New Finding: Generator output cables (laid on floor) are not protected and supported. | If possible route all the power cable through overhead cable tray. Or ensure adequate protection for power cables arranging cable trench with checkered plate. Do not make any arrangement that obstacle personnel's movement within working clearance. | We have done this | Feb 15 2016 | On 05/01/2016: Not corrected. New committed timeline is given till February 15, 2016. On 28/03/2016: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 22 | New Finding: Thermal issue detected. Thermographic scanning of the entire electrical system has not been tested and recorded. | Thermographic scanning for the entire electrical system must be performed on a bi-annual basis and recorded. | We have done this | Oct 30 2015 | On 05/01/2016: Corrected. | Within 4 Months | Corrected
Follow Up Inspection |  | 23 | New Finding: Phase barrier/separator has not installed. | Put purposely made phase separator (rubber type) between two phases; also terminate cables by proper sized cable lugs and cover cable lugs by heat shrink. | We have done this | Aug 30 2015 | On 05/01/2016: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 24 | New Finding: Panel identification and danger signs not marked on the panels. | Panels must be identified and danger signs marked on the panels. Each panel must be provided with schematic diagram of the panel showing branch circuits. | We have done this | Aug 30 2015 | On 05/01/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 25 | New Finding: Cable trays and channel cover left open. | Fix the cover properly with the channel or trays so that lint and dust cant get inside. | We have done this | Jun 30 2015 | On 05/01/2016: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 26 | New Finding: Wiring is not protected from excessive heat near boiler. | Wires close/attached to boiler must be protected from external heat. In unavoidable case use metal type flexible pipe. Again Power cable should keep 0.9m apart from hot area. | We have done this | Feb 15 2016 | On 05/01/2016: Not corrected. New committed timeline is given till February 15, 2016. On 28/03/2016: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 27 | New Finding: Control devices are not securely fixed. | Control devices and switches installed inside panel must be securely fixed. | We have done this | Jun 30 2015 | On 05/01/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding: Cables terminated at electrical bus bar/MCCB without cable lugs. | Terminate all the power /earth/neutral cable with proper sized cable lug. | We have done this | Jun 30 2015 | On 05/01/2016: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 29 | New Finding: Multiple cables terminated at MCCB terminals/ Bus bar. | Terminate each power cable at single terminal and use proper sized cable lug. Multiple cables termination is allowed if all are soldered properly and powering to a single circuit. | We have done this | Jun 30 2015 | On 05/01/2016: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 30 | New Finding: Multiple cables connected in the bus bar through single lugs. | Each cable must be connected in the bus bar through single lugs. | We have done this | Aug 30 2015 | On 05/01/2016: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 31 | New Finding: Lightning Protection System(LPS) has not installed yet. | Design and Install LPS for your factory; Factory have to submit LPS design to Accord before starting installation. | We have done this | May 15 2016 | On 05/01/2016: Not corrected. New committed timeline is given till February 15, 2016. On 28/03/2016: Not corrected. LPS Design is available. Drawing needs some modification. Redesign LPS & install accordingly. New committed timeline is given till 15/05/2016. On 19/07/2016: Not corrected. LPS design seems fine. Installation process is going on. On 09/10/2016: Not corrected. LPS installation is improper. On 08/12/2016: Not corrected. On 20/02/2017: Not corrected. On 28/11/2021: Not corrected. Insert correct design information. Factory has completed installation - but inadequate conductor connection to air terminal baseplate. On 06/03/2023: Corrected. | Within 4 Months | Corrected
Follow Up Inspection |  | 32 | New Finding: Electrical Single Line Diagram (SLD) is unavailable. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by Accord. | We have done this | Apr 30 2016 | On 05/01/2016: Not corrected. New committed timeline is given till February 15, 2016. On 28/03/2016: Not corrected. This drawing is available but it does not contain all required information for whole building. This issue is not closed yet. New committed timeline is given till 30/04/2016. On 19/07/2016: Corrected. The drawing is as-built for the occupied floors for which the initial inspection was done. | Within 4 Months | Corrected
Follow Up Inspection |  | 33 | New Finding: Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | Hang this instruction near all electrical equipment (LT panel, MDB, FDB, DB, SDB) on a visible location. | We have done this | Jun 30 2015 | On 05/01/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 34 | New Finding: Insulation resistance test of electrical equipment is not performed. | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off). | We have done this | Sep 30 2015 | On 05/01/2016: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 35 | New Finding: Earth pit resistance record is unavailable. | Record earth pit resistance for all the earth pit and do once in a year. | We have done this | Sep 30 2015 | On 05/01/2016: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 36 | New Finding: There is no programmed schedule for periodical inspection & testing of electrical equipment. | Develop an electrical maintenance program that includes inspections and testing of the electrical systems (preventive, proactive and breakdown maintenance). | We have done this | Sep 30 2015 | On 05/01/2016: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 37 | New Finding: Earth pits are not identifiable. | Identify each earth pit and mark it for periodic maintenance purpose. | We have done this | Sep 30 2015 | On 05/01/2016: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 38 | New Finding: Maintenance record doesn’t reflect with house keeping (fake record). | Maintenance in charge/Safety officer should check the record with housekeeping. | We have done this | Apr 30 2016 | On 05/01/2016: Not corrected. New committed timeline is given till February 15, 2016. On 28/03/2016: Not corrected. New committed timeline is given till 30/04/2016. On 19/07/2016: Not corrected. No progress was found for preparing full maintenance documents. No proper schedule, checklists and records documents are maintained. On 09/10/2016: Not corrected. On 08/12/2016: Not corrected. Report keeping must be continued. On 20/02/2017: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 39 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly. | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. | We have done this | Mar 15 2016 | On 28/03/2016: Corrected. 200 A breaker with 50 rm cable. Set point was at 140 A. | Within 2 Months | Corrected
Follow Up Inspection |  | 40 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/ undersize. | Resize earth lead cable/ECC for LT panel/MDB/DB; follow BNBC 2006 Part 8 chapter 2 section 2.8 for sizing your earthing cables (Usually ECC should be equal to the half of the respective phase cable). | We have done this | Apr 30 2016 | On 28/03/2016: Not corrected. New committed timeline is given till 30/04/2016. On 19/07/2016: Not corrected. Earth Continuity Conductor is still inadequate. On 09/10/2016: Not corrected. MDB-1 do not have earth connection. Other DB has but inadequate. On 08/12/2016: Although proper in size, Earth lead cable to SDBs are looped. On 20/02/2017: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 41 | New Finding: Earth connections are not segregated. Generator earthing and system earthing are connected in same pit. | Ensure separate earthing connection for all neutrals, generator body, transformer body, electrical system and Lightning Protection System. Need to provide identification for all of them. | We have done this | Mar 15 2016 | On 28/03/2016: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 42 | New Finding: New floors are not covered in SLD. As built Single Line Diagram (SLD) of the new floors is not available. | Amend Electrical SLD properly. All the required information of those floors must be mentioned there; and it shall be updated when you do significant amount of changes of your electrical system. | We have done this | Nov 20 2016 | On 19/07/2016: New floors have been added in this factory. Hence the drawing needs addition of circuits for those floors. The wiring is not done yet for those floors. After completion of this wiring, SLD needs to be redrawn as per as-built condition for whole floors which shall cover all information including circuit marking and load specifications. On 09/10/2016: Not corrected. Time extension is given till 20/11/2016. On 08/12/2016: Not corrected. On 20/02/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 43 | New Finding: Multiple termination and Loop connection has been used powering multiple MCB/MCCBs. | Any kind of multiple termination and looped power connection must be avoided from electrical installation. | We have done this | Nov 20 2016 | On 09/10/2016: Not corrected. Time extension is given till 20/11/2016. On 08/12/2016: Corrected. | 4 Weeks | Corrected
Follow Up Inspection |  | 44 | New Finding: Cables are connected to earth bus bar in a congested manner. | Earth bus bar sized shall be determined according to main power cable (or bus bar if those are ok). | We have done this | Jan 23 2017 | On 20/02/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Earth connections for different electrical installation are not segregated. | All the earth connections (transformer, generator and electrical systems) must be segregated and clearly marked (for TT earthing system). | We have done this | Jan 23 2017 | On 20/02/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Neutral earthing of generator (400 kVA) is undersize (2 6 mm dia copper cable to pit). | Neutral earthing shall be provided as per BNBC or after consulting supplier. Supplier documentation on neutral earthing requirement must be made available during inspection. | We have done this | Jan 23 2017 | On 20/02/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Cables passing through wall/floor slab are not protected at the entry/exit point(s). | Cables passing through permanent wall/floor slab must be protected. Floor to floor openings shall be sealed by proper type materials (consult with fire expert). | We have done this | Mar 20 2017 | On 20/02/2017: Not corrected. Timeline extended up to 23/03/2017. On 28/11/2021: Not corrected. Factory has solved the issue at several places. But the issue still exists at several places. On 06/03/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Electrical power cables are not identified properly. | Proper identification (by using cable marker, tag, Colored heat shrink) shall be done on major power cables used in the system according to SLD. | We have done this | Mar 30 2017 | On 28/11/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: MCB is installed without any enclosure. | Each MCCB/MCB must be enclosed by proper type material. the material must not be more than 18 SWG graded. | We have done this | Jan 10 2021 | On 06/03/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Electrical devices are not fixed at base (socket). | All electrical component must be fixed at base with proper arrangement. | We have done this | Jan 10 2021 | On 06/03/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Cable duct/channels are filled with fluffs (lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | We have done this | Feb 10 2021 | On 06/03/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 52 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | We have done this | Feb 10 2021 | On 06/03/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 53 | New Finding: Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. | We have done this | Feb 10 2021 | On 06/03/2023: Not corrected. They are working on this issue On 05/02/2024: Not corrected. Some progress (approx. 40%) is observed as SLD is accepted from RSC on June 2023. Still some load marking, cable and breaker identification, higher size individual protection and inadequate ECC of generator observed. RPO Comments: On 09-July-2024, The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. On 18/08/2024: Not corrected. Some higher-size breakers (LT Panel), fuses & inadequate ECC of generator were observed. Overall, the progress on this issue is approx. 60%. RPO Comments: 23-Oct-2024, the factory management reported the remediation completion. This item will be verified in the next inspection. On 21/01/2025: Not corrected. Progress has been observed since the last follow-up (individual protection found okay, load identification found partially okay). However, found some observations including CB rating mismatch, cable identification missing, earthing layout mismatch including inadequate ECC for 165 kVA generator etc. Most of the observations are found in substation area. RPO Comments: 16-Mar-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. On 15/06/2025: Not corrected. No significant progress has been observed since last follow-up. Issues include earthing information mismatch, panel earthing inadequate, CB rating mismatch, loads are not properly identified etc. RPO Comments: 11-Nov-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. On 12/04/2026: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 54 | New Finding: Periodicity of insulation resistance test record is not continued. | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | We have done this | May 25 2023 | On 05/02/2024: Not corrected. Some progress is observed but all power cables from 25 sq mm needs to be tested. RPO Comments: 27-May-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 18/08/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 55 | New Finding: Periodicity of thermographic survey is not continued. | Thermography survey shall be conducted on entire electrical system in the facility at least twice in a year. And the remediation suggestions mentioned in the report shall be carried out. | We have done this | May 25 2023 | On 05/02/2024: Not corrected. Need to perform at least twice a year. RPO Comments: 27-May-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 18/08/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 56 | New Finding: Periodicity of earth Pit resistance test record is not continued. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. | We have done this | May 25 2023 | On 05/02/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 57 | New Finding: Uncovered/Perforated type cable tray/PVC pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | We have done this | May 25 2023 | On 05/02/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 58 | New Finding: Safety training materials inadequate. No policies for PPE & LOTO (Lock-Out-Tag-Out) are introduced for safety of the personnel during any kind of the personnel during any kind of maintenance work. | Safety Training materials need to be updated covering all aspects of electrical safety in the workplace. Moreover, safety training needs to be conducted by qualified person and training impact shall reflect in the electricians attitude. Need to introduce and implement PPE & LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all records of using LOTO. | We have done this | Mar 10 2024 | RPO Comments: 27-May-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 18/08/2024: Not corrected. The LOTO policy is available but not properly followed. No progress has been observed regarding safety training materials. RPO Comments: 23-Oct-2024, the factory management reported the remediation completion. This item will be verified in the next inspection. On 21/01/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: There is no programmed schedule for periodical inspection & testing of electrical equipment. | An electrical maintenance program shall be prepared which will include inspections and testing of the electrical systems (preventive and proactive). | We have done this | Mar 10 2024 | RPO Comments: 27-May-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 18/08/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: Combustible materials are attached with cable duct/channels. | Cable channels/ducts must be kept neat and clean; these must be free from combustible materials. | We have done this | Mar 10 2024 | RPO Comments: 27-May-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 18/08/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Cable duct/channels are filled with fluffs (lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | We have done this | Mar 10 2024 | RPO Comments: 27-May-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 18/08/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Wiring or extensions to connect equipment/ devices are laid on floors unprotected in flexible PVC. | The cable connection to machines/equipment may be run under the checkered plates (existing) and in trenches or rigid conduits/cable trays and supports to protect from external damages. | We have done this | Mar 10 2024 | RPO Comments: 27-May-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 18/08/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Electrical distribution box/panels are full of fluffs (lint/dirt). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. | We have done this | Mar 10 2024 | RPO Comments: 27-May-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 18/08/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 64 | New Finding: Outdoor cables are not covered to protect from weather effect. | Outdoor cable tray/ladders shall be covered properly to avoid seasonal effect on cables and its longevity. | We have done this | Sep 22 2024 | RPO Comments: 22-Dec-2024, the factory management reported the remediation completion. This item will be verified in the next inspection. On 21/01/2025: Corrected. | 1 Month | Corrected

## Boiler
Date
16-Apr-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | INTERLOOP BD LTD, 86,SOYDANA, NATIONAL UNIVERSITY, Gazipur
Date of Inspection |  | 2022-03-07
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 8728 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | We have installed emergency stop push switch on the boiler control panel and outside the boiler room near the entrance door. | Dec 14 2024 | Comments on 24-Oct-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 8728 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have marked the gauge glass | Dec 14 2024 | Comments on 24-Oct-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 8728 | Necessary technical documents (manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We will collect all documents from manufacturur . | Dec 14 2024 | Comments on 24-Oct-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 4 | BB 8728 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | We have done | Dec 14 2024 | Comments on 24-Oct-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 8728 | Steam line connection is not terminated properly. | Any unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | Done | Dec 14 2024 | Comments on 24-Oct-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 8728 | Fuel gas line safety valve(s) /pressure relief valve(s) blowoff is not directed to the outside of the boiler room. | Any fuel gas line safety valve or pressure relief valve blowoff shall be diverted to the outside of the boiler room (open to atmosphere condition) to prevent gas accumulation in the boiler room. | Done | Oct 28 2024 | Comments on 24-Oct-24: Will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 7 | Non BBR-9994-1 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | We have installed emergency stop push switch on the boiler control panel and outside the boiler room near the entrance door. | Dec 14 2024 | Comments on 24-Oct-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 8 | Non BBR-9994-1 | The boiler does not have water level gauge. | The boiler shall have requisite functional mountings and fittings as per Bangladesh Boiler Regulations (BBR) and recognized manufacturing standards. | We are working | Dec 14 2024 | Comments on 24-Oct-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 9 | Non BBR-9994-1 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | We are working | Nov 14 2024 | Comments on 24-Oct-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 10 | Non BBR-9994-1 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We will collect all documents from manufacturur . | Dec 14 2024 | Comments on 24-Oct-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | Functional test inspection | 11 | BB 8728 | There was no Low Low Water (LLWL) level trip with an interlock for the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | Done | Oct 28 2024 | Comments on 24-Oct-24: Will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | Functional test inspection | 12 | BB 8728 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | Done | Nov 14 2024 | Comments on 24-Oct-24: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 13 | Non BBR-9994-1 | There was no Low Low Water (LLWL) level trip with an interlock for the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We are working | Oct 28 2024 | Comments on 24-Oct-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. | 2 WEEKS | In Progress