## Structural
Date
10-May-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | IRIS FABRICS LIMITED, Zirani Bazar, Kashimpur, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-03-24
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Storage Above Allowable Live loads within Building A and Dormitory | (a) Reduce storage loads throughout factory building A and throughout Dormitory to design load levels | Done | Dec 31 2015 | On 9/5/16: Storage loads were reduced and within allowable limit. On 21/08/2017: Corrected from previous follow up inspection report. During inspection, loading was found within limit as per load plan of building A but heavy loading was observed on dormitory building on several floors. On 10-04-2018 : This issue is corrected in previous follow-up inspection .Load was found below maximum allowable limit. On 27-Feb-2020: Load plans were posted. Loading was found below the allowable limit. Issue was found corrected from previous follow up inspection. On 24-Oct-2021: This issue is corrected in previous follow-up inspection. During inspection loading was found below the allowable limit (2 kpa) and load plans were posted on each floor. On 01-Oct-2024: Corrected previously. The load plan was produced as part of DEA which was accepted on 23/11/2015 by ACCORD and re-accepted on 28/4/2021 by RSC. During the inspection, load plan was found posted on the floor also loading was found within the allowable limit of the accepted load plan (2 kPa for typical production area; 3 kPa for dining, prayer, and conference) for Building A. Overloading observed in the 6-storied Dormitory building, see item no-12. On 14-Sep-2025: Previously corrected. | Immediate | Corrected
Initial Inspection |  | 2 | Storage Above Allowable Live loads within Building A and Dormitory | (b) Factory Engineer to develop and actively monitor a loading plan for all floor plates within the factory complex giving consideration to slab, colummn and foundation capacity. | Done | Dec 31 2015 | On 9/5/16: This issue was covered in DEA. DEA was accepted by ACCORD on 23rd November, 2015. On 21/08/2017: Corrected from previous follow up inspection report. Load plan of building A has been prepared as a part of DEA which was accepted on 23rd November, 2015. During inspection, loading was found within limit as per load plan of building A but heavy loading was observed on dormitory building on several floors. On 10-04-2018 : This issue is corrected in previous follow-up inspection .Load was found below maximum allowable limit. On 27-Feb-2020: Load plans were posted. Loading was found below the allowable limit. Issue was found corrected from previous follow up inspection. On 24-Oct-2021: This issue is corrected in previous follow-up inspection. During inspection loading was found below the allowable limit (2 kpa) and load plans were posted on each floor. On 01-Oct-2024: Corrected previously. During the inspection, load plan was found posted on the floor and loading was found within the allowable limit of the accepted load plan (2 kPa for typical production area; 3 kPa for dining, prayer, and conference) for Building A. Overloading observed in the 6-storied Dormitory building, see item no-12. On 14-Sep-2025: Previously corrected. | 06 weeks | Corrected
Initial Inspection |  | 3 | Soil bearing capacity does not appear adequate to support spread footing loads | (a) detailsed engineering assessment to be performed upon Building A foundations | Done | Dec 31 2015 | On 9/5/16: This issue was covered in DEA. DEA was accepted by ACCORD on 23rd November, 2015. On 21/08/2017: Corrected from previous follow up inspection report. DEA was accepted by ACCORD. On 10-04-2018 : This issue is corrected in previous follow-up inspection .DEA has been performed . On 27-Feb-2020: DEA was accepted on 23rd November 2015. Issue was found corrected from previous follow up inspection. On 24-Oct-2021: This issue has been covered under the DEA which has been reviewed and accepted on 23-Nov-2015 by Accord and re-accepted on 28-Apr-2021 by RSC. On 01-Oct-2024: Corrected previously. This issue has been covered in the DEA which was re-accepted by RSC dated 28/4/2021. On 14-Sep-2025: Previously corrected. | 06 weeks | Corrected
Initial Inspection |  | 4 | Soil bearing capacity does not appear adequate to support spread footing loads | (b) Implement all works mandated by the above mentioned detailed engineering assessment | Done | Dec 31 2015 | On 9/5/16: This issue was covered in DEA. DEA was accepted by ACCORD on 23rd November, 2015. On 21/08/2017: Corrected from previous follow up inspection report. DEA was accepted by ACCORD. On 10-04-2018 : This issue is corrected in previous follow-up inspection . On 27-Feb-2020: DEA was accepted on 23rd November 2015. As per accepted DEA, no retrofitting was required. Issue was found corrected from previous follow up inspection. On 24-Oct-2021: This issue has been covered under the DEA which has been reviewed and accepted on 23-Nov-2015 by Accord and re-accepted on 28-Apr-2021 by RSC. The timeline for remediation work was 30-Jul-2021. Remediation work was found completed during inspection and original copies of material test reports were also available. On 01-Oct-2024: Corrected previously. On 14-Sep-2025: Previously corrected. | 06 months | Corrected
Initial Inspection |  | 5 | Storage shed framed with roof trusses appears poorly constructed | (a) Factory engineer to conduct a review of the storage shed roof truss framing to determine its adequacy | Done | Dec 31 2015 | On 9/5/16: This issue was covered in DEA. DEA was accepted by ACCORD on 23rd November, 2015.On 21/08/2017: Corrected from previous follow up inspection report. Factory has demolished the storage shed and ETP was observed on this location. On 10-04-2018 : This issue is corrected in previous follow-up inspection . On 27-Feb-2020: Storage shed was demolished. Issue was found corrected from previous follow up inspection. On 24-Oct-2021: This issue was corrected from previous inspection. Storage shed was found demolished. On 01-Oct-2024: Corrected previously. The factory has demolished Storage Shed. On 14-Sep-2025: Previously corrected. | 06 weeks | Corrected
Initial Inspection |  | 6 | Storage shed framed with roof trusses appears poorly constructed | (b) Perform any remediation required to the shed roof truss framing or demolish the shed. | Done | Dec 31 2015 | On 9/5/16: This issue was covered in DEA. DEA was accepted by ACCORD on 23rd November, 2015. According to DEA no remedial works were required. On 21/08/2017: Corrected from previous follow up inspection report. Factory has demolished the storage shed and ETP was observed on this location. On 10-04-2018 : This issue is corrected in previous follow-up inspection . On 27-Feb-2020: Storage shed was demolished. Issue was found corrected from previous follow up inspection. On 24-Oct-2021: This issue was corrected from previous inspection. Storage shed was found demolished. On 01-Oct-2024: Corrected previously. The factory has demolished Storage Shed. On 14-Sep-2025: Previously corrected. | 6 months | Corrected
Follow Up Inspection |  | 7 | New Findings-1: Discrepancy observed on As built drawing and on site condition of Building-A | Revise As built drawing and design report as per on site condition. | We got Re acceptance of D.E.A on 29.04.2021 and we have completed retrofitting work as per approved DEA. | Feb 10 2017 | On 21/08/2017: During inspection, discrepancy was observed on column layout and As built structural drawing. Factory is required to submit revised DEA and analysis file (including corrected wind load) as per verification report. On 10-04-2018 : Factory has submitted revised As-built drawing and design report as per verification report on 11-02-2018 .With some revisions ,factory is required to submit revised DEA within 08-04-2018 .Till date of inspection ,factory did not submit revised DEA to Accord . On 27-Feb-2020: Factory is required to submit revised documents as per verification report to ACCORD within 15 days after receiving the report. On 24-Oct-2021: : As-built drawings have been prepared as part of DEA which has been reviewed and accepted on 23-Nov-2015 by Accord and re-accepted on 28-Apr-2021 by RSC. During inspection, as-built drawings were found matched with on-site condition. On 01-Oct-2024: Corrected previously. This issue has been covered in the DEA which was re-accepted by RSC dated 28/4/2021. On 14-Sep-2025: Previously corrected. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 8 | New Findings-2: Heavy Loading observed on several floors of dormitory building. | Produce and actively manage a load plan with respect to floor capacity and column capacity | Already reduced excessive load. Now maintain as per load plan. 25.09.2017 | Feb 10 2017 | On 21/08/2017: During inspection, heavy loading was observed 3rd and 4th floor of the dormitory building which exceeds 84 psf. Building engineer is required to produce and submit the load plan to ACCORD with respect to floor capacity and column capacity. On 10-04-2018 :Heavy loading was not found .Factory has produced and posted a Load plan(40psf) of dormitory building. Factory submitted load plan of dormitory building to Accord. On 27-Feb-2020: Load plan was found posted. Floor loading was found below 40 psf. Issue remains corrected. On 24-Oct-2021: This issue is corrected from previous follow up inspection. During inspection loading was found below 2 kpa and load plan was posted. On 01-Oct-2024: Corrected previously. See item no-12. On 14-Sep-2025: Previously corrected. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 9 | New Findings-3: Corrosion observed on steel stair between generator and boiler building | Factory engineer in required to investigate the extent of corrosion and take necessary repairing action accordingly. | Maintenance done.28.10.2017 | Feb 10 2017 | On 21/08/2017: During inspection, corrosion was observed at several places of steel stair. At some places, steel section was found decayed. Factory engineer is required to investigate the extent of corrosion and take necessary repairing action accordingly On 10-04-2018 :Corrosion has been repaired by paint On 27-Feb-2020: Issue was found corrected. On 24-Oct-2021: This issue is corrected from previous follow up inspection. Stair was found coated with rust proof paint. On 01-Oct-2024: Corrected previously. During the inspection, corrosion was not observed. On 14-Sep-2025: Previously corrected. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 10 | New Findings-4: Mismatch observed in core test report. | Factory is required to clarify the issue and incorporate all core test results in DEA. | We got Re acceptance of D.E.A on 29.04.2021 and we have completed retrofitting work as per approved DEA. | Feb 10 2017 | On 21/08/2017: During inspection, Core test report provided by the factory did not match with submitted core test report along with DEA. Besides, no core location was observed during inspection. Factory is required to clarify this issue and incorporate all the values of all core test report into analysis of the building-A. On 10-04-2018 : Factory submitted revised core layout plan to Accord with revised as built drawing and design .During inspection it was observed that every core location was covered with tiles .Randomly a column core location was checked by removing tiles and found ok . On 27-Feb-2020: Core layout was found. Factory is required to submit revised documents as per verification report to ACCORD within 15 days after receiving the report. During inspection, original reports were available onsite. After DEA reacceptance, issue will be verified. On 24-Oct-2021: Core layout has been verified in previous inspection and core layout matched after re-acceptance. Original reports were available onsite and all core test result has been incorporated in DEA report. DEA of this factory has been reviewed and accepted on 23-Nov-2015 by Accord and re-accepted on 28-Apr-2021 by RSC. On 01-Oct-2024: Corrected previously. On 14-Sep-2025: Previously corrected. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 11 | New Findings -5: Hairline cracks were observed in different beams of factory building . | Factory engineer is required to investigate the extent b of cracks ,make investigation and repair with proper suitable method | We have already investigated the extends of cracks by competent engineering firm & report submitted to accord. -Done on 24.04.18. | May 24 2018 | On 10-04-2018: Hairline cracks were observed in different locations of beams and in some area of slab .Factory is required to check extends of cracks ,produce an investigation report ,and repair with proper suitable method. On 27-Feb-2020: Crack investigation report was found onsite. Cracks were non-structural as per investigation report. During inspection, no cracks were found visible. On 24-Oct-2021: This issue is corrected from previous follow up inspection. Crack investigation report was available. Cracks were non-structural as per investigation report and no cracks were observed during inspection. On 01-Oct-2024: Corrected previously. During the inspection, beam crack was not observed. On 14-Sep-2025: Previously corrected. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 12 | New Finding-6: Change of floor occupancy (Storage & Prayer instead of Office & Rest House on 1F, 3F, 4F, 5F) and overloading on 1F & 5F (Dormitory Building) | The factory is required to reduce the loading within 2 kPa. As the occupancy is being changed and the loading was found above 2 kPa, the building engineer is required to perform the Engineering Assessment (EA) and comply with the BNBC loading requirements. | On this regards we made a declaration that this building will use as per submitted drawing and ocupency load should be keep in limit (42psf) 2 kPa. | Nov 28 2024 | RPO Comments: On 07/04/2026 - The design documents (EA) are currently under RSC’s review. On 01-Oct-2024: As per the inspection on 21-Aug-2017 (item-8) the building engineer was required to produce and submit the load plan to ACCORD with respect to floor capacity and column capacity. Later the inspection on 10-Apr-2018, the factory has produced & posted a load plan considering 40psf of and submitted to Accord which was found satisfactory. During the inspection, overloading was observed on the 1st and 5th floors, along with changes in occupancy on the 1st, 3rd, 4th, and 5th floors. The 1st floor has been using as a prayer area instead of office space, while the 3rd to 5th floors are now using for storage instead of office space. The factory is required to reduce the loading within 2 kPa. As the occupancy is being changed and the loading was found above 2 kPa, the building is required to perform the Engineering Assessment (EA) and comply with the BNBC loading requirements. Submit the EA report to the RSC. On 14-Sep-2025: The factory submitted a declaration to revert to the previously allowable load plan. However, storage was observed on the 4th and 5th floors instead of office/resthouse use, with loading below 40 psf. The Building Engineer is required to produce EA reflecting the occupancy change and submit it to RSC. Progress Status: 0% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 13 | New Finding-7: New structure found in the factory premises. Two-storied (G+1) RC New Utility Building (227 sqm / 2442 sft per floor) Observation:- Lack of load plan and design report. Single-storied (G+M) RC New Boiler Building (total 246 sqm / 2646 sft) Observation:- Lack of architectural drawing. | The building engineer is required to prepare as-built drawings and load plan as part of EA for the New Utility Building in compliance withBNBC. The factory is required to carryout the remedial works if required. Also, the building engineer is required to prepare as-built drawings for the New Boiler Building (G+M) and keep it on-site which will be verified in the further inspection. | We submitted E.A report and related others documents to R.S.C on 17.02.2026. | Nov 28 2024 | RPO Comments: On 07/04/2026 - The design documents (EA) are currently under RSC’s review. On 01-Oct-2024: During the inspection, RC two-storied (G+1) New Utility Building and Single-storied (G+M) New Boiler Building found in the factory premises. The construction drawing of the buildings were found satisfactory as per the site condition. The building engineer is required to prepare as-built drawings and load plan as part of EA for the New Utility Building in compliance with BNBC and submit to RSC within 28-Nov-2024. The factory is required to carryout the remedial works if required. Also, the building engineer is required to prepare as-built drawings for the New Boiler Building (G+M) and keep it on-site which will be verified in the further inspection. On 14-Sep-2025: The factory is required to submit the revised documents as per review comments by 30 September 2025. Progress Status: 30% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 14 | New Finding-8: Mismatches in as-built drawing 1. Security Building (single storied, 733 sft) 2. Fire Control Room (single storied, 204 sft) 3. RMS Room (single storied, 298 sft) 4. Security Post (single storied, 185 sft) Lack of as-built drawing 5. Maintenance Shed (single storied, 697 sft) | The building engineer is required to update/produce as-built drawing as per site condition and submit the updated drawings to RSC | We submitted all structures as built drawings to R.S.C on 17.02.2026. | Nov 11 2025 | RPO Comments: On 07/04/2026 - The design documents (EA) are currently under RSC’s review. On 14-Sep-2025: During inspection, five new structures were found. As-built drawings were available for all structures except the Maintenance Shed. Mismatches in grid dimensions, beam depth etc. were observed between as built drawings and onsite condition. The building engineer is required to prepare as-built drawings for the Maintenance Shed, update as-built drawings for other structures as per onsite conditions and submit the updated drawings to RSC. | (within 6 weeks) | In Progress

## Fire
Date
10-May-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | IRIS FABRICS LIMITED, Zirani Bazar, Kashimpur, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-04-03
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The Exit Stairs are not separated from work areas, and other spaces on each floor by fire rated construction. This was reflected throughout the building on all floors. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tide to the fire alarm system. | Done | Apr 30 2016 | On 21/Aug/2017: Corrected. On 30-11-2017: Corrected as per previous follow-up. On 28/03/2018: Corrected. Note: New printing building didn't cover on FUI. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Referred to the issue no-30. | 03 months | Corrected
Initial Inspection |  | 2 | Areas used for combustible storage are not separated by fire construction. This was reflected throughout the building on the first third, fourth, sixth and seventh floors. | Provide dedicated storage rooms separated by minimum 1-hr fire rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows : (i) Maximum height of 2.4 m and maximum area 23m2 (ii) If sprinkler protected : Maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Done | Jan 31 2016 | On 11/Dec/2016 : Corrected. On 21/Aug/2017: On 28/03/2018: Issue has been cover on point no 18. On 11/07/2018: Issue has been cover on point no 18. On 24/11/2018: Corrected On 28/03/2022: Corrected as per previous FUI. On 01-Oct-24: Corrected | 03 months | Corrected
Initial Inspection |  | 3 | The boiler, generator, and transformer room located in a separate building 03, is not separated by fire rated construction, openings, non-rated doors, and penetrations. | Separate the boiler, generator, and transformer room by a minimum 2- hr fire rated construction. Seal and / or protected all openings to maintain the required fire separations. | Done | Dec 31 2015 | On 11/Dec/2016 : Corrected. On 21/Aug/2017: Corrected. On 30-11-2017: Corrected as per previous follow-up. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected as per previous FUI. On 01-Oct-24: Corrected | 03 months | Corrected
Initial Inspection |  | 4 | Storage rooms used for combustible storage are not separated by fire rated construction. This was reflected throughout the building on the first, third, fourth, sixth, and seventh floors | Provide dedicated storage rooms, separated by minimum 01-hr fire-rated constructions. | Done | Dec 31 2015 | On 09-May-16: Corrected On 11/Dec/2016 : Corrected. On 21/Aug/2017: On 28/03/2018: Issue has been cover on point no 18. On 11/07/2018: Issue has been cover on point no 18. On 24/11/2018: Corrected. On 28/03/2022: Referred to the issue no-19. | 03 months | Corrected
Initial Inspection |  | 5 | Egress doors / gates with locking features are provided at building exits, exit stairs, along egress routes and exit discharges. This was reflected throughout the building on all floors. | Remove locking features from all egress doors/ gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Done | Aug 16 2014 | On 11/Dec/2016 : Corrected. On 21/Aug/2017: Corrected. On 30-11-2017: Corrected. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | Immediate | Corrected
Initial Inspection |  | 6 | Storage areas were Located in all exit stairwells on the ground floor, underneath the stairs. | Remove all storage from exit stairs and egress paths. | Done | Aug 16 2014 | On 11/Dec/2016 : Corrected. On 21/Aug/2017: Corrected. On 30-11-2017: Corrected. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | Immediate | Corrected
Initial Inspection |  | 7 | There was storage located in egress paths throughout the first through seventh floors. | Keep egress paths and stairs clear of storage. | Done | Jan 31 2016 | On 11/Dec/2016 : Corrected. On 21/Aug/2017: On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | Immediate | Corrected
Initial Inspection |  | 8 | The fire command room is located underneath the west exit stairwell on ground floor. | Remove all storage / rooms from exit stairs on egress paths | Done | Aug 16 2014 | On 11/Dec/2016 : Corrected. On 21/Aug/2017: Corrected. On 30-11-2017: Corrected. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | Immediate | Corrected
Initial Inspection |  | 9 | Collapsible gates/ sliding doors are provided at building exits, exit stairs, along egress routes, and exit discharge. This was reflected throughout the building on all floors. | Replace all gates. Sliding doors along the means of egress with side-hinged swinging egress doors. If locks are required for security reasons, utilize special door locking features complying NFPA 101. | Done | Aug 16 2014 | On 11/Dec/2016 : Corrected. On 21/Aug/2017: Corrected. On 30-11-2017: Corrected. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | 01 months | Corrected
Initial Inspection |  | 10 | The high-rise building has an occupied floor greater than 23m (75ft) and is not provided with automatic sprinkler protection. The large occupant loads, heavy fuel loading, and anticipated extended egress times warrant sprinkler protection. | Provide automatic sprinkler protection throughout the building in accordance with NFPA 13. | Done | Jan 31 2016 | On 09-May-16: Corrected On 11/Dec/2016 : Corrected. On 21/Aug/2017: On 28/03/2018: Issue has been covered on point no 23. On 11/07/2018: Issue has been covered on point no 23. On 24/11/2018: Corrected as per previous FUI. On 28/03/2022: Corrected as per previous FUI. On 01-Oct-24: Corrected as per previous FUI considering the current reservoir condition. Note: Hydraulic calculation is required to be done according to the system as-built condition. If any modification is required on the sprinkler system in future for any reason, the modification shall be done maintaining the mentioned standard. | design within 06 months, install within 12 months. | Corrected
Initial Inspection |  | 11 | Inspection, testing, and maintenance records for the fire alarm system was not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on site, in accordance with NFPA 72. | Done | Dec 31 2015 | On 09-May-16: Corrected On 11/Dec/2016 : Corrected. On 21/Aug/2017: Corrected. On 30-11-2017: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | 03 months | Corrected
Initial Inspection |  | 12 | Manual on-off switch is provided for emergency lighting units. This was reflected throughout the building in various locations. | Remove manual on/off switches from emergency lighting units to prevent them from being switched off | Done | Aug 16 2014 | On 21/Aug/2017: Corrected. On 30-11-2017: Corrected. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | 01 month | Corrected
Initial Inspection |  | 13 | Exit signage not illuminated (burned out, broken, etc). This was reflected throughout the building on various floors. | Regularly inspected all exit signage and replace/ install lights as needed to illuminate signs. | Done | Aug 16 2014 | On 09-May-16: Corrected On 11/Dec/2016 : Corrected. On 21/Aug/2017: On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | 01 months | Corrected
Initial Inspection |  | 14 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. This was reflected throughout the building on all floors. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Done | Feb 15 2016 | On 11/Dec/2016 : Corrected. On 21/Aug/2017: Corrected. On 30-11-2017: Corrected. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | within 03 months | Corrected
Initial Inspection |  | 15 | Inspection, testing, and maintenance records for the emergency lighting system were not available | Inspect, test and maintain the emergency lighting system in accordance with the ACCORD standard. Keep written records on-site. | Done | Oct 2 2016 | On 11/Dec/2016 : Corrected. On 21/Aug/2017: Corrected. On 30-11-2017: Corrected. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | within 03 months | Corrected
Follow Up Inspection |  | 16 | NEW FINDING (3rd Follow up): Distance between sprinkler and slab was more than 30 cm | Re adjust the distance (Minimum 2.5 cm and maximum 30 cm) | Done | Jun 9 2016 | On 21/Aug/2017: Corrected On 30-11-2017: Corrected. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | 1 month | Corrected
Follow Up Inspection |  | 17 | NEW FINDING (3rd Follow up): Exit stair is not separated from office floor at 8th Floor. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tide to the fire alarm system. | Corrected on 10.12.2018, All exit stairs are separated from office area. | Jun 9 2016 | On 21/Aug/2017: Corrected. On 30-11-2017: Corrected. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Exit stair - 03 enclosure is not separated from the interior of production floor on all floor levels. On 28/03/2022: Corrected. Sealed by brick wall. On 01-Oct-24: Corrected | 1 month | Corrected
Follow Up Inspection |  | 18 | New Finding (5th FU): Heavy fire load has been observed at the production floors due to the presence of large area of unenclosed combustible storages. | Provide defined storage areas and limit the storage arrangement as follows:- If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. or Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Done | Oct 21 2017 | On 21/Aug/2017: New Finding. On 30-11-2017: Not defined yet. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | Within 02 months | Corrected
Follow Up Inspection |  | 19 | New Finding (5th FU): Finished Godawn used for storage of combustible materials are not separated from the surrounding occupancy/areas. | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour construction. | We shifted all storage of combustable materials from the room as well as we using the room as per RSC instruction accordingly. -Done | Oct 21 2017 | RPO Comments: On 07/04/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 21/Aug/2017: New Finding. On 30-11-2017: No progress observed. On 28/03/2018: No action has been taken yet. On 11/07/2018: Not corrected. On 24/11/2018: Corrected On 28/03/2022: Issue reopened. During inspection unprotected storage was observed at 7th floor of factory building & 3rd floor of dormitory building. On 01-Oct-24: No storage was found on the 7th floor of the factory building. Fire rated door interfacing was functional at almost all the locations except 5th floor of the dormitory building. Door coordinator also did not work on the 5th floor in northwest stair. | Within 02 months | Pending Verification
Follow Up Inspection |  | 20 | New Finding (5th FU): The exits are not remotely located from each other such that a single fire event could compromise both exits. Location: 8th Floor, Office area. | Specify appropriate upgrade based on conditions: -Modify exit arrangement. -Provide additional exit(s) | Done | Oct 21 2017 | On 21/Aug/2017: New Finding. On 30-11-2017: Corrected. Additional exit has been provided. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | Within 02 months | Corrected
Follow Up Inspection |  | 21 | New Finding (5th FU): As-built drawings, Documentations, Certification of products used in the system and Installation of Fire Alarm is not as per NFPA-72. | Provide proper as-built drawings, Documentations, Certification of products used in the system and Install Fire Alarm is as per NFPA-72. | We submitted the FADS documents and drawings for Pre-T&C on 29 March 2026 and currently waiting for RSC’s response. -Waiting for Review | Oct 21 2017 | RPO Comments: On 07/04/2026 - The FADS Pre-T&C docs are under review by the RSC with RSC ID 24209 combinedly. On 21/Aug/2017: New Finding. On 30-11-2017: Subject to reverification of the T&Cx of the CFDS. On 28/03/2018: Pending for T&C. Still listed cable did not installed. On 11/07/2018: T&C is pending. Factory has installed sprinkler system. On 24/11/2018: Details T&C is required to verify this issue. Factory management is required to apply for T&C. On 28/03/2022: FADS work in progress (reportedly). SLC and NAC were open during the inspection. Detector was covered by external source in some areas. On 19/12/2023: PreT&C of fire alarm & detection system found that system is not ready for full functional T&CVI. See details in the preT&C report. On 01-Oct-24: Remediation according to the last Pre-T&C report is in progress. The fire alarm control panel has been found in abnormal condition. It was reported that the fire alarm control panel will be relocated to a newer location. | Within 02 months | In Progress
Follow Up Inspection |  | 22 | New Finding (5th FU): Interfacing of Fire doors and Exhaust fans with FACP are not done properly. | Interfacing of different components with FACP shall be done as per ACCORD recommendation. | Interfacing of different components with the FACP has been carried out in accordance with ACCORD recommendations. -Done | Oct 21 2017 | RPO Comments: On 07/04/2026 - The FADS Pre-T&C docs are under review by the RSC with RSC ID 24209 combinedly. On 21/Aug/2017: New Finding. On 30-11-2017: Subject to reverification of the T&Cx of the CFDS. On 28/03/2018: Subject to reverification of the T&Cx of the CFDS. On 11/07/2018: T&C is pending. On 24/11/2018: Corrected. Interfacing of Fire doors & Exhaust fan with FACP has been completed and was verified during FUI. On 28/03/2022: Issue reopened. During FUI interfacing was not working properly. Also, It is an integrated part of the fire alarm system. On 19/12/2023: It is integrated part of FADS. PreT&C of fire alarm & detection system found that system is not ready for full functional T&CVI. See details in the preT&C report. On 01-Oct-24: Remediation according to the last Pre-T&C report is in progress. The fire alarm control panel has been found in abnormal condition. It was reported that the fire alarm control panel will be relocated to a newer location. | Within 02 months | In Progress
Follow Up Inspection |  | 23 | New Finding (5th FU): Proper third party certification for fire pump were not present. | Provide proper third party certification for fire pump | Done | Oct 21 2017 | ON 07/06/2018 Factory asked for extended timeline till: 30.10.2018 Timeline extension request is not accepted. On 21/Aug/2017: New Finding. On 30-11-2017: Subject to reverification of the T&Cx of the fire protection system. The system does not comply with NFPA 20 requirements. On 28/03/2018: Still listed diesel pump is not installed. After installation required T&C. On 11/07/2018: L/C has not been opened for fire pump. On 24/11/2018: Corrected. 3rd party Listed Diesel Pump is installed & diesel pump, existing electrical pump was in functional status during FUI. On 28/03/2022: Corrected as per previous FUI. On 01-Oct-24: Corrected | Within 02 months | Corrected
Follow Up Inspection |  | 24 | New Finding (5th FU): Common path of egress travel exceeds 30 m. Location: 3rd Floor. | Reconfigure the egress arrangement to reduce the maximum common path of travel to not more than 30 m. | Done | Oct 21 2017 | On 21/Aug/2017: New Finding. On 30-11-2017: Corrected. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | Within 02 months | Corrected
Follow Up Inspection |  | 25 | New Finding (5th FU): During the inspection egress aisles were obstructed by combustible storages and available clear width were found less than 36 inch. | Provide aisles free from obstructions and with minimum clear widths of 36-inch. | Done | Oct 21 2017 | On 21/Aug/2017: New Finding. On 30-11-2017: No progress observed. On 28/03/2018: Corrected. On 11/07/2018: Reponed. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | Within 02 months | Corrected
Follow Up Inspection |  | 26 | New Finding (5th FU): The egress path along means of egress has interrupted by obstruction/storage. | Means of egress shall be maintained continuously free and clear of all obstructions/storage. Or Keep egress paths and stairs clear of storage. | Done | Oct 21 2017 | On 21/Aug/2017: New Finding. On 30-11-2017: Not corrected yet. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | Within 02 months | Corrected
Follow Up Inspection |  | 27 | New Finding (5th FU): Penetrations through floor/ceiling assemblies are found unsealed in electrical shafts. | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. | Done | Oct 21 2017 | On 21/Aug/2017: New Finding. On 30-11-2017: Corrected. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | Within 02 months | Corrected
Follow Up Inspection |  | 28 | New Finding (5th FU): Directional exit signage not illuminated during testing (burned out, broken, etc.). Note: Wires were found cut off. | Regularly inspect all exit signage as per Accord standard and replace/install lights as needed to illuminate signs | Done | Oct 21 2017 | On 21/Aug/2017: New Finding. On 30-11-2017: Corrected. On 28/03/2018: Corrected. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | Within 02 months | Corrected
Follow Up Inspection |  | 29 | New Finding (5th FU): The factory is using/storing liquefied gas cylinders without proper separations. | Remove them from the factory building. or Provide 2-hr rated room for using/storing liquefied gas cylinders and ensure proper ventilation of that room. Source of fire such as electrical connection is prohibited. | Done | Oct 21 2017 | On 21/Aug/2017: New Finding. On 30-11-2017: Corrected. Not observed during inspection. On 28/03/2018: Corrected. Not founded. On 11/07/2018: Corrected. On 24/11/2018: Corrected On 28/03/2022: Corrected. On 01-Oct-24: Corrected | Within 02 months | Corrected
Follow Up Inspection |  | 30 | New Finding (10th FUI): Fire doors has been installed in the openings of required fire rated assemblies (Exit stairs and other occupancy separations), However, fire door were found with following issues- 1. Doors were kept open by means of door wedges. 2. Doors were not provided with adequate/required hardware. 3. Doors were found with excessive clearance. 4. Doors were not provided with required positive latching. 5. Fire doors and frames were found with holes/scratches that could impact the fire protection rating. | Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. The clearance under the bottom of a fire door shall be a maximum of 19mm. From edges and top shall be limited to a maximum 4.8 mm. All measurement shall be taken from the "pull side" of the door. Any modification of fire doors beyond the job site preparation shall be approved by the door manufacturer. | We ensured the fire doors are self-closing and positive latching, which are provided with fire exit (panic) hardware are serving at production floors.To keep the door held open for functional reasons, we provided the automatic closing devices tied to the fire alarm system. -Done | Jun 27 2022 | RPO Comments: On 07/04/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 28/03/2022: New Finding. On 01-Oct-24: Gap under the fire door is observed more than 19 mm at the northwest stair on the 7th floor of the factory building. Door latching device is missing at northwest stair on 6th floor at the factory building. Door is found open by unapproved means on the ground floor east exit of the main building. | Within 3 months | Pending Verification
Follow Up Inspection |  | 31 | New Finding (10th FUI): Electrical cable riser has Passed through the exit enclosure. Location: Ground floor of factory building stair-02 & Dormitory building stair-01. | Penetration is prohibited into and through an exit enclosure.Re-route the cable raceway to comply Accord 6.14.4.Seal all penetrations and openings in exit stair enclosure walls to maintain the required fire separation. | We sealed the Electrical cable riser which Passed through the exit enclosure. Location: Ground floor of factory building stair-02 & Dormitory building stair-01. by civil construction which is adequate to ensure 2 hours rating.-Done | Jun 27 2022 | RPO Comments: On 07/04/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 28/03/2022: New Finding. On 01-Oct-24: Factory building- the factory has tried to separated the cable trench by brick construction on ground floor, but it was not adequate to assure 2-hrs rated. Dormitory building-Rated separation is provided. | Within 3 months | Pending Verification
Follow Up Inspection |  | 32 | New Finding (11th FUI): Occupiable roof is not provided with an adequate parapet / guard rail. Location: Main factory building roof. | All occupiable roofs shall be provided with parapets or guards with a minimum height of 1067 mm (42 in.) | we provided with parapets or guards with a minimum height of 1067 mm (42 in.) at all occupiable roofs. -Done | Dec 1 2024 | RPO Comments: On 07/04/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 01-Oct-24: New Finding. | Within 2 months | Pending Verification
Follow Up Inspection |  | 33 | New Finding (11th FUI): Storage were observed underneath the cutting tables. Location: Main factory building (6th floor) | Storage underneath the cutting tables shall be kept clear of combustibles at all time, except as provided for miscellaneous storage in accordance with the RSC Technical Guidelines (Standard) section 3.4.2.1.6 or where automatic sprinkler protection is installed. Where an automatic sprinkler system is installed sprinklers are required to be installed beneath cutting tables greater than 4 ft. in width that are used for storage of combustibles. | we removed all storage underneath the cutting table by following the RSC standard. -Done | Dec 1 2024 | RPO Comments: On 07/04/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 01-Oct-24: New Finding. | Within 2 months | Pending Verification
Follow Up Inspection |  | 34 | New Finding (11th FUI): Aisle are not properly marked. Location: 3rd and 4th floor of main factory building. | Aisles shall be properly marked and provided with a minimum unobstructed clear- width of 0.9m (36 in). | we marked the Aisles properly and kept clear minimum 0.9m -Done | Nov 1 2024 | RPO Comments: On 07/04/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 01-Oct-24: New Finding. | Within 1 month | Pending Verification
Follow Up Inspection |  | 35 | New Finding (11th FUI): Chemical storage room is not properly separated by fire-rated construction from surrounding occupancy. Location: Dyeing shed. | Separate the chemical storage room by 4-hr fire rated construction. Seal all penetrations and protect the openings to maintain the required fire separations for 4-hrs. Opening is not permitted for 4-hrs fire rated separation. Keep 16-points SDS of all chemicals in the storage area. Note: Construction type shall be Type-1 and separation shall be as per Table 3.2.1 of BNBC-2006. | We shifted the chemical storage to another place which is constructed by followong the BNBC guideline and RSC Instructions. -Done | Jan 1 2025 | RPO Comments: On 07/04/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 01-Oct-24: New Finding. | Within 3 months | Pending Verification
Follow Up Inspection |  | 36 | New Finding (11th FUI): Travel distance to reach an exit exceed the standard limit according to the RSC Technical Guidelines (Standard), during inspection it was more than 200 ft. Location: Dyeing shed | Travel distance limitations for G2 (RMG factories) shall be increased to 60 m (200ft) where a complete automatic fire detection system, portable fire extinguishers, and standpipe system are provided in accordance with RSC Technical Guidelines (Standard).Travel distance limitations for G2 (RMG factories) shall be increased to 122 m (400 ft.) where a complete automatic sprinkler system, automatic fire alarm system and portablefire extinguishers are provided in accordance with RSC Technical Guidelines (Standard). | We provided an extra exit at old dyeing shed by maintaining RSC technical Guideline. -Done | Jan 1 2025 | RPO Comments: On 07/04/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 01-Oct-24: New Finding. | Within 3 months | Pending Verification
Follow Up Inspection |  | 37 | New Finding (11th FUI): The dining shed on the 8th floor of high rise (9 storied) building is constructed with pre-fabricated column, purlin and rafter. Location: Main factory building. | Existing high-rise RMG factory buildings (height exceeding 20m) will be of Type -1 construction as per BNBC 2006 Part 3 Table 3.2.4. So, provide require rating for the structural elements of the building following BNBC 2006-Table 3.2.4, 3.1.9 and 3.3.1. Factory shall ensure that, all the design, datasheet, certificate, and the design-philosophy has been reviewed from the RSC prior to install the passive fire protection system. | We submitted documents and drawings on 06 April 2026 and currently waiting for RSC’s response. -Waiting for Review | Jan 1 2025 | RPO Comments: On 07/04/2026 - The factory management submitted the required design docs and under review by the RSC now. On 01-Oct-24: New Finding. | Within 3 months | In Progress
Follow Up Inspection |  | 38 | New Finding (11th FUI): The exit discharge is not separated from the oil storage on the ground floor at east side of the main factory building. | Provide minimum 2 hr. fire rated exit discharge path which will lead directly outside. | we remove all oil storage from exit discharge and now exit discharge is free from oil storage hazard.we ensured 2 hr. fire rated exit discharge path which lead directly outside. -Done | Nov 1 2024 | RPO Comments: On 07/04/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 01-Oct-24: New Finding. | Within 1 month | Pending Verification

## Electrical
Date
10-May-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | IRIS FABRICS LIMITED, Zirani Bazar, Kashimpur, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-04-03
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Phase Barrier/ Separators between different phases with voltage exceeding 400V are not installed. | Phase barriers between different phases must be installed to avoid are flashing. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 1 Month | Corrected
Initial Inspection |  | 2 | Wires and Cables Inside distribution panel not arranged and firmly fixed. | Cables and wiring inside panels must be arranged and firmly fixed away to avoid unintendedly touching other parts. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 3 Months | Corrected
Initial Inspection |  | 3 | Rubber Mat in front of high voltage panels not provided. | Rubber mat of electrically graded must be provided in front of high voltage panels. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 1 Month | Corrected
Initial Inspection |  | 4 | Cables supported on cable trays/ raceways are not firmly fixed. | cables supported on cable trays must be firmly fixed. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 3 Months | Corrected
Initial Inspection |  | 5 | Power cables entering to panel not protected. | Cables must be protected with tray and covered. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 6 Months | Corrected
Initial Inspection |  | 6 | Base plates of panels not installed. | Base Plate must be installed at the panel. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 3 Months | Corrected
Initial Inspection |  | 7 | Cable glands not used in panels. | Cable glands must be used for termination inside panel. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 1 Month | Corrected
Initial Inspection |  | 8 | Unused cable entry holes are not closed/ sealed. | Unused cable entry holes must be sealed. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 1 Month | Corrected
Initial Inspection |  | 9 | Opening for cables leaving the electrical shafts to deliver power supply at various floors are not sealed with fie rated sealant. | The electrical shafts must be sealed with fire rated materials. | Done | Nov 1 2015 | On 09/05/2016: Corrected on second follow up. Also found same in current. | 3 Months | Corrected
Initial Inspection |  | 10 | Cables joints at the point of cable gland below the panel. | Cable joints must not do at the point. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 1 Month | Corrected
Initial Inspection |  | 11 | Wires joints not insulated / protected properly. | Wires joints must be insulated or protected properly to avoid sparking. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 1 Month | Corrected
Initial Inspection |  | 12 | Wires entering in wiring duct not protected. | Wiring entering in duct must be protected. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 1 Month | Corrected
Initial Inspection |  | 13 | Wires entering to panel not covered at full length. | Wires must be covered at its full length. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 1 Month | Corrected
Initial Inspection |  | 14 | Power points and light point installed on a wooden rack. | Electrical fittings must not installed on combustible materials. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 1 Month | Corrected
Initial Inspection |  | 15 | PVC conduit circular box not covered. | PVC conduit circular must covered. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 1 Month | Corrected
Initial Inspection |  | 16 | Cables are passes through ventilators. | Cables must passes through the trays or ducts. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 1 Month | Corrected
Initial Inspection |  | 17 | Cables are not dressed properly. | Cables must dressed properly to avoid stress. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 1 Month | Corrected
Initial Inspection |  | 18 | Cables in flexible conduit are passing through concrete wall. | Cables must pass through a tray or ducts. | Done | Nov 1 2015 | On 09/05/2016: Corrected on second follow up. Also found same in current. | 3 Months | Corrected
Initial Inspection |  | 19 | Cables are run on ducts without covering. | Cables are run on ducts without covering the dust deposits. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 3 Months | Corrected
Initial Inspection |  | 20 | Holes on ceiling not sealed. | Holes must be sealed with rated materials. | Done | Sep 19 2014 | On 09/05/2016: Corrected on first follow up. Also found same in current. | 1 Month | Corrected
Follow Up Inspection |  | 21 | New Finding: Early Streamer Emission (ESE) type Lightning Protection system has no design, certificate and test report. | Submit Design, field test report, third party (UL, FM, Intertek, TUV, USTC, ARL etc.) to Accord for acknowledgement. | Done | Nov 1 2015 | On 09/05/2016: Corrected on second follow up. Also found same in current. | 3 Months | Corrected
Follow Up Inspection |  | 22 | New Finding: Electrical Single Line Diagram (SLD) has inadequate information which has no effectiveness. | Prepare SLD more informative thus anyone can understand it. | Done | Feb 28 2016 | On 11/01/2016: Prepare SLD properly & get it reviewed by Accord. New committed timeline is given till 28th February, 16 On 09/05/2016: Still not corrected. On 11/12/2016: Not corrected. On 21/08/2017: Not corrected. Still many places are not updated according to the as-built condition. On 30/11/2017: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 23 | New Finding: Insulation resistance test of electrical cables is not performed. | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off). | Done | Nov 1 2015 | On 09/05/2016: Corrected on second follow up. Also found same in current. | 2 Months | Corrected
Follow Up Inspection |  | 24 | New Finding: Earth pit resistance record is unavailable. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the inspector when required | Done | Oct 30 2015 | On 11/01/2016: Take necessary steps to reduce earth resistance of respective earth pits. On 09/05/2016: Corrected in second follow up. Also found same in current. | 2 Months | Corrected
Follow Up Inspection |  | 25 | New Finding: Thermo graphic scanning of the entire electrical system has not been tested and recorded. | Thermo graphic scanning for the entire electrical system must be performed on a bi annual basis and recorded. | Done | Jul 10 2015 | On 09/05/2016: Corrected on second follow up. Also found same in current. | 2 Months | Corrected
Follow Up Inspection |  | 26 | New Finding: Earth lead cable/ earth continuity conductor size is inadequate/ undersize. | Resize earth lead cable / ECC for LT panel / MDB/ DB; follow BNBC 2006 Part 8 chapter 2, section 2.8 for sizing your earthing cables (usually ECC should be equal to the half of the respective phase cable). | Done | Oct 30 2015 | On 09/05/2016: Corrected on second follow up. Also found same in current. | 3 Months | Corrected
Follow Up Inspection |  | 27 | New Finding: Transformer Breather oil cup is empty. | Fill the transformer breather oil cup by transformer oil. | Done | Jul 10 2015 | On 09/05/2016: Corrected on second follow up. Also found same in current. | 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding: Oversized circuit breakers or circuit breakers are not adjusted accordingly. | Adjust or replace all the MCCBs/ MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. Check this issue all through the factory. | Done | Feb 28 2016 | On 11/01/2016: This issue is still open. New committed timeline is given till 28th February, 16 On 09/05/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 29 | New Finding: Oil leakage has been observed from transformer. | Stop oil leakage from transformer and keep clean top of transformer. | Done | Jan 31 2016 | On 09/05/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 30 | New Finding: Transformer has been installed congested. | Ensure minimum 1.07 m (42 inch) working clearance around every electrical installation. | Done | Jun 5 2016 | On 1/12/2016 Factory asked for extended timeline till: December 31,2016.Timeline extension request is not accepted. On 09/05/2016: Still not corrected. Factory informed verbally they would relocate substation. On 11/12/2016: Not Corrected. On 21/08/2017: Corrected. | 4 Months | Corrected
Follow Up Inspection |  | 31 | New Finding: Multiple cables terminated at MCB terminals. | Terminate each power cable at single terminal and use proper sized cable lug (where applicable). | Done | Feb 15 2016 | On 09/05/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 32 | New Finding: Power cable is covered by sand in the cable trench (or cable trench is filled with sand). | If it is designed keeping Power cable under sand, its OK; otherwise remove sand from cable trench avoiding physical damage of cables. | Done | Mar 30 2016 | On 09/05/2016: Corrected. As cables derated value matches with the load demand, its fine. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: Cable duct/ channels /trench are filled with fluffs (Lint/dust). | Clean all the cable channels/ ducts; then cover them. After each maintenance, keep record. | Done | May 30 2016 | On 09/05/2016: Still not corrected. New timeline is given till 30/05/2016. On 11/12/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 34 | New Finding: Battery terminals are left open. Also, batteries are kept on concrete floor. | Use insulated rubber cap to cover all the battery terminals. Generator battery should be kept in metallic (steel) frame. | Done | May 30 2016 | On 11/12/2016: Corrected. | 2 weeks | Corrected
Follow Up Inspection |  | 35 | New Finding: Earth pits are not identifiable. | Identify each earth pit and mark it for periodic maintenance purpose. | Done | Jun 15 2016 | On 11/12/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 36 | New Finding: Power cables inside cable trench are buried by sand/ soil. | Power cables should not be buried in any case. If it is not designed through sand/soil, removal of sand/soil must be done. | Done | Jan 20 2017 | On 21/08/2017: Not Corrected. No steps taken. 1.The cables routed from LT panel to production building are buried into sand/soil. 2.Cables below LT panels, COS/ATS in substation room (main supply room in generator house) are buried in sand/soil. On 30/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Power Cables are hanging without support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. | Done | Jan 20 2017 | On 30/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per load current; if adjustment is not possible, replacement will be the only way. | Done | Sep 25 2017 | On 30/11/2017: Not corrected. Breakers are not adjusted in the generator room. On 28/03/2018: Not corrected. On 11/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 39 | New Finding: Cross-run-conductors are not installed properly at some places on roof of main building. Mesh width is found fore than 50 feet at few places. The design is not as-built. | Need to modify the drawing and modify the installation according to standard. Need to prepare an as-built drawing after installation. | Done | Sep 25 2017 | On 30/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: Base plates of panels not installed (Most of the panels in LT panel room, MDB in production building). | Panel base plates must be installed, at all time, and cables entering panel must be firmly fixed with cable gland. | Done | Sep 25 2017 | On 30/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Generator terminal box is open (not sealed). | Need to seal the generator terminal box and cables entering panel must be firmly fixed with cable gland. | Done | Sep 25 2017 | On 30/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Multiple cables (came from different electrical consumers) terminated at CB terminals. Multiple cables were found in specially some small mcb box in dyeing sheds. | Each electrical circuit must be terminated at single MCB/ MCCB terminals. | Done | Sep 25 2017 | On 30/11/2017: Not corrected. Multiple connection from single point has not been eliminated. On 28/03/2018: Not corrected. On 11/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Circuit is drawn from bus bar without any protective means. No protection (few panels in dyeing sheds) is given. | Each electrical circuit must be drawn from distribution board busbar using a proper type protection arrangement (MCCB/ MCB). | Done | Sep 25 2017 | On 30/11/2017: Not corrected. Protection has not been provided in the dyeing section. On 28/03/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Panel/ Distribution boxes are inaccessible for panel Height (specially some panels in dyeing sheds). | Each electrical distribution board/panel must be easily accessible. In case of height its top shall not be higher than 2m from base; and door opening shall be at least 90 degree. | Done | Sep 25 2017 | On 30/11/2017: Not corrected. Panel is inaccessible due to storage of fabrics around. On 28/03/2018: Not corrected. On 11/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. | Done | Sep 25 2017 | On 30/11/2017: Not corrected. Cable bending has not been removed. On 28/03/2018: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Phase barrier/separators are missing in MCCBs. | Phases must be separated by insulator (a rubber type no-flammable materials shall be used for it). | Done | Sep 25 2017 | On 30/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Air terminal are missing at several points of Lightning Protection System. | Factory has to design Lightning Protection System (LPS) for the whole factory (where the Risk index is more than 40). Once a LPS is designed properly, installation must be done accordingly asap. | Corrected. Already Installed air terminal in missing area. | Apr 30 2018 | On 11/07/2018: Not corrected. LPS for the Utility building need to be installed properly. On 25/11/2018: Not Corrected. On 4-Mar-21: Not Corrected. Still some work is pending. On 12-04-2021: Factory is asking for timeline extension till 30-05-2021, which is not accepted. On 19/12/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Electrical power cables are not identified properly. | Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables used in the system according to SLD. | Done | Apr 30 2018 | On 11/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Generator /Transformer/ System neutral has no earth connection. | Adequate earthing for generator/ transformer neutral must be ensured. | Done | Apr 30 2018 | On 11/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per cable current ampacity/load current; if adjustment is not possible, replacement will be the only way. | Corrected. Already Adjusted as per load demand | Dec 25 2018 | On 4-Mar-21: Not Corrected. On 12-04-2021: Factory is asking for timeline extension till 30-04-2021, which is not accepted. On 19/12/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Electrical Single Line Diagram (SLD) is available in the factory but some mismatch found. | As built Electrical SLD must be prepared; it must have factory's whole electrical installation information. |  | Dec 25 2018 | On 4-Mar-2021: Not Corrected. Not matching with field. Still some work need to do. On 12-04-2021: Factory is asking for timeline extension till 30-04-2021, which is not accepted. On 19/12/2023: Not corrected. Significant progress has been observed. SLD is accepted by RSC on 16-May-2023. But few mismatches have been found (earthing size inadequate for generator, ecc bus bar inadequate for LT panel, improper load identification, individual protection missing etc.). On 03/06/2024: Not Corrected. Due to changes of the electrical system from accepted SLD will be subjected to further review and acceptance. Need to communicate with the RSC with mentioning the changes and send the updated SLD. On 27/04/2026: Not Corrected. No significant progress observed since last follow-up inspection. SLD accepted from RSC on 28-Jun-2025 which is not as-built cases such as - information mismatch for transformer, cable, circuit breaker, individual protection, cable/circuit /load identification, inadequate/missing Ecc/ earth electrode. Factory need to re-submit update SLD to RSC for review for significant changes from accepted SLD. | 1 Month | In Progress
Follow Up Inspection |  | 52 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Corrected. Steam line are properly insulated. | Dec 25 2018 | On 4-Mar-21: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected. Already we conducted Thermography and corrected the hotspot area. | Dec 25 2018 | On 4-Mar-21: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: Heat shields/ blankets missing to protect component and operator from excessive heat. | Heat shields/blankets must be installed to shield hot surface to protect component and operator from excessive heat. Proper guards shall be provided after shielding hot surface. Blankets on exhaust manifold, turbocharger housing and other engine components is not necessary. Suggested to consult with the generator supplier/service provider/expert before doing the job. | We solved all issue accordingly as per RSC instruction, ---Done | Feb 29 2024 | On 03/06/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 55 | New Finding: Single point of disconnection is not provided for the electrical distribution board which has multiple sources. | Each electrical distribution board shall have readily accessible single point of disconnection where multiple sources are fed. | We ensured that each electrical distribution board are readily accessible single point of disconnection where multiple sources are fed. -Done | Feb 29 2024 | On 03/06/2024: Not Corrected. This issue found in another panel. On 27/04/2026: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 56 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Cable channels/ducts are kept neat and clean and we sealed properly thus no scope of ingression of fluffs. ---Done | Jan 29 2024 | On 03/06/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: Earth pit resistance test records found unsatisfactory for several pits of utility system. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be satisfactory and available to the Inspector when required. | We are maintaining the test record of Eart pit test as per instructions. ---Done | Jan 29 2024 | RPO Comments: On 11/02/2024 - The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. On 03/06/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: Hot spots have been observed at some points. (above 40ºC of ambient). | Hot spots must be eliminated from entire electrical system. |  | Jul 14 2024 | RPO Comments: On 07/04/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 27/04/2026: Not Corrected. Hotspot has been observed in few panels. | 1 Month | In Progress
Follow Up Inspection |  | 59 | New Finding: Thermographic survey is not performed for whole panel board (partially done on circuit breaker). | Thermography survey shall be conducted on entire electrical system in the facility at least twice in a year. And the remediation suggestions mentioned in the report shall be carried out. | We maintain the Thermography survey on entire electrical system in the facility at least twice in a year. -Done | Jul 14 2024 | On 27/04/2026: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: Insulation resistance record (cable information) doesn't match with field. (IR test not performed for all power cables, 25rm and above) | Field information must be reflected in the record. Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | we updated the Insulation resistance report as per RSC guideline. -Done | Jul 14 2024 | On 27/04/2026: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Inadequate working space around (or in front of) board/ panels and access to the board/ panels is obstacles | At least 1 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel. |  | Jul 14 2024 | RPO Comments: On 07/04/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 27/04/2026: Not Corrected. Inadequate working space around panels has been found in several panels. | 1 Month | In Progress
Follow Up Inspection |  | 62 | New Finding: Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ Busbar (TOB). | Each electrical circuit must be terminated at single MCB/MCCB terminals. | We terminated the single cable at single MCB/MCCB Terminal. -Done | Jul 14 2024 | On 27/04/2026: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Distribution board's and TOB (Tap-off box) top/bottom is left open (typical issue). | Each electrical distribution board or panel must be sealed to prevent the ingress of fluffs and dust. Adequate ventilation must also be ensured to maintain optimal operating temperatures. Cable glands should be used where required to secure cables and maintain the integrity of the seal. |  | May 27 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 64 | New Finding: Circuit breaker has no capacity information. | Each circuit breaker must be clearly labeled with its capacity information. |  | May 27 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 65 | New Finding: Panel room has inadequate illumination. | Ensure adequate illumination in the substation/panel room to facilitate comfortable maintenance activities. The lighting level needs to be maintained at a minimum of 150 lux to meet operational standards. |  | May 27 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 66 | New Finding: PVC pipe used for wiring in chemical storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. |  | May 27 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 67 | New Finding: Power sockets are kept on floor. | Power sockets must be securely installed on rigid supports or bases, positioned at a minimum height of 200 mm above the floor level. |  | May 27 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 68 | New Finding: Cables are laid on floor inside cable trench haphazardly. | Cables inside cable trench have to be guided and routed properly. A cable tray shall be installed in the trench to ensure proper support and dressing for cables. Cable trench must be kept clean. |  | May 27 2026 |  | 1 Month | In Progress

## Boiler
Date
10-May-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | IRIS FABRICS LIMITED, Zirani Bazar, Kashimpur, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2022-05-26
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 4935 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | Done. Emergency stop push switches installed on the boiler control panel and outside the boiler room near the entrance door | Dec 19 2024 | Comments on 5-Nov-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 10119 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | Done. Emergency stop push switch was installed near the entrance outside of the boiler room and on the boiler control panel. | Dec 19 2024 | Comments on 5-Nov-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 12627 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | Done. Emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Dec 19 2024 | Comments on 5-Nov-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 4935 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Done. Low Low Water Level (LLWL) has been marked properly on water level gauge glass system. | Dec 19 2024 | Comments on 5-Nov-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 10119 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Inprogress. within given timeline we'll ensure the Low Low Water Level (LLWL) mark properly on water level gauge glass system. | Dec 19 2024 | Comments on 5-Nov-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 6 | BB 12627 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Inprogress. within given timeline we'll ensure the Low Low Water Level (LLWL) mark properly on water level gauge glass system. | Dec 19 2024 | Comments on 5-Nov-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 7 | BB 4935 | A boiler with a height of 8 feet or more was observed with an inadequate platform and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet and a railing with a minimum height of 3.5 feet should be provided. | Done. We constructed adequate platform and handrial to make it accessable. | Dec 19 2024 | Comments on 5-Nov-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 4935 | Necessary technical documents (manufacturing drawings & calculations) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Now all Necessary technical documents (manufacturing drawings & calculations) is available to verify boiler design and operation parameters. | Dec 19 2024 | Comments on 5-Nov-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 10119 | Leakage was observed from the water level gauge glass. | The water level gauge glass must be tightened or replaced if necessary. | Done. We have solved the leakage at water level gauge glass. | Nov 19 2024 | Comments on 5-Nov-24: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 10119 | The economizer was not equipped with a safety valve. | Economizers that can be isolated from a boiler allowing the economizer to become a fired pressure vessel, shall have a minimum of one pressure safety valve in a location recommended by the manufacturer or as close as practical to the economizer outlet. | Done. We have equipted a safety valve with the Economizer. | Nov 19 2024 | Comments on 5-Nov-24: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 4935 | Steam line connection is not terminated properly. | Any unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | Done. Steam line connection is terminated properly. | Dec 19 2024 | Comments on 5-Nov-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 12 | BB 4935 | Valves are observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. | Inprogress. Within given timeline we'll take initiative regarding this issue. | Oct 31 2024 | Comments on 5-Nov-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline | 2 WEEKS | In Progress
Initial Inspection | External visual inspection | 13 | BB 10119 | Valves are observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. | Inprogress. Within given timeline we'll take initiative regarding this issue. | Oct 31 2024 | Comments on 5-Nov-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline | 2 WEEKS | In Progress
Initial Inspection | External visual inspection | 14 | BB 12627 | Valves are observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. | Inprogress. Within given timeline we'll take initiative regarding this issue. | Oct 31 2024 | Comments on 5-Nov-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline | 2 WEEKS | In Progress
Initial Inspection | Functional test inspection | 15 | BB 12627 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | Done. The Steam Pressure limiter has installed | Nov 19 2024 | Comments on 5-Nov-24: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 16 | BB 4935 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | Done. The Steam Pressure limiter has installed | Nov 19 2024 | Comments on 5-Nov-24: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 17 | BB 12627 | There was no Low Low Water (LLWL) level trip with an interlock for the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | Done. We provide the Low Low Water (LLW) tripping mechanism for the boiler | Oct 27 2024 | Comments on 5-Nov-24: Will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 18 | BB 4935 | There was no Low Low Water (LLWL) level trip with an interlock for the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | Done. We provide the Low Low Water (LLW) tripping mechanism for the boiler | Oct 27 2024 | Comments on 5-Nov-24: Will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification