## Structural
Date
03-May-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | KNIT CONCEPT LIMITED, AZAD PLAZA. D.N.ROAD, FATULLAH.NARAYANGONJ, BANGLADESH., Naranyanganj
Date of Inspection |  | 2025-03-09
Finance Plan Agreed
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Stress in the foundation exceeds the normal design limit (Factory Building). | A geotechnical engineer is required to prepare a new soil test report to determine the actual pile capacity up to the full depth of the pile. | In Progress | Jun 17 2025 | .On 16-Oct-2025: No action has been taken. The extended timeline was 17 Jun 2025. A geotechnical engineer is required to prepare a new soil test report (as a part of DEA) to determine the actual pile capacity up to the full depth of the pile. Progress Status: 0% RPO Comments: On 23-Feb-2026 the design documents are pending to be submitted to RSC. | within 6 weeks | In Progress
Initial Inspection |  | 2 | Stress in the foundation exceeds the normal design limit (Factory Building). | Based on the actual pile capacity, the building engineer is required to check the adequacy of the foundation and prepare a design report as per 1.9.1 BNBC. Submit it to RSC for review. | In Progress | Jun 17 2025 | .On 16-Oct-2025: This issue is required to be addressed in the DEA. As of the inspection date, no action has been taken. The factory is required to appoint a consultant to conduct the DEA for this building and submit the report to the RSC for review. Progress Status: 0% RPO Comments: On 23-Feb-2026 the design documents are pending to be submitted to RSC. | within 6 weeks | In Progress
Initial Inspection |  | 3 | Stress in the foundation exceeds the normal design limit (Factory Building). | Produce and actively manage a floor load plan. | In Progress | Jun 17 2025 | .On 16-Oct-2025: Load Plans are required to be prepared as a part of DEA. Till the date of inspection, no action has been taken regarding this issue. During the inspection, floor loading was found within 3 kPa. Progress Status: 0% RPO Comments: On 23-Feb-2026 the design documents are pending to be submitted to RSC. | within 6 weeks | In Progress
Initial Inspection |  | 4 | Stress in the foundation exceeds the normal design limit (Factory Building). | Implement remediation work if required. | In Progress | Nov 6 2025 | .On 16-Oct-2025: After receiving the DEA acceptance from RSC the factory is required to carry out remedial work (if any). Progress Status: 0% RPO Comments: On 23-Feb-2026 the design documents are pending to be submitted to RSC. | within 6 months | In Progress
Initial Inspection |  | 5 | Stress in the foundation exceeds the normal design limit (Factory Building). | Implement floor load plan. | In Progress | Nov 6 2025 | .On 16-Oct-2025: Load Plans are required to be prepared as a part of DEA. Till the date of inspection, no action has been taken regarding this issue. During the inspection, floor loading was found within 3 kPa. The factory will post final load plan and maintain accordingly after the acceptance. Progress Status: 0% RPO Comments: On 23-Feb-2026 the design documents are pending to be submitted to RSC. | within 6 months | In Progress
Initial Inspection |  | 6 | Lack of material test report (Factory Building). | Take a minimum of 4 no of 100 mm diameter concrete core from columns (lower level) to verify the in-situ concrete strength. | In Progress | Jun 17 2025 | .On 16-Oct-2025: Core are taken as a part of DEA. Till the date of inspection, no action has been taken. The factory is required to appoint a consultant to perform DEA for this building and submit the DEA report to RSC for review. Progress Status: 0% RPO Comments: On 23-Feb-2026 the design documents are pending to be submitted to RSC. | within 6 weeks | In Progress
Initial Inspection |  | 7 | Stress in flat slabs exceeds the normal design limit (Factory Building). | The building engineer is required to check the adequacy of the flat slab as part of the design report. | In Progress | Jun 17 2025 | .On 16-Oct-2025: This issue is required to be covered in DEA. Till the date of inspection, no action has been taken. The factory is required appoint a consultant to perform DEA for this building and submit the DEA report to RSC for review. Progress Status: 0% RPO Comments: On 23-Feb-2026 the design documents are pending to be submitted to RSC. | within 6 weeks | In Progress
Initial Inspection |  | 8 | Stress in flat slabs exceeds the normal design limit (Factory Building). | Take a minimum of 2 no of concrete core from the slab to verify the in-situ concrete strength. | In Progress | Jun 17 2025 | .On 16-Oct-2025: Core are taken as a part of DEA. Till the date of inspection, no action has been taken. The factory is required appoint a consultant to perform DEA for this building and submit the DEA report to RSC for review. Progress Status: 0% RPO Comments: On 23-Feb-2026 the design documents are pending to be submitted to RSC. | within 6 weeks | In Progress
Initial Inspection |  | 9 | Discrepancy in construction/local authority approval drawing (Factory Building). | The factory is required to collect a revised permit drawing/layout from the local authority for the additional floor at the roof and reflect the onsite condition. Otherwise, remove the undocumented floor from the roof. | In Progress | Nov 6 2025 | .On 16-Oct-2025: No action has been taken in this regard. The factory is required to obtain the revised permit drawings from the local authority for approval. Progress Status: 0% RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | within 6 months | In Progress
Initial Inspection |  | 10 | Discrepancy in construction/local authority approval drawing (Factory Building). | Also, prepare an accurate as-built drawing as per the onsite condition. | In Progress | Jun 17 2025 | .On 16-Oct-2025: As-built drawings are required to be prepared as a part of DEA. Till the date of inspection, no action has been taken. The factory is required to prepare an accurate as-built drawing as per the onsite condition. Progress Status: 0% RPO Comments: On 23-Feb-2026 the design documents are pending to be submitted to RSC. | within 6 weeks | In Progress
Initial Inspection |  | 11 | Lack of lateral stability (Utility Shed). | The building engineer is required to check the lateral stability of the shed and prepare an Engineering Assessment (EA) report as per 1.9.1 BNBC. | In Progress | Jun 17 2025 | .On 16-Oct-2025: This issue is required to be addressed in the EA. As of the inspection date, no action has been taken. The factory is required to appoint a consultant to conduct the EA for this building and submit the report to the RSC for review. Progress Status: 0% RPO Comments: On 23-Feb-2026 the design documents are pending to be submitted to RSC. | within 6 weeks | In Progress
Initial Inspection |  | 12 | Lack of lateral stability (Utility Shed). | Implement remediation work if required. | In Progress | Nov 6 2025 | .On 16-Oct-2025: After receiving the EA acceptance from RSC the factory is required to carry out remedial work (if any). Progress Status: 0% RPO Comments: On 23-Feb-2026 the design documents are pending to be submitted to RSC. | within 6 months | In Progress
Initial Inspection |  | 13 | Absence of bracing system (Yarn Store Shed). | The building engineer is required to prepare a safety check report with a remediation plan incorporating a bracing system. | In Progress | Jun 17 2025 | .On 16-Oct-2025: This issue is required to be addressed in the safety check report. As of the inspection date, no action has been taken. The factory is required to appoint a consultant to prepare the safety check report for this building and submit the report to the RSC for review. Progress Status: 0% RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | within 6 weeks | In Progress
Initial Inspection |  | 14 | Absence of bracing system (Yarn Store Shed). | Implement remediation work where required. | In Progress | Nov 6 2025 | .On 16-Oct-2025: After receiving the EA (safety check report) acceptance from RSC the factory is required to carry out remedial work (if any). Progress Status: 0% RPO Comments: On 23-Feb-2026 the design documents are pending to be submitted to RSC. | within 6 months | In Progress
Initial Inspection |  | 15 | Nonstructural elements found not anchored/braced (Yarn Store Shed). | The building engineer is required to anchor/brace all nonstructural elements within the factory. | In Progress | Nov 6 2025 | .On 16-Oct-2025: No action has been taken. The building engineer is required to anchor/brace all nonstructural elements within the factory. Progress Status: 0% RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | within 6 months | In Progress
Initial Inspection |  | 16 | Lack of approval layout/drawing from local authority. (Yarn Store Shed, Utility Shed). | The factory is required to collect approval layout/drawing from the relevant local authority for all structures within the factory. | In Progress | Nov 6 2025 | .On 16-Oct-2025: No action has been taken in this regard. The factory is required to obtain the permit drawings from the local authority for approval. Progress Status: 0% RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | within 6 months | In Progress

## Fire
Date
03-May-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | KNIT CONCEPT LIMITED, AZAD PLAZA. D.N.ROAD, FATULLAH.NARAYANGONJ, BANGLADESH., Naranyanganj
Date of Inspection |  | 2025-03-09
Finance Plan Agreed
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The exit stair enclosures are not separated from work areas and other spaces on each floor by fire-rated construction. Location: Factory Building (6-Storied (with partial occupied roof)-main production building). | The exit stair enclosure shall be provided with a minimum 1-hr fire resistance rating for buildings with 3 or fewer stories and a minimum of 2- hr. fire resistance rating for buildings 4 or more stories. Provide 1-hr. fire rated door and seal all penetrations and openings by 1 hr. fire rated fire rated barrier construction for building with 3 or fewer stories. Provide 1.5 hr. fire rated door and seal all penetrations and openings by 2 hr. fire rated fire rated barrier construction for building with 4 or more stories in accordance with section 6.3.1.2 of RSC Technical Guidelines (Standard)¹ V1.0. Provide a fire-resistive rated assembly between the exterior exit stairs and the building up to 10 ft. beyond the end of the stair to achieve the required separation. The rated assembly shall be approved and/or designed by a qualified fire protection engineer. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 2 | Sliding type doors have provided along means of egress [building exits, exit stairs, along egress routes, exit discharge]. Location: Factory Building, Yarn Store Shed, Utility Shed. | Replace all collapsible/sliding/shutter type doors & gates by the side-hinged swinging type doors in accordance with section 6.8.1 of RSC Technical Guidelines (Standard)¹ V1.0. All doors in a means of egress shall be of the side-hinged swinging type. Roll--down and sliding gates and shutters shall not be allowed. Doors serving an occupant load of more than 50 shall swing in the direction of egress travel. | In Progress | Jun 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 1 month | In Progress
Initial Inspection |  | 3 | Doors along means of egress are provided with non-compliant locking devices. Location: Occupied roof-floor exits, Medical/Doctor room. | Remove locking devices from all egress devices in accordance with section 6.8.2 of RSC Technical Guidelines (Standard)¹ V1.0. No locks or other devices shall be installed on a means of egress component that would prevent any occupant from having safe egress from the building or structure and doors shall not be locked in the direction of egress under any conditions. All hasps, locks, slide bolts, and other locking devices are prohibited unless meet the following conditions: • Doors may be locked where the latch and lock are disengaged with one motion where the occupant load does not exceed 49 persons. Turning a door handle and disengaging a lock is considered two motions. • Doors may be provided with locking hardware from the ingress side provided that a panic bar is installed on any door with an occupant load exceeding 49 persons. | Corrected | Mar 11 2025 | On 22-Apr-26 (Special Inspection): Not Corrected. Non-compliant locking features were identified at multiple exit points, including main factory building, yarn store shed. | Immediate | In Progress
Initial Inspection |  | 4 | Storage was located in the exit stair/stair enclosure. Location: All stairs of 6-Storied-factory building. | Remove all storage from exit stairs and egress path in accordance with section 13.8 of RSC Technical Guidelines (Standard)¹ V1.0. Means of egress shall be maintained continuously free and clear of all obstructions or impediments to full instant use in the case of fire or other emergency. No furnishings, decorations, or other objects shall obstruct exits and access to exits. Nothing shall obstruct or impede visibility to exits. | Corrected | Mar 11 2025 | On 22-Apr-26 (Special Inspection): Not Corrected. Storage was located obstructing the exit stairs on most of the floors. | Immediate | In Progress
Initial Inspection |  | 5 | The egress path along means of egress has interrupted by obstruction/storage/process work/machineries. Location: Factory Building, Yarn Store Shed, Utility Shed. | Keep egress paths and stairs clear of storage/obstruction in accordance with section 6.3.9 of RSC Technical Guidelines (Standard)¹ V1.0. Means of egress shall be maintained continuously free and clear of all obstructions or impediments to full instant use in the case of fire or other emergency. No furnishings, decorations, or other objects shall obstruct exits and access to exits. Nothing shall obstruct or impede visibility to exits. | Corrected | Mar 11 2025 | On 22-Apr-26 (Special Inspection): Not Corrected. Storage was located obstructing the egress path, aisles, etc. | Immediate | In Progress
Initial Inspection |  | 6 | Aisles were found missing on several locations throughout the building. Location: Factory Building, Yarn Store Shed, Utility Shed. | Aisles shall be provided with a minimum unobstructed clear width of 0.9 m (36 in.) in accordance with section 6.5.1 of RSC Technical Guidelines (Standard)¹ V1.0. | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 7 | The exit discharge path [serving exit stair-3 (South-West Stair)] is less than 10 ft wide and is not separated from the building interior which is not in accordance with section 6.17.2 of RSC Technical Guidelines (Standard)¹ V1.0. | Egress courts less than 3050 mm (10 ft) in width (as measured from the building and the adjacent property line) shall be provided with walls having a 1-hr fire resistance rated construction for a distance of 3050 mm (10 ft) above the floor of the court. Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft. to provide a minimum 1-hr fire separation. Alternatively, provide a second remote discharge path to the public way. | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 8 | Electrical panels were located in the exit stair enclosure. Location: Stair-3 (4th Floor) of Factory building.. | Remove and re-locate all electrical panels and water pumps from exit stair enclosures. Or, Provide fire separation with stair enclosure in accordance with section 6.3.1 of RSC Technical Guidelines (Standard)¹ V1.0. | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 9 | Storage room discharges directly into the exit stair enclosure. Location: Ground floor (Stair-1 (South-East Stair) of Factory building. | Openings from exit enclosure to Storage areas/ basements/ transformer rooms/ generator rooms/ boiler rooms and similar normally unoccupied spaces shall be provided with a vestibule with fire rated construction and openings in accordance with section 6.14.3 of RSC Technical Guidelines (Standard)¹ V1.0. . Provide a 1.5 hr. fire rated door on the exit stair side and a 1- hr. fire rated door on the Store, generator, sub-station room side . Ensure that the fire rating of the vestibule construction matches that of the exit stair enclosure as per RSC Technical Guidelines (Standard)¹ V1.0. section 6.14.3. The minimum width for vestibules shall not be less than 1.1m and length 1.8m. | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 10 | Dead-end aisle/corridor exceed 20ft in non-sprinklered area (found 72 feet) at office area (F occupancy). Location: 1st floor (office block) of Factory Building. | Reconfigure the egress arrangement to reduce the maximum dead-end corridor to meet Table 6.13.3 of RSC Technical Guidelines (Standard). | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 11 | Parapets or guards are provided in occupied roof which is less than 1067mm (42 inch). Location: Factory Building. | Provide parapets or guards with a minimum height of 1067mm (42 inch.) in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.12. Open guards/parapets shall have intermediate rails or pattern such that a sphere 200 mm (8 in.) in diameter cannot pass through any opening up to a height of 865 mm (34 in.). Guard shall construct in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.12. | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 12 | Boiler or furnace room is not properly separated by fire rated construction with other Occupancies/Areas. Location: Utility shed. | Boilers or other heat producing equipment shall be separated from other occupancies by a minimum 1-hr fire rated construction (wall, floor, slab etc.). Seal all penetrations and openings (door, window etc.) should be protected by 0.75-hr (45 min) fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. Or Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. Boiler room separation shall meet section 3.4.2.1.2 of RSC Technical Guideline (Standard). | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 13 | Generator room is not properly separated by fire rated construction with other Occupancies/Areas. Location: Utility shed. | Generator room shall be separated from other occupancies by a minimum 2-hr fire rated construction (wall, floor, slab etc.). Seal all penetrations and openings (door, window etc.) should be protected by 1.5-hr fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. Or Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. Generator room separation shall meet section 3.4.2.1.2 of RSC Technical Guideline (Standard). | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 14 | Transformer is not properly separated by fire rated construction with other Occupancies/Areas. Location: Ground floor of Factory Building | Oil filled transformer shall be separated from other occupancies by a minimum 2-hr fire rated construction (wall, floor, slab etc.). Switch gears and transformer bays shall be separately housed with a 2-hr rated wall in between. Seal all penetrations and openings (door, window etc.) should be protected by 1.5-hr fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. Oil filled transformers shall not be housed above ground level. Or, Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. Transformer room separation shall meet section 3.4.2.1.4 of RSC Technical Guideline (Standard). | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 15 | Compressor room was not separated from the other occupancy at ground floor. Location: Factory building (Ground floor) & Utility shed. | Separate the compressor by a minimum 1-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | In Progress | Aug 6 2025 | On 22-Apr-26: (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 16 | Flammable liquid storage area is not separated by fire-rated construction (openings, non-rated doors, penetrations). Location: Utility Shed (Generator room). | Separate the flammable liquid storage room by a minimum 2- hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 17 | Elevator shafts open directly into the exit enclosure, which is a violation of RSC Technical Guidelines (Standard) 6.14.3. Location: Factory Building-(Ground & 2nd floor of Stair-1 (SE Stair) | Provide a minimum 2-hr fire rated elevator shaft to separate it from each floor. Seal all openings to maintain fire separations. Factory is recommended to follow RSC published "SUPPLEMENTARY PAPER ON REMEDIATION GUIDANCE ELEVATOR OR LIFT SHAFT OPENING IN EXIT ENCLOSURES" for different solutions. | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 18 | Elevator shafts open directly into the production floor without proper fire separation due to unprotected opening. Location: Factory Building-(1st, 4th & 5th). | Elevator shaft shall be separated from production area by 2 hours fire rated construction. 2-hr fire barriers shall be protected with minimum 1.5-hr fire protective opening assemblies. | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 19 | Unsealed penetrations are located in the fire-rated floor/ceiling assemblies in between the exterior wall and due to electrical cable riser, PVC plumbing pipes & glass partition etc. Location: Factory Building. | Seal all penetrations and openings in floor/ceiling assemblies by a listed through-penetration fire stop system tested in accordance with ASTM E814 or approved alternative standard to maintain minimum 3-hr. fire resistance rating. Installation shall be as per manufacturer published installation guideline and the certification authority guideline to ensure the fire?rating in accordance with section 4.7 of RSC Technical Guideline (Standard) Or, Provide a minimum 2-hr fire rated shaft to separate the penetration from each floor level. Factory shall ensure that, all the design, datasheet, certificate, and proposed drawing of installation has been reviewed from the RSC prior to install the passive fire protection system (If required). | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 20 | The required fire separation distance does not comply with the requirements of BNBC 2006/2020. Location: Factory Building, Utility Shed. | The exterior walls shall have a fire resistance and opening protection as specified in BNBC 2006, Tables 3.2.2 and Part 3 Section 2.4.1.3. / BNBC 2020 Part 3 Table 3.2.2 & 3.2.3 and BNBC 2020 Part 3 Section 2.4.1.3. | In Progress | Nov 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 6 months | In Progress
Initial Inspection |  | 21 | The main structural element of the interim building is steel which is non-rated construction and were found in exposed condition without any fire protection. Location: Yarn Store Shed [Occupancy: Storage (H2)], Utility Shed [Occupancy: Utility (L) & Storage (H2)]. | As per RSC Technical Guideline and BNBC 2006, The Fire rating of the structure requires to be confirmed as per BNBC 2006. The "Ministry of Housing and Public Works” has issued a resolution based on the recommendations from the House Building Research Institute (HBRI) and the Public Works Department (PWD) to assess structural fire protection requirements of steel buildings (unprotected non-combustible construction type) according to BNBC 2020. The construction type shall confirm to be in accordance with BNBC 2020 Part-3, Table 3.1.7. Ensure fire resistive rated construction following Table 3.3.1 (a) Part 3 Section-3, Table 3.2.2 and Table 3.2.3 Part 3 Section 2 and Table 4.1.1 from BNBC 2020 Part 4 Section 1. Provide design philosophy to determine the construction type as per BNBC 2020. If any construction rating requires, Consult a qualified fire protection engineer to achieve the require fire rating. | In Progress | Nov 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 6 months | In Progress
Initial Inspection |  | 22 | Liquefied or compressed gas cylinders & CNG high pressure appliances (i.e. CNG high pressure line & Pressure reducing/regulating control unit) were located within the factory on ground floor east side without adequate fire separation. Location: Factory Building (Roof-top: LPG & Ground floor: CNG). | Remove the liquefied or compressed flammable gas cylinders. The storage or use of liquefied or compressed flammable gas (LPG/CNG) cylinders within the factory building as per section 3.4.2.1.11 of RSC Technical Guidelines (Standard)¹ V1.0. Or, Factory shall follow the requirements RSC Published "SUPPLEMENTARY PAPER ON TECHNICAL GUIDANCE NOTE FOR USE OF LIQUIFIED OR COMPRESSED FLAMMABLE GAS IN FACTORY PREMISES" to use or store liquefied or compressed flammable gas cylinders in the factory premises. | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 23 | Rooms used for storage of combustible materials are not separated from the surrounding occupancy. Location: Factory Building (Roof-top & Ground floor) and Utility shed. | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour construction in accordance with section 3.4.2.1.5 of RSC Technical Guideline (Standard) | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 24 | Areas used for in-process storage of combustible materials are open to the surrounding occupancy (specify the occupancy/area, location) Location: Factory Building (Ground, 1st, 2nd & 4th floors). | Provide defined storage areas and limit the storage arrangement as follows: Maximum height of 2.45 m and maximum area of 23 m² and is separated by a minimum 3.0 m (10ft) from other storage areas and they do not exceed 10 percent of the building area of the story in which they occur. or, If sprinkler protected, Maximum height 12 ft (3.66 m) and maximum area of 1000 ft² (93 m²) and separated by a at least 25 ft (7.62 m) and does not constitute more than 10 percent of the building area or 4000 ft² (372 m²) of the sprinklered area, whichever is greater. or, Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 25 | Storages were found underneath the cutting tables. Location: Factory Building (4th Floor). | Storage underneath the cutting tables shall be kept clear of combustibles at all time, except as provided for miscellaneous storage in accordance with 3.4.2.1.6 or where automatic sprinkler protection is installed. Where an automatic sprinkler system is installed sprinklers are required to be installed beneath cutting tables greater than 4 ft in width that are used for storage of combustibles. | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 26 | Combustible construction material has been used in the building. Location: Door and Partition wall of Jacquard Section. Combustible construction materials were used in the shed. (Wooden wall, Plywood wall, false ceiling, wooden palette etc.) Location: Factory Building (5th Floor). | Remove all combustible construction materials (Wooden wall, ceiling and doors) in the building and replace by non combustible materials. (BNBC 2006 Section-2.8 and Table-4.2.2 | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 27 | The fire detection system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. Location: All Buildings. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. Submit the as built fire alarm and detection system drawing and documents to RSC for review. Once the design is reviewed, install the fire alarm and detection system throughout the building in accordance with review comment, RSC Technical Guidelines (Standard) and NFPA 72. After installation the owner shall conduct internal testing and commissioning and then contact the RSC for witness of final acceptance testing. | In Progress | Nov 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Design within 2 months and Installation within 4 months | In Progress
Initial Inspection |  | 28 | The required standpipe system is not installed in accordance with the RSC Technical Guidelines (Standard)¹ V1.0. Location: Factory Building. | A standpipe system shall be installed in buildings with the highest occupiable floor 10 m (33 ft.) above grade or more to meet section 5.4.2 of RSC Technical Guideline (Standard). If the building is protected throughout by an approved automatic sprinkler system a class I system shall be permitted.) Installation of the Standpipe system shall be in accordance with RSC Technical Guidelines (Standard)¹ V1.0. section 5.4 and NFPA 14. Submit the standpipe system drawing to RSC for review. Once reviewed, install or modify the standpipe system throughout the building in accordance with RSC Technical Guidelines (Standard)¹ V1.0. and NFPA 14,20,22 and 24. After installation the owner shall contact the RSC for witness of conducting the final acceptance testing of the standpipe system. | In Progress | Nov 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Design within 2 months and Installation within 4 months | In Progress
Initial Inspection |  | 29 | Evacuation map needs to be updated and emergency evacuation plan is found missing. Locations: All Buildings. | Updated fire evacuation maps shall be posted at the entrance to each exit stair and emergency evacuation plan needs to be developed. | In Progress | Jul 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 2 months | In Progress
Initial Inspection |  | 30 | Building does not have stair/floor level designation signs at required locations on all floors. Location: All Buildings. | Provide stair designation sign at each floor entrance from the stair to the floor in English and Bengali. Signs shall indicate the name of the stair and the floor level. Signs shall be posted adjacent to the door in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.9.3. | In Progress | Jul 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 2 months | In Progress
Initial Inspection |  | 31 | Building does not have occupant load signs at required locations on all floors. Location: All Buildings. | Post the occupant load for every assembly and production floor in a facility in a conspicuous space near the main exit or exit access doorway for the space in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.4.4. | In Progress | Jul 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 2 months | In Progress
Initial Inspection |  | 32 | Exit sign not provided at exit. Location: All Buildings. | Lighted exit signs shall be placed at entrance to an exit. Additional directional exit signs shall be placed throughout the facility anywhere the continuation of the egress is not obvious. Lighted exit signs shall be provided with either battery backup or uninterruptable power supply systems and shall be continuously illuminated at all times. Exit Sign shall provide in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.11. | In Progress | Jul 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 2 months | In Progress
Initial Inspection |  | 33 | Directional signs are not provided where direction of the path of travel to an exit has changed. Location: All Buildings. | Illuminated directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious. | In Progress | Jul 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 2 months | In Progress
Initial Inspection |  | 34 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. Location: All Buildings. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. Illumination on means of egress shall meet in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 10.12.2. | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 35 | Inspection, testing and maintenance for the fire detection and alarm system was not in accordance with standard. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with Table-14.3.1 of NFPA 72. | In Progress | Dec 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 1 month (after installation) | In Progress
Initial Inspection |  | 36 | Inspection, testing and maintenance of the fire pump system is not in accordance with NFPA 25. | Inspect, test and maintain the fire pump system and keep written records on-site, in accordance with NFPA 25 and RSC standards. | In Progress | Dec 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 1 month (after installation) | In Progress
Initial Inspection |  | 37 | Inspection, testing and maintenance of the standpipe system is not in accordance with NFPA 25. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 25 and RSC standards. | In Progress | Dec 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 1 month (after installation) | In Progress
Initial Inspection |  | 38 | Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with the RSC standard. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with the RSC standard. Keep written records on-site. | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress
Initial Inspection |  | 39 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records on- site, in accordance with NFPA 10 and RSC standards. | In Progress | Aug 6 2025 | On 22-Apr-26 (Special Inspection): Not in scope. | Within 3 months | In Progress

## Electrical
Date
03-May-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | KNIT CONCEPT LIMITED, AZAD PLAZA. D.N.ROAD, FATULLAH.NARAYANGONJ, BANGLADESH., Naranyanganj
Date of Inspection |  | 2025-03-09
Finance Plan Agreed
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Electrical Single Line Diagram (SLD) is not available in the factory. | As-built Electrical Single Line Diagram (SLD) must be prepared by a qualified engineer, including all essential details of the electrical system. This diagram must be reviewed and approved by the RSC. The accepted SLD needs to be implemented at the factory. All cables, all circuits, all terminals, all equipment are required to be identified as per the accepted Single line diagram. | In Progress | Nov 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 6 Months | In Progress
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not installed where the risk index equal or greater than 40 (According to BNBC). | For factory buildings with a Risk Index of 40 or higher, a comprehensive Lightning Protection System (LPS) required to be designed as per standard for the entire facility. Once the LPS is properly designed, it must be installed according to the design specifications to ensure effective protection against lightning strikes. | In Progress | Nov 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 6 Months | In Progress
Initial Inspection |  | 3 | Electrical safety training program is not initiated by qualified Electrical personnel. | Electrical safety training and awareness programs for electrical personnel must be conducted regularly by qualified personnel and documented. This periodic task is crucial for continuously improving overall electrical safety for factory staff. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 4 | No policies for PPE/LOTO (Lock-Out-Tag-Out) are introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement PPE (Personal Protective Equipment) and LOTO (Lock-Out-Tag-Out) policy using LOTO devices to ensure personnel safety during maintenance activities. All LOTO usage records must be maintained for compliance and safety monitoring. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 5 | There is no programmed schedule for periodical inspection & testing of electrical equipment. | Electrical maintenance program shall be developed to include regular inspections and testing of electrical systems, focusing on preventive and proactive measures. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 6 | Transformer Oil Test (dielectric strength test) report is unavailable. | Testing of transformer oil, specifically the dielectric strength test needs to be conducted at least once in a year from government-authorized entities such as BPDB, BREB, PGCB, EGCB, DESCO, or DPDC. This ensures adherence to an unaltered, verifiable, standardized format, thereby maintaining the integrity and reliability of the transformer's insulation system. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 7 | Earth pit resistance record is not available. | All earthing systems must be tested for resistance on a dry day at least once every two years. Records of each earthing test and its results must be available for inspection when required. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 8 | Insulation resistance test of electrical power cables is not performed. | Insulation resistance testing of all cables (excluding those less than 25 sq.mm) must be conducted once every two years and documented. This testing may require power shutdown to ensure accurate results and safety. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 9 | Thermography scanning report is not available. | Thermography survey of the entire electrical system must be conducted and documented by bi-annual, including real-time and scanned images with recommendations for corrective actions. This helps identify overheating, loose connections, and safety hazards, preventing equipment failure and reducing downtime. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 10 | Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | CPR instructions must be posted near all electrical installations (such as LT panels, MDBs, FDBs, DBs, and SDBs) in a clearly visible location. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 11 | Danger signs are not available on each electrical panel/board. | Danger signs must be displayed on each electrical panel or board, clearly indicating the proper voltage information to ensure safety and awareness of electrical hazards. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 12 | Distribution board is installed without proper grout. | Distribution panels and boards must be installed with proper grouting to ensure a stable and secure foundation, minimizing the risk of movement or vibration that could affect the operation of electrical components. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 13 | Cables inside distribution board are disorganized. | Cables inside each distribution board must be well-organized to prevent confusion during troubleshooting and maintenance activities. Proper cable management helps ensure clear identification of circuits and reduces the risk of errors. The use of a structured distribution board form is appreciated as it further aids in system clarity and documentation, improving safety and efficiency. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 14 | Uncovered cable tray used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | In Progress | Aug 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 3 Months | In Progress
Initial Inspection |  | 15 | Transformer Silica gel is discolored. | Discolored Silica gel needs to be changed. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 16 | Transformer Breather oil cup is empty. | Transformer breather oil cup must be filled up to the oil-mark on the cup. Ensure the tube inside the breather cup is properly submerged in oil. If it's not, air may bypass the oil seal, reducing the effectiveness of moisture control. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 17 | Lint and dust deposited on and around the transformer. | Transformer top and around it shall be kept neat and clean. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 18 | Oil level in transformer conservator oil tank is below minimum level. | Minimum oil level in the transformer conservator oil tank must be maintained and checked periodically. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 19 | No working separation between LT ( Low Tension) panel/s and HT (High Tension) unit/s (Transformer). | A solid-type working separation, preferably a brick wall, must be established between LT (Low Tension) and HT (High Tension) areas. Additionally, adequate working clearance and proper ventilation must be maintained in accordance with RSC technical guidelines. This ensures the safe operation of electrical systems, prevents cross-contamination between LT and HT sections, and enhances overall safety and operational efficiency. | In Progress | Sep 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 4 Months | In Progress
Initial Inspection |  | 20 | Inadequate working space around transformer for performing maintenance work. | Adequate working clearance and proper ventilation must be maintained in accordance with RSC technical guidelines. This ensures the safe operation of electrical systems, prevents cross-contamination between LT and HT sections, and enhances overall safety and operational efficiency. Access needs to be restricted to qualified personnel wearing appropriate PPE (Personal Protective Equipment). | In Progress | Sep 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 4 Months | In Progress
Initial Inspection |  | 21 | Transformer body earthing (equipment earthing) cable is not available/ inadequate. | The size of the earth cable shall be determined according to BNBC or the Adiabatic method. The number of earth pits shall be calculated based on acknowledged standards to ensure effectiveness. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 22 | Generator body earthing (equipment earthing) cable is not available/ inadequate. | Ensure that the generator is equipped with at least two separate earth pits. The size of the earth cable shall be determined according to BNBC or the Adiabatic method. The number of earth pits shall be calculated based on acknowledged standards to ensure effectiveness. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 23 | Hot spots have been observed at some points. (above 40° C of ambient) | Hot spots throughout the entire electrical system must be eliminated to ensure safety and prevent potential equipment failures or hazards and reduce downtime and repair costs. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 24 | Generator terminal box left open to allow cable entry. | Generator terminal box must have a base plate installed, and cables entering the terminal box must be securely fixed with cable glands. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 25 | Power cables are not identified. | All power cables must be clearly and distinctly marked in accordance with the Single Line Diagram (SLD) to ensure proper identification, safe handling, and efficient operation. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 26 | Electrical panel board installed near combustible materials. | Factories shall install panel boards with appropriate protection. A minimum clearance of 10 feet must be maintained between the panel boards and any stored materials to ensure safety and compliance with regulations. Alternatively, Install protective barrier wall around the panel to reduce potential hazards. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 27 | Distribution boxes are inaccessible or cannot be opened to perform any maintenance work or inadequate clearance. | Each electrical distribution board or panel must be easily accessible, maintaining a minimum working clearance of 1 meter (or equal to the width of the board/panel, whichever is greater). The panel's height must not be exceed 2 meters, and the bottom must be at least 0.45 meters above from the floor or working platform (for wall-mount panel). The board/panel door must open at least 90 degrees to ensure safe and efficient operation and maintenance. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 28 | Electrical distribution box/panels are full of fluffs (lint/dirt). | Each electrical distribution board/panel must be sealed to prevent the ingress of fluffs, while ensuring adequate ventilation. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 29 | Panel doors are not connected with earth. | All metal components within the electrical system must be securely connected to the earth. This earthing is essential to mitigate the risk of electrical shock or electrocution by providing a safe path for fault currents to dissipate. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 30 | Circuit breaker has no capacity information. | Each circuit breaker must be clearly labeled with its capacity information. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 31 | Multiple cables from different electrical consumers are terminated at circuit breaker terminals. | Each electrical circuit must be terminated at a single circuit breaker terminal or busbar to ensure distribution and protection within the electrical system. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 32 | Enclosure of the Distribution Board is rusted. | The enclosures of Distribution Boards must be free of rust. Regular maintenance should be performed to prevent rust and ensure the longevity and safety of the electrical system. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 33 | Loop connection has been used powering multiple circuits through circuit breakers. | No loop connections are allowed. Each cable must be terminated with a single cable lug at each terminal. Combo bus bars are permitted if the incoming cable size meets the rated capacity. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 34 | The terminals of the circuit breaker, connected by copper buses, are neither separated by an insulating barrier nor insulated. | Separator must be used along the length of bare busbars (if the gap between busbars is less than 50mm). Proper insulating tubes can alternately applied to keep the phases separated from one another to ensure safety and prevent short circuits. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 35 | Cable connected to circuit breakers terminal without cable lug. | Each electrical circuit must be terminated at single busbar/circuit breakers terminal using cable proper sized cable lug (where applicable). | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 36 | Nut-bolt, bus-bar & washer are rusted in the sub/distribution board. | Rusted nut-bolt, bus-bar & washer must be replaced with new one. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 37 | Distribution Board's front door is left open for cable entry. | Each electrical distribution board/panel must be sealed to prevent the ingress of dust and debris, and a ventilation system must be ensured. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 38 | Panel door lock broken. | Provide proper type lock on panel door and keep the panel door close. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 39 | Circuit breaker is kept/installed inside of the DB without support. | Each MCB/ Relay/ Magnetic contactor/ any other electrical device must be installed inside of the DB with support (fixed base). | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 40 | Manually operated machines (may have chance to be touched by operator/user) have no earth connection. | Each manually operated machine, accessible to users/operators, must be equipped with an earth connection. Cable selection should be based on the protective device's response and the power demand of the circuit. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 41 | Unterminated live wire is kept inside the electrical panel, cable tray & floor. | All unterminated live power cables must be expeditiously removed. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 42 | Inadequate access to the compressor room poses a fall hazard. | The maintenance and operation area must be free of obstacles and all fall hazards. The floor should be even, and all trench covers must be aligned with the floor level to prevent injuries from uneven heights. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 43 | Cable duct/ channels are filled with fluffs (Lint/dust). | Cable channels and ducts must be kept clean and sealed to prevent any ingress of dust and debris. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 44 | Cables joint or tapping do not have adequate insulation and mechanical strength. | Cable joints shall be made through porcelain/PVC connectors with PIB tape wound around the joint in respect of conductivity, insulation, and mechanical strength. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 45 | Power cables entering or exiting from Distribution board/panel are not fixed. | Power cables entering or exiting the distribution board/panel must be fixed through the base or top plate with cable glands (metal or PVC) of the correct size. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 46 | Cable channel/ ducts are not connected with earth. | Ensure cable channels/ducts are grounded. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 47 | Outdoor Cable is not covered to protect from the weather effects. | All power cables exposed to weather shall have cover unless it is specified for outdoor wiring. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 48 | Flexible PVC pipe is used to cover power and signal cable for boiler. | Power and signal cable for boilers shall be distributed using proper type insulator to avoid damage of cables. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 49 | The Buchholz relay is not installed, compromising the transformer’s protection system. | The Buchholz relay must be integrated with the High Tension (HT) panel protection system to ensure effective monitoring and fault detection in transformer operations. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 50 | Heat shields/ blankets missing to protect component and operator from excessive heat. | Install heat shields or blankets to protect components and operators from excessive heat on hot surfaces. After providing shield or blankets, ensure proper guards are installed, except on exhaust manifolds, turbocharger housings etc. Consult with the generator supplier, service provider, or expert before proceeding with the installation. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 51 | No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation, with a thickness of at least 3 mm for rubber mats, must be provided at the working area of each electrical installation. Length of the mat shall be equal to 1 meter or the width of the board/panel, whichever is greater. This includes areas of LT panels, MDBs, DBs, SDBs, and other manually operated machinery to ensure safety and prevent electrical hazards. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 52 | Combustible materials are attached with electrical panel board/BBT/cable channel/duct. | All flammable and combustible materials, including water bottles and other items, must be cleared from electrical cable channels, ducts, and BBTs. Separate storage arrangements for these materials should be implemented. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 53 | Wooden support used for electrical installation/element. | Replace wooden support and each electrical devices shall be fixed with non-combustible support. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 54 | No mechanical guards are provided for rotating electrical equipment where necessary (in working floor). | Ensure all rotary installations are equipped with adequate safety measures, including the provision of mechanical guards to prevent accidents. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 55 | Power sockets are kept on floor/hung without support. | Power sockets must be securely installed on rigid supports or bases, positioned at a minimum height of 200mm above the floor level. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 56 | Power Cables are hanging without support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor cables must be covered, if required. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 57 | Maintenance movement is obstacle due to uneven height of cable trench in utility area (transformer). | The workspace surrounding the transformer, generator, or any other electrical installations must be level and uniform in height. This ensures safe and efficient access for maintenance and operational activities while minimizing potential trip hazards, thereby enhancing overall safety and productivity. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 58 | Lead acid battery terminals are filled with rust and left open. | Lead-acid battery terminals must be covered or capped, and any rust must be thoroughly cleaned to ensure safe and efficient operation. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 59 | Distribution boards have no clear identification markings. | Clearly mark all distribution boards, switchboards, sub-main boards, and switches for identification. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 60 | Burnt sign visible at circuit breaker/ cable lug. | Check the connections and circuit breaker to identify the cause of the burning. If necessary, replace the burned breaker. Assign an engineer to take the appropriate action based on the problem identified. | In Progress | Jun 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Initial Inspection |  | 61 | Protective device is not installed/ adjusted per load demand. | Protective devices must be installed or adjusted according to the connected load current. If adjustment is not feasible, replacement is necessary. Each motor load exceeding 376W requires separate protection, adhering to nameplate data for selecting the appropriate protective device. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 62 | The working space in front of the panel is uneven. | Ensure the grade, floor, or platform in the required working space is clear, level, and flat throughout its entire depth and width to facilitate smooth operation and prevent any trip hazards. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 63 | Indicator lamps installed on panel board are not operational. | All indicator lamps and metering devices installed on the panel board must be fully operational to prevent the risk of false or misleading information, which could compromise the safety and proper functioning of the electrical system. Regular checks and maintenance should be conducted to ensure their accuracy and reliability. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 64 | Earthing busbar size is inadequate. | Size of the earth busbar must be determined based on the main earthing cable, adhering to standards like BNBC (Bangladesh National Building Code) or designed using the Adiabatic method. This ensures adequate capacity to handle fault currents safely. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 65 | Wiring or extensions connecting equipment/devices are laid on floors without protection. | Run the cable connections to machines/equipment through trenches covered with checkered plates or within rigid conduits/cable trays and supports to prevent external damage. | In Progress | Jul 6 2025 | RSC does not accept the time extension mentioned by the factory without any proper explanation and expects the issue to be closed as per recommendation within the given timeline. On 24/11/2025: Not corrected. No progress has been observed. RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 66 | New Finding: Earth pits/earthing lead/earthing conductor are not identifiable. | Each earth pits/earthing lead/earthing conductor shall be properly constructed and marked for periodic maintenance. | In Progress | Jan 24 2026 | RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 67 | New Finding: Circuit breaker is installed without any enclosure. | Each circuit breaker must be enclosed by proper type material. the material must not be more than 18 SWG graded. | In Progress | Dec 24 2025 | RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 68 | New Finding: Substation room has inadequate ventilation. | Adequate ventilation must be maintained in sub-station room. Cross/forced ventilation must be ensured. | In Progress | Feb 24 2026 | RPO Comments on 23-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 3 Months | In Progress
Follow Up Inspection |  | 69 | New Finding: Exhaust fan body and fan blade enclosure are not equipped with earth connection. | Exhaust fan frame and its enclosure in the production area/s shall be connected to earth. | In Progress | Jan 24 2026 | RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 70 | New Finding: Earth lead cable/Earth Continuity Conductor size is not available. | Earth lead cable/ Earth Continuity Conductor (ECC) shall be determined according to BNBC or Adiabatic method (considering CB's response time, fault current & type of earth conductor other factors). | In Progress | Jan 24 2026 | RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 71 | New Finding: Exposed terminal joint or unsafe wiring on outer surface of panel board. | All unsafe wiring shall be removed. Cable terminal joint using busbar shall be done within enclosure with proper earthing. | In Progress | Jan 24 2026 | RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 72 | New Finding: Electrical distribution board/panels are adjacent to water source. | Electrical distribution board/panels must not be installed within 2.5 meter of any water source. For unavoidable cases, use a panel with a high Ingress Protection (IP) rating, IP55 or higher, to protect against water ingress and moisture. Additionally, ensure all conduit entries and cable penetrations are properly sealed to prevent water ingress. | In Progress | Jan 24 2026 | RPO Comments on 23-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress

## Boiler
Date
03-May-2026 | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address
Date of Inspection
Finance Plan Agreed