## Structural
Date
31-Mar-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | M.M. Knitwear Ltd., Ambagh Road, Konabari, Nilnagar, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-12-14
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Verify concrete strengths for all internal columns which are 380 x 380 structural dimension (brick aggregate) | Storage areas (minor area) to be reduced in loading to 2 boxes high on any level (1.2metre max high) | Done | May 17 2015 | On 04/10/2015: During our inspection, we found that height of boxes near 6 feet (1.82m) where as per initial inspection report they should maintain the boxes within 4 feet (1.2m). Factory management are advised to follow the initial inspection report. On 06/11/2017: This issue was covered in DEA. Factory authority performed DEA and accepted by ACCORD on 12nd July,2017. During inspection, loading was observed within accepted load plan. On 10/06/2018: This issue has been corrected from previous inspection. During inspection, loading was observed within the allowable safe load limit (20 psf) as per accepted load plan. On 24/09/2018: Corrected in previous follow up inspection. During inspection loading was found below 42 psf. On 11-Feb-2020: Corrected from previous follow up inspection. During inspection loading was found below 42 psf. On 12-Jan-2021: Corrected from previous follow up inspection. DEA was accepted by ACCORD on 12-July-2017 for B-1. During inspection live load was found as per accepted load plan (42 psf) at all floor level. On 03-Nov-2022: This issue was corrected in previous follow-up inspection. Load plan(42 psf) was found posted. Loading was found below 42 psf. On 18-Jun-2025: Corrected previously. During inspection, floor load was found within allowable limit (42 psf) as per accepted floor load paln. | Immediate-Now | Corrected
Initial Inspection |  | 2 | Verify concrete strengths for all internal columns which are 380 x 380 structural dimension (brick aggregate) | Factory Engineer to review design, loads and columns stresses in area identified above. | Done | Jul 31 2015 | On 04/10/2015: Review design is on going as part of DEA. During our inspection, factory management showed some documents of DEA agreement with the consultancy firm. Factory management have ensured us that they will submit DEA within 15 October 2015. On 06/11/2017: This issue was covered in DEA. Factory authority performed DEA and accepted by ACCORD on 12nd July,2017. On 10/06/2018: This issue has been corrected from previous inspection. Factory authority has performed DEA and got acceptance from ACCORD on 12nd July,2017. On 24/09/2018: Corrected in previous follow up inspection. Factory authority got acceptance from ACCORD on 12nd July,2017. On 11-Feb-2020: Corrected from previous follow up inspection. DEA was accepted by ACCORD on 12-July-2017 for B-1. On 12-Jan-2021: Corrected from previous follow up inspection. DEA for B-1 was reviewed and accepted from Accord on 12-July-2017. On 03-Nov-2022: This issue was corrected in previous follow-up inspection. DEA was accepted by ACCORD on 12-July-2017 for B-1. On 18-Jun-2025: Corrected previously. | Immediate-Now | Corrected
Initial Inspection |  | 3 | Verify concrete strengths for all internal columns which are 380 x 380 structural dimension (brick aggregate) | Verify insitu concrete stresses either by cores or existing cylinder strength data for internal columns. Minimum Core size 100mm diameter | Done | Jul 31 2015 | On 04/10/2015: Factory consultant has taken several cores to verify insitu concrete strength as part of DEA. On 06/11/2017: Core test was done as part of DEA. Factory authority performed DEA and accepted by ACCORD on 12nd July,2017. During inspection, nos of core was not matched with core layout. Factory is required to clarify this issue. On 10/06/2018: Factory did the DEA and got acceptance from ACCORD on 12nd July,2017. Core test was done as part of DEA. During inspection, nos of core found matched with core layout plan. On 24/09/2018: Corrected in previous follow up inspection. During inspection original core test report were kept onsite. On 11-Feb-2020: Corrected from previous follow up inspection. Original core test report was found on site during inspection. On 12-Jan-2021: Corrected from previous follow up inspection. On 03-Nov-2022: This issue was corrected in previous follow-up inspection. Cores were taken as a part of DEA. On 18-Jun-2025: Corrected previously. | Immediate-Now | Corrected
Initial Inspection |  | 4 | Verify concrete strengths for all internal columns which are 380 x 380 structural dimension (brick aggregate) | A Detail Engineering Assessment of Factory to be commenced, see attached Scope | Done | Jul 31 2015 | On 04/10/2015: DEA is on going. Factory management have ensured us that they will submit DEA within 15 October 2015. On 06/11/2017: Factory authority performed DEA and accepted by ACCORD on 12nd July,2017. On 10/06/2018: This issue has been corrected from previous inspection. On 24/09/2018: Corrected in previous follow up inspection. Factory authority got acceptance from ACCORD on 12nd July,2017. On 11-Feb-2020: Corrected from previous follow up inspection. DEA was accepted by ACCORD on 12-July-2017 for B-1. On 12-Jan-2021: Corrected from previous follow up inspection. DEA for B-1 was reviewed and accepted from Accord on 12-July-2017. On 03-Nov-2022: This issue was corrected in previous follow-up inspection. DEA was accepted by ACCORD on 12-July-2017 for B-1. On 18-Jun-2025: Corrected previously. | Immediate-Now | Corrected
Initial Inspection |  | 5 | Verify concrete strengths for all internal columns which are 380 x 380 structural dimension (brick aggregate) | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | Done | Jun 21 2015 | On 04/10/2015: Creation of Load plan is on going as part of DEA. They will submit load plan with DEA within 15 October 2015. On 06/11/2017: Load plan was produced as part of DEA and DEA accepted by ACCORD. During inspection, load plan was found posted in each floor. Factory is required to post final load plan after completion of remediation works. On 10/06/2018: Load plan has been prepared along with DEA report which was accepted by Accord on 12nd July,2017. During inspection, loading was not within the safe load limit (20 psf) as per accepted load plan. Load plan was found posted in each floor. Factory is required to post final load plan after completion of remediation works. On 24/09/2018: Load plan had been prepared as a part of DEA. Factory authority got acceptance from ACCORD on 12nd July,2017. Load plan was found posted to each floor but loading was found greater than 42 psf in some storage area. Height marking was not seen also. In addition, foundation drawing didn't match with onsite retrofitting condition. So factory is required to submit updated drawing with analysis file to ACCORD. On 11-Feb-2020: Corrected from previous follow up inspection. Load plan was found posted on each floor. On 12-Jan-2021: Corrected from previous follow up inspection. Load plan had been produced and accepted as a part of DEA. During inspection accepted load plan was found posted at every and live load was found below the allowable limit (42 psf). On 03-Nov-2022: This issue was corrected in previous follow-up inspection. Load plan(42 psf) was found posted. Loading was found below 42 psf. On 18-Jun-2025: Corrected previously. During inspection, floor load was found within allowable limit (42 psf) as per accepted floor load paln. | 6 Weeks | Corrected
Initial Inspection |  | 6 | Verify concrete strengths for all internal columns which are 380 x 380 structural dimension (brick aggregate) | Detail Engineering Assessment to be completed | Done | Jun 21 2015 | On 04/10/2015: DEA is on going. Factory management have ensured us that they will submit DEA within 15 October 2015. On 06/11/2017: Factory authority performed DEA and accepted by ACCORD on 12nd July,2017. Factory is required to complete the remediation works as per accepted DEA within given timeline. On 10/06/2018: Factory authority performed DEA and get acceptance from ACCORD on 12nd July,2017. Factory is required to complete all the remediation works as per approved DEA within the given timeline. On 24/09/2018: Factory authority performed DEA and get acceptance from ACCORD on 12nd July,2017. Factory is required to complete all the remediation works as per approved DEA. However, foundation drawing didn't match with onsite retrofitting condition. So factory is required to submit updated drawing with analysis file to ACCORD. On 11-Feb-2020: Corrected from previous follow up inspection. DEA was accepted by ACCORD on 12-July-2017 for B-1. All retrofitting works were completed. On 12-Jan-2021: Corrected from previous follow up inspection. DEA for B-1 was reviewed and accepted from Accord on 12-July-2017. Factory had completed all retrofitting works as per accepted drawing. On 03-Nov-2022: This issue was corrected in previous follow-up inspection. DEA was accepted by ACCORD on 12-July-2017 for B-1. Retrofitting was completed as per accepted DEA. On 18-Jun-2025: Corrected previously. | 6 Weeks | Corrected
Initial Inspection |  | 7 | Verify concrete strengths for all internal columns which are 380 x 380 structural dimension (brick aggregate) | Continue to implement load plan | Done | Nov 6 2015 | On 04/10/2015: Factory management didn't get the load plan yet. They are advised to implement load plan immediately. On 06/11/2017: Load plan was produced as part of DEA and DEA accepted by ACCORD. During inspection, load plan was found posted in each floor. Factory is required to post final load plan after completion of remediation works. On 10/06/2018: Load plan has been prepared along with DEA report which was accepted by Accord on 12nd July,2017. During inspection, loading was not within the safe load limit (20 psf) as per accepted load plan. Load plan was found posted in each floor. Factory is required to post final load plan after completion of remediation works. On 24/09/2018: Load plan had been prepared as a part of DEA. Factory authority got acceptance from ACCORD on 12nd July,2017. Load plan was found posted to each floor but loading was found greater than 42 psf in some storage area. Height marking was not seen also. In addition, foundation drawing didn't match with onsite retrofitting condition. So factory is required to submit updated drawing with analysis file to ACCORD. On 11-Feb-2020: Corrected from previous follow up inspection. During inspection the load was found below the accepted load (42psf). On 12-Jan-2021: Corrected from previous follow up inspection. During inspection accepted load plan was found posted at every and live load was found below the allowable limit (42 psf). On 03-Nov-2022: This issue was corrected in previous follow-up inspection. Load plan(42 psf) was found posted. Loading was found below 42 psf. On 18-Jun-2025: Corrected previously. During inspection, floor load was found within allowable limit (42 psf) as per accepted floor load paln. | 6 Months | Corrected
Initial Inspection |  | 8 | Water damage and risk of corrosion from roof slab | Engineer to inspect water damaged structure including the exterior and propose a suitable repair. Roof drainage system/water proofing to be installed | Done | Nov 6 2015 | 04/10/2015: Factory management are advised to take immediate action regarding the water damaged problem. They are also advised to install water proofing material on the roof top. On 06/11/2017: Factory authority is required to construct water proofing layer in rest of the area and necessary steps to remove dampness. On 10/06/2018: Factory is required to provide water proofing layer and take necessary steps to avoid dampness. On 24/09/2018: During inspection water proofing layer installation work was found ongoing but not completed. On 11-Feb-2020: Corrected from previous follow up inspection. During inspection water proofing layer was found completed. On 12-Jan-2021: Corrected from previous follow up inspection. Factory has improved the drainage system on roof slab. During inspection water proofing was found on roof slab and no water ponding was visible. On 03-Nov-2022: This issue was corrected in previous follow-up inspection. No signage of water damage was observed. Drainage system has been improved. On 18-Jun-2025: Corrected previously. | 6 Months | Corrected
Initial Inspection |  | 9 | Load management –design loads from engineer | Design check all columns, beams and slabs. Create loading plans and heights to match actual structural code capacity. | Done | Jun 21 2015 | On 04/10/2015: Design check of all columns, beams, slabs, & creation of load plan are on going as part of DEA. Factory management has ensured us that they will submit DEA within 15 October 2015. On 06/11/2017: This issue has covered in DEA. Factory authority performed DEA and accepted by ACCORD on 2nd December 2016. During inspection, this was observed that factory authority completed retrofitting works and posted final load plan on each floor. On 10/06/2018: This issue has been corrected from previous inspection. On 24/09/2018: Corrected in previous follow up inspection. Factory authority got acceptance from ACCORD on 2nd December 2016. On 11-Feb-2020: Corrected from previous follow up inspection. On 12-Jan-2021: Corrected previously. DEA of B-2 had been accepted from ACCORD on 2nd December 2016. Retrofitting works have been completed. During inspection load plans were posted on floors and Load height marking was available. Loading was observed within load plan limit(42psf). On 03-Nov-2022: This issue was corrected in previous follow-up inspection. Load restriction height marking was observed. On 18-Jun-2025: Corrected previously. During inspection, floor load was found within allowable limit (42 psf) as per accepted floor load paln. | 6 Weeks | Corrected
Initial Inspection |  | 10 | Drawings do not match the as built condition Assess double storey height columns at ground floor for stability | Design check all columns, beams and slabs. Produce As-Built drawings showing actual conditions. | Done | Jun 21 2015 | On 04/10/2015:This portion will be covered in DEA. On 06/11/2017: As built drawing was produced as part of DEA. Factory performed DEA and accepted by ACCORD on 11th September 2017. On 10/06/2018: This issue has been corrected from previous inspection. During inspection approved As built drawing found in factory. On 24/09/2018: Corrected in previous follow up inspection. Factory authority got acceptance from ACCORD on 11th September 2017. On 11-Feb-2020: Corrected in previous follow up inspection. On 12-Jan-2021: Corrected previously. DEA of B-3 was accepted by ACCORD on 11th September 2017. On 03-Nov-2022: This issue was corrected in previous follow-up inspection On 18-Jun-2025: Corrected previously. | 6 Weeks | Corrected
Initial Inspection |  | 11 | Verify concrete strengths for small internal columns which are 320 x 470 structural dimension (brick aggregate) | Storage (minor area) on Level 2, 3 and 5 in area indicated on following page to be reduced in loading to 1.5m high. | Done | May 17 2015 | On 04/10/2015: During our inspection, we found that height of boxes near 5.5 feet on level 5 (1.67m) where as per initial inspection report they should maintain the boxes within 4.92 feet (1.5m). Factory management are advised to follow the initial inspection report. On 06/11/2017: During inspection, loading was observed within allowable limit. On 10/06/2018: This issue has been corrected from previous inspection. During inspection, loading was observed within the allowable load limit (42 psf) as per accepted load plan. On 24/09/2018: Corrected in previous follow up inspection. During inspection loading was found below 42 psf. On 11-Feb-2020: Corrected from previous follow up inspection. On 12-Jan-2021: Corrected previously. Load plans and load height markings were present during inspection. Loading was observed within load plan limit ( 42 psf). On 03-Nov-2022: This issue was corrected in previous follow-up inspection. Load plan(42 psf) was posted. loading was found within 42 psf. On 18-Jun-2025: Corrected previously. During inspection, floor load was found within allowable limit (42 psf) as per accepted floor load paln. | Immediate-Now | Corrected
Initial Inspection |  | 12 | Verify concrete strengths for small internal columns which are 320 x 470 structural dimension (brick aggregate) | Factory Engineer to review design, loads and columns stresses in area identified above. | Done | Jul 31 2015 | 04/10/2017: Review design is on going as part of DEA. During our inspection, factory management showed some documents of DEA agreement with the consultancy firm. Factory management have ensured us that they will submit DEA within 15 October 2015. 06/11/2017: This issue was covered in DEA. Factory performed DEA and accepted by ACCORD on 11st September 2017. On 10/06/2018: This issue has been corrected from previous inspection. Factory authority has performed DEA and got acceptance from ACCORD on 11th September,2017. On 24/09/2018: Corrected in previous follow up inspection. Factory authority got acceptance from ACCORD on 11th September,2017. On 11-Feb-2020: Corrected from previous follow up inspection. On 12-Jan-2021: Corrected previously. DEA of B-3 was accepted from ACCORD on 11th September 2017. On 03-Nov-2022: This issue was corrected in previous follow-up inspection. DEA was accepted by ACCORD on 11th September,2017. On 18-Jun-2025: Corrected previously. | Immediate-Now | Corrected
Initial Inspection |  | 13 | Verify concrete strengths for small internal columns which are 320 x 470 structural dimension (brick aggregate) | Verify insitu concrete stresses either by cores or existing cylinder strength data for internal columns.Minimum Core sizes 100mm | Done | Jul 31 2015 | 04/10/2015: Factory consultant has taken several cores to verify insitu concrete strength as part of DEA. 06/11/2017: Core test was done as part of DEA. Factory performed DEA and accepted by ACCORD on 11st September 2017. On 10/06/2018: This issue has been corrected from previous inspection. During inspection, nos of core found matched with core layout plan. On 24/09/2018: Corrected in previous follow up inspection. During inspection original core test report were kept onsite. On 11-Feb-2020: Corrected from previous follow up inspection. Original core test report was found on site during inspection. On 12-Jan-2021: Corrected previously. This issue has been covered in DEA which got acceptance from ACCORD on 11th September 2017. On 03-Nov-2022: This issue was corrected in previous follow-up inspection. Cores were taken as a part of DEA. DEA was accepted by ACCORD. On 18-Jun-2025: Corrected previously. | Immediate-Now | Corrected
Initial Inspection |  | 14 | Verify concrete strengths for small internal columns which are 320 x 470 structural dimension (brick aggregate) | A Detail Engineering Assessment of Factory to be commenced, see attached Scope | Done | Jul 31 2015 | On 04/10/2015: DEA is on going. Factory management have ensured us that they will submit DEA within 15 October 2015. On 06/11/2017: Factory has performed DEA and accepted by ACCORD on 11st September 2017. On 10/06/2018: This issue has been corrected from previous inspection. On 24/09/2018: Corrected in previous follow up inspection. Factory authority got acceptance from ACCORD on 11th September 2017. On 11-Feb-2020: Corrected from previous follow up inspection. On 12-Jan-2021: Corrected previously. DEA of the factory has been accepted from ACCORD on 11th September 2017. Retrofitting works have been completed. On 03-Nov-2022: This issue was corrected in previous follow-up inspection. DEA was accepted by ACCORD on 11-Sep-2017. On 18-Jun-2025: Corrected previously. | Immediate-Now | Corrected
Initial Inspection |  | 15 | Verify concrete strengths for small internal columns which are 320 x 470 structural dimension (brick aggregate) | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | Done | Jun 21 2015 | 04/10/2017: Creation of Load plan is on going as part of DEA. They will submit load plan with DEA within 15 October 2015. 06/11/2017: Load plan produced as part of DEA. Factory performed DEA and accepted by ACCORD on 11st September 2017. During inspection, Loading was observed below accepted load plan. Factory is required to posted final load plan after completion of remedial works. On 10/06/2018: Load plan has been prepared along with DEA report which was accepted by Accord on 11th September,2017. During inspection, loading was observed within the allowable load limit (42 psf) as per accepted load plan. Load plan was found posted in each floor. Factory is required to post final load plan after completion of remediation works. On 24/09/2018: Load plan had been prepared as a part of DEA. Factory authority got acceptance from ACCORD on 11th September,2017. Load plan was found posted to each floor and loading was found below 42 psf. During retrofitting verification inspection some mismatch were found in between existing condition & accepted retrofitting drawing. So, factory is required to submit revised DEA to Accord. On 11-Feb-2020: Load plan was produced as part of DEA. DEA was accepted by ACCORD on 12-July-2017 & re-accepted on 23-Dec-2019. Load plan (42 psf) was found posted on each floor. On 12-Jan-2021: Corrected previously. Load plans and load height markings were present during inspection. Loading was observed within load plan limit ( 42 psf). On 03-Nov-2022: This issue was corrected in previous follow-up inspection. Load plan(42 psf) was posted. loading was found within 42 psf. On 18-Jun-2025: Corrected previously. During inspection, floor load was found within allowable limit (42 psf) as per accepted floor load paln. | 6 Weeks | Corrected
Initial Inspection |  | 16 | Verify concrete strengths for small internal columns which are 320 x 470 structural dimension (brick aggregate) | Detail Engineering Assessment to be completed | Done | Jun 21 2015 | 04/10/2015: DEA is on going. Factory management have ensured us that they will submit DEA within 15 October 2015. 06/11/2017: Factory performed DEA and accepted by ACCORD on 11st September 2017. Factory is required to complete the remediation works as per accepted DEA within given timeline. On 10/06/2018: Factory authority performed DEA and get acceptance from ACCORD on 11th September,2017. Factory is required to complete all the remediation works as per approved DEA within the given timeline. On 24/09/2018: Factory authority got acceptance from ACCORD on 11th September,2017. During retrofitting verification inspection some mismatch were found in between existing condition & accepted retrofitting drawing. So, factory is required to submit revised DEA to Accord. On 11-Feb-2020: All types of retrofitting works have been completed by factory management at B-3 as per accepted DEA. On 12-Jan-2021: Corrected previously. DEA of the factory has been accepted from ACCORD on 11th September 2017. Retrofitting works have been completed On 03-Nov-2022: This issue was corrected in previous follow-up inspection. DEA was accepted by ACCORD on 11-Sep-2017 for B-3. Retrofitting was completed as per accepted DEA. On 18-Jun-2025: Corrected previously. | 6 Weeks | Corrected
Initial Inspection |  | 17 | Verify concrete strengths for small internal columns which are 320 x 470 structural dimension (brick aggregate) | Continue to implement load plan | We have already maintaing as per load plan. | Nov 6 2015 | 04/10/2015: Factory management didn't get the load plan yet. They are advised to implement load plan immediately. 06/11/2017: Load plan was produced as part of DEA. Factory performed DEA and accepted by ACCORD on 11st September 2017. During inspection, load plan was found posted in each floor and loading was observed below accepted load plan. Factory is required to posted final load plan after completion of remedial works. On 10/06/2018: Load plan has been prepared along with DEA report which was accepted by Accord on 11th September,2017. During inspection, loading was observed within the allowable load limit (42 psf) as per accepted load plan. Load plan was found posted in each floor. Factory is required to post final load plan after completion of remediation works. On 24/09/2018: Load plan had been prepared as a part of DEA. Factory authority got acceptance from ACCORD on 11th September,2017. Load plan was found posted to each floor and loading was found below 42 psf. During retrofitting verification inspection some mismatch were found in between existing condition & accepted retrofitting drawing. So, factory is required to submit revised DEA to Accord. On 11-Feb-2020: During inspection load plan (42 psf) was found posted, but no load height mark was observed. Uncontrolled loading in Building-2 & Building-3 was found during inspection. Factory is required to provide load height mark on each floor & to maintain the loading limit below the accepted load (42 psf). On 12-Jan-2021: During inspection, Load plans and load height markings were present. Loads were kept below load height mark and loading was observed within load plan limit ( 42 psf). On 03-Nov-2022: This issue was corrected in previous follow-up inspection. Load plan(42 psf) was posted. loading was found within 42 psf. On 18-Jun-2025: Corrected previously. During inspection, floor load was found within allowable limit (42 psf) as per accepted floor load paln. | 6 Months | Corrected
Initial Inspection |  | 18 | Check the structural capacity of modified roof elements (trusses/purlins) and lateral stability of the roof to ground level | Design check modified trusses and purlins and check lateral stability of the roof down to ground level. | Correcting based on comment from after retrofitting EA. | Jun 21 2015 | 04/10/2015: This portion will be covered in DEA. 06/11/2017: Design report of shed submitted to ACCORD along with DEA and accepted by ACCORD. During inspection, remedial works were observed going on. On 10/06/2018: Design report of sheds submitted to ACCORD and accepted by ACCORD. Factory is required to complete all the remediation works as per approval within the given timeline. On 24/09/2018: Factory authority got acceptance from ACCORD. During retrofitting verification inspection some mismatch were found in between existing condition & accepted retrofitting drawing. So, factory is required to submit revised DEA to Accord. On 11-Feb-2020: During inspection the retrofitting works found completed. On 12-Jan-2021: Corrected from previous follow up inspection. Engineering Assessment (EA) of this sheds was re-accepted from Accord on 23th Dec 2019 from Accord. Factory has completed all retrofitting works as per accepted drawing. On 03-Nov-2022: This issue was corrected in previous follow-up inspection. As per accepted EA, retrofitting was completed for the sheds. On 18-Jun-2025: Corrected previously. | 6 Weeks | Corrected
Follow Up Inspection |  | 19 | New Findings-1: Above loading unloading area mezzanine floor was found connected in between unit-1 & 2. | Factory Engineer to review design check for column, beam and slab. Create loading plans and heights to match actual structural code capacity. | Corrected. We have already removed the shed | Jan 10 2019 | On 24/09/2018: During inspection above loading unloading area mezzanine floor was found connected in between unit-1 & 2. Factory Engineer to review design check for column, beam and slab. Create loading plans and heights to match actual structural code capacity. On 11-Feb-2020: Factory has already demolished the mezzanine floor above the loading unloading area. On 12-Jan-2021: Corrected from previous follow up inspection. The Mezzanine floor above loading unloading area has been demolished. On 03-Nov-2022: This issue was corrected in previous follow-up inspection. The Mezzanine floor above loading-unloading area was demolished. On 18-Jun-2025: Corrected previously. The Mezzanine floor above loading-unloading area was demolished. | 6 Weeks | Corrected
Follow Up Inspection |  | 20 | New Findings-2: New non-engineered steel structure was found during inspection. | Factory engineer is required to provide analysis file and as built drawing for the non-engineered new steel structure. | Corrected. We have already removed the shed | Jan 10 2019 | On 24/09/2018: During inspection a non-engineered steel structure was found. Factory engineer is required to provide analysis file and as built drawing for the non-engineered new steel structure. On 11-Feb-2020: Factory has demolished the non-engineered shed. On 12-Jan-2021: Corrected from previous follow up inspection. The non engineered shed has been demolished. On 03-Nov-2022: This issue was corrected in previous follow-up inspection. Factory demolished the non-engineered shed. On 18-Jun-2025: Corrected previously. | 6 Weeks | Corrected

## Fire
Date
31-Mar-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | M.M. Knitwear Ltd., Ambagh Road, Konabari, Nilnagar, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2015-02-06
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | An electrical panel and two pumps were located under the northwest exit stair enclosure on the ground floor. | Remove and re-locate the electrical panel and pumps from the exit stair enclosure. | Corrected | Mar 28 2016 | On 25/08/16: Corrected On 03/11/16: Corrected On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected. On 07-11-2019: Corrected. None found. On 26-10-2021: Corrected. None found. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 2 | Both exits from the ground floor embroidery room discharge to the finished fabrics store. Exit access corridors are not provided with 1 hr. fire resistance rating or approved NFPA 13 sprinkler system. | Provide exit access corridors from the ground floor embroidery room to exterior exit discharge, with 1 hr. fire resistance rating or approved NFPA 13 sprinkler system. | Corrected | Jul 24 2016 | On 25/08/16: In progress. On 03/11/16: Sprinkler system installation work has been started for unit-1. On 9/1/2017: No action has been taken yet. On 6/04/2017: In progress. On 25/07/2017: Corrected. The factory has informed that they have removed the embroidery section from the mentioned place to another factory building. On 6-11-2017: Corrected. Embroidery section has been removed from here. On 24.04.2018: Corrected as per previous follow-up inspections. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected as per previous follow-up inspections. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 3 | The ground floor air compressors in Shed-1 were not separated by fire-rated construction. In one location, the air compressors were open to the factor floor and unseparated from the adjacently located generators. In the other location, the air compressors were not separated due to openings and non-rated doors. | Separate the air compressors by a minimum 1-hr fire-rated construction for non-high rise, and 2-hr fire rated construction for high rise. Seal and/or protect all openings to maintain the required fire separations. When located to the exterior of a building, 3m (10 ft.) separation is required. Provide proper ventilation and consult a qualified engineer. | Corrected | May 24 2016 | On 25/08/16: Corrected On 03/11/16: Corrected On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected as per previous follow-up inspections. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 4 | The fourth floor boiler room in Unit-1 was not separated by fire-rated construction due to openings, a non-rated door and penetrations. The ground floor boilers in Shed-1 were not separated by fire-rated construction and open to the factory floor. The boilers were not separated from the adjacently located generators. | Separate the boilers by a minimum 1-hr fire-rated construction for non-high rise, and 2-hr fire rated construction for high rise. Seal and/or protect all openings to maintain the required fire separations. When located to the exterior of a building, 3m (10 ft.) separation is required. Provide proper ventilation and consult a qualified engineer. | Corrected | May 24 2016 | On 6/04/2017: Corrected. On 25/07/2017: Corrected as per previous follow-ups. On 6-11-2017: Corrected. Note: Proper internal separation is required in between boilers and generator. On 24.04.2018: Corrected as per previous follow-up inspections. Note: Some parts of fire door were found missing during inspection. On 05.02.2019: Corrected as per previous follow up inspection. On 07-11-2019: Corrected as per previous follow-up. Factory shall maintain fire separation by sealing all unprotected openings as required. On 26-10-2021: Corrected. Boiler room has been removed from 4th floor. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 5 | Rooms used for combustible storage are not separated by fire rated construction. Specifically, the storage rooms adjacent to the east exit stair on the sixth, fifth, fourth and third floors, the finished goods area and accessory store on the first floor and the finished fabrics store on the ground floor. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. | Corrected | Jun 24 2016 | On 25/08/16: Corrected. Fire doors have been installed. On 03/11/16: Corrected On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 6 | Both exit stairs are unenclosed and not separated from work areas on the ground floor by fire-rated construction. | The exit stair enclosure shall be provided with a minimum 1-hr fire resistance rating for buildings with 3 or fewer stories and a minimum of 2- hr fire resistance rating for buildings 4 or more stories. | Corrected | Jun 24 2016 | On 25/08/16: Corrected On 03/11/2016: Corrected as per last follow up. On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected as per previous follow-ups. On 6-11-2017: Corrected as per previous follow-up. On 24.04.2018: Corrected as per previous follow-up inspections. On 05.02.2019: Corrected. On 07-11-2019: Corrected. Factory shall maintain doors such that they are functional at all times. On 26-10-2021: Corrected as per previous follow-up inspections. On 03/11/2022: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 7 | The exit stairs are not separated from work areas and other spaces on each floor by fire rated construction. | Provide minimum 1-hr rated doors for buildings with 3 or fewer stories and 1.5-hr fire rated doors for buildings that are 4 or more stories. Seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. Once fire doors are installed, every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets ACCORD standard 6.8.3.1. | Done. Fire door has been installed. | Jun 24 2016 | On 6/04/2017: Issue has been reopened. Door coordinator is missing in some places and vision glass on fire door has been broken at different places. On 25/07/2017: Fire door accessories (vision panel, door co-ordinator, door closer, push bar, hinges) were found missing in different fire doors at the time of inspection. Moreover, unprotected opening was observed at ground floor exit stair enclosure (newly constructed office area) in Unit-1. The factory shall prove proper fire rating of total door set. On 6-11-2017: Comment is as per 8th follow-up. On 24.04.2018: Not corrected. Fire doors were found being repaired without proper authentication, unsealed penetrations were found and the gap between the bottom of fire door & floor level was found more than standard. On 05.02.2019: Unsealed penetration has been found and the interfacing of fire doors shall be checked during T & Cx. On 07-11-2019: Factory shall maintain fire doors such that they are functional at all times. If doors are to stay open, interfacing shall be done properly with FACP. Factory shall maintain the fire rating of the fire doors by sealing any gaps or openings around the doors. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. Note: Re-entry sign shall be provided as per inspection recommendation. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 8 | An unsealed penetration (hydrant piping) was located in the northwest exit stair enclosure on the first floor. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | Corrected | Jun 24 2016 | On 25/08/16: Corrected On 03/11/16: Corrected. Some penetrations observed as there sprinkler system installation work is going on. On 9/1/2017: In progress. Lots of penetration has been found for sprinkler work. On 6/04/2017: Corrected. On 25/07/2017: Corrected as per previous follow-up. Note: Sprinkler system installation work is going on. On 05.02.2019: Corrected as per previous follow up inspection. On 07-11-2019: Corrected. On 26-10-2021: Corrected as per previous follow-up inspections. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 9 | The storage rooms on the sixth, fifth, fourth and third floors, all discharge directly into the east exit stair enclosure. The finished goods area on the first floor discharges directly into both exit stair enclosures and the accessory store on the first floor discharges directly into the northwest exit stair enclosure. | Openings from exit enclosure to storage rooms shall be provided with a vestibule with fire rated construction and openings. Provide a 1.5-hr. fire rated door on the exit stair side and a 1-hr. fire rated door on the storage room side. Ensure that the fire rating of the vestibule construction matches that of the exit stair enclosure. | Corrected | Jun 24 2016 | On 25/08/16: Corrected. On 03/11/16: Corrected. None of the store is directly connected with exit enclosure with fire separation. On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected as per previous follow-up. Issue is merged with finding no. 61. On 05.02.2019: Follow issue no. 61 On 07-11-2019: Refer to Issue #61 On 26-10-2021: Refer to Issue #61 On 03/11/2022: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 10 | Building did not have stair designation signs or occupant load signs. Emergency evacuation plans were provided in some locations, but not at all required locations. | Provide stair designation signs, occupant load signs and emergency evacuation plans at required locations. | Corrected | Mar 28 2016 | On 25/08/16: Corrected On 03/11/16: Corrected (Shall be upgraded regularly). On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 11 | Egress gates with locking features are provided at building exits and exit stairs. Not all doors were open and unlocked during the inspection, specifically the door from the first floor accessory store to the east exit stair. | Remove locking features from all egress gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101 and ACCORD standard 6.8.2. Ensure that the door to the east exit stair from the first floor accessory store is kept unlocked to avoid egress issues. | Corrected | Feb 28 2016 | On 25/08/16: Corrected On 03/11/16: Corrected, during inspection no non-compliant locking features found in any location along the means of egress for unit-1. On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. Removed. On 23-Oct-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 12 | Collapsible gates and sliding doors are provided at building exits and exit stairs. | Replace all sliding gates and collapsible doors along the means of egress with side hinged, swinging egress doors in accordance with ACCORD standard 6.8.1. | Corrected | Feb 28 2016 | On 25/08/16: Corrected On 03/11/16: Corrected, during inspection no non-compliant exit door found in any location along the means of egress for unit-1. On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. Replaced. On 23-Oct-25: Corrected. | 1 Month | Corrected
Initial Inspection |  | 13 | The width of an egress aisle on the second floor was less than 36-in. | Provide minimum aisle widths of 36-in. | Corrected | Mar 28 2016 | On 25/08/16: Corrected On 03/11/16: Corrected On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 14 | Handrails are not provided on both sides of each exit stair, on all floors. | Provide handrails on both sides of the exit stair. New handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in.) | Corrected | Mar 28 2016 | On 03/11/16: Corrected On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 15 | A single means of egress is provided from the second floor (third story) east office area, where a single exit is not permitted. | Ground or basement story is allowed a maximum of 50 occupants and 23 m (75ft) travel distance. The second story is allowed a maximum of 30 occupants and 23 m (75ft) travel distance. All other stories require a minimum of 2 egress exits. Provide additional means of egress. | Corrected | Jun 24 2016 | On 25/08/16: The mentioned building is now 7 storied. Only one floor (2nd) is currently using as office. So, secondary exit stair is required. On 03/11/16: No action has been taken yet. On 9/1/2017: Corrected. As per Accord standard 6.13.3 is corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected as per previous follow-up. On 6-11-2017: Corrected as per previous follow-up. On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected as per previous follow-up. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 16 | The fire alarm system is antiquated, not a listed system and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | Done. Alarm system is ACTIVE, wafting for T&C by ACCORD | Jun 24 2016 | On 25/08/16: Drawing has been reviewed. L/C has been done. Shipment date 30 August, 2016. On 03/11/16: Fire alarm system modification work as per the reviewed design has been started for unit-1. On 9/1/2017: Installation is going on. On 6/04/2017: Installation is going on. On 25/07/2017: Installation work is going on. On 6-11-2017: Interfacing work is not done. Overall T&Cx verification shall be done by Accord. On 24.04.2018: Design has been reviewed from Accord and installation is going on. On 05.02.2019: Fire alarm system shall comply NFPA-72. On 07-11-2019: Factory has informed that they have rectified all issues regarding their alarm system. The system shall be in compliance with NFPA 72. Accord will verify through Testing & Commissioning inspection. On 30/11/2021: T&CVI found that the fire alarm & detection system is required final verification on-site. See detailed T&CVI Report. On 17.01.2022: The system is approved on the Final Verification Inspection. On 03/11/2022: Corrected. On 05/04/2023: Corrected as per last FVI on 17/01/1022. On 23-Oct-25: Corrected. During inspection, fire alarm control panel was found normal with active condition. | Design within 4 months, install within 9 months | Corrected
Initial Inspection |  | 17 | The required no smoking signs are not present in the factory. | Smoking is prohibited in any garment factory building or separate storage building. Signs shall be posted in Bengali and English at all building entrances. If the factory creates a designated smoking area outside the building, information of these areas will be posted on the signs. | Corrected | Feb 28 2016 | On 25/08/16: Corrected. On 03/11/16: Corrected. On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 1 Month | Corrected
Initial Inspection |  | 18 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10. | Corrected | Feb 28 2016 | On 25/08/16: Corrected On 03/11/16: Corrected On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 19 | Inspection, testing and maintenance for the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with NFPA 72. | Corrected | Jun 24 2016 | On 25/08/16: Corrected. Factory is maintaining standard checklist for their existing system. On 03/11/16: Corrected but shall be upgraded the system after installation of compliant system. On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected as per previous follow-up. On 6-11-2017: Corrected as per previous follow-up. On 24.04.2018: Corrected as per previous follow-up inspections. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 20 | Inspection, testing and maintenance of the standpipe system is not in accordance with NFPA 14. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 14. | Corrected | Jul 24 2016 | On 03/11/16: Corrected On 9/1/2017: Corrected. Factory is maintaining as per Accord standard for their existing system. On 6/04/2017: Corrected. Factory is maintaining as per Accord standard for their existing system. On 25/07/2017: Corrected as per previous follow-up. On 6-11-2017: Corrected as per previous follow-up. On 24.04.2018: Corrected as per previous follow-up inspections. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 21 | Visible notification was not provided for the building in accordance with NFPA 72. | Provide visible notification for the building in accordance with NFPA 72. | Done. Alarm system is ACTIVE within visible notification, waiting for T&C by ACCORD | Jun 24 2016 | On 25/08/16: It is an integrated part of fire alarm system. On 03/11/16: It is an integrated part of fire alarm system. On 9/1/2017: Installation work is in progress. On 6/04/2017: Installation work is in progress. On 25/07/2017: It is an integrated part of fire alarm system. On 6-11-2017: T&Cx verification shall be done by Accord. On 24.04.2018: It is an integrated part of fire alarm system. On 05.02.2019: It is an integrated part of fire alarm system. On 07-11-2019: It is an integrated part of the fire alarm system. On 30-11-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 22 | Fire department connection is not provided. | Provide fire department connection in accordance with ACCORD standard 5.5.4. | Corrected | Apr 28 2016 | On 25/08/16: Corrected. On 03/11/16: Corrected however this is an integrated part of standpipe system. On 9/1/2017: Corrected. On 6/04/2017: Corrected however this is an integrated part of standpipe system. On 25/07/2017: Corrected as per previous follow-up. However, it is an integrated part of fire fighting system. On 6-11-2017: Corrected as per previous follow-up. On 24.04.2018: Corrected as per previous follow-up inspections. On 05.02.2019: Corrected. On 07-11-2019: It is an integrated part of the fire fighting system. On 26-10-2021: Follow the issue no-23. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 23 | The required standpipe system is not installed in accordance with the ACCORD standard. | Install a new standpipe system in accordance with ACCORD standard 5.4 and NFPA 14. A class III system shall be installed in buildings with the highest occupiable floor 10 m (33 ft.) above grade or more. A class I system shall be permitted in buildings protected throughout by an approved automatic sprinkler system. | Done. The standpipe system is active, waiting for T&C by ACCORD | Jul 24 2016 | On 25/08/16: Sprinkler system installation is on going. On 03/11/16: Partially Corrected. Hose system installation almost complete for unit-1 where sprinkler system installation is started. On 9/1/2017: Installation work is in progress. On 6/04/2017: Installation work is going on. On 25/07/2017: Installation work is going on. On 6-11-2017: T&Cx verification shall be done by Accord. On 24.04.2018: Design has been reviewed from Accord and installation is going on. On 05.02.2019: In progress. On 07-11-2019: The system shall be in compliance with NFPA 14 & 20. Accord will verify through Testing & Commissioning inspection. On 30/11/2021: T&CVI found that the standpipe system is required final verification on-site. See detailed T&CVI Report. On 17.01.2022: The system is approved on the Final Verification Inspection. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. During inspection, it was observed that fire pump sets were normal with active condition. | 6 Months | Corrected
Initial Inspection |  | 24 | Lighted exit signage was not provided along a path of egress from the first floor finished goods area to the accessory store. | Provide exit signs above all building exits to the exterior, all doors to the exit stairs and along all paths of travel where a change of direction is not obvious. | Corrected | Feb 28 2016 | On 25/08/16: Corrected. On 03/11/16: Corrected On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 1 Month | Corrected
Initial Inspection |  | 25 | Inspection, testing and maintenance for the emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | Corrected | Feb 28 2016 | On 25/08/16: Corrected. On 03/11/16: Corrected On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 26 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along all egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to supply adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and along exit discharge paths and a minimum 2.5 lux along exit access aisles. | Corrected | May 24 2016 | On 25/08/16: Corrected On 03/11/16: Corrected On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected as per previous follow-up. The factory shall ensure proper illumination for emergency lighting system. On 6-11-2017: Corrected as per previous follow-up. On 05.02.2019: Corrected. he factory shall ensure proper illumination for emergency lighting system On 07-11-2019: Corrected. Factory shall maintain illumination as per recommendation. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 27 | The second exit from the fourth floor office area and sample section pass through the finished goods storage room. An exit access corridor is not provided with 1 hr. fire resistance rating or approved NFPA 13 sprinkler system. | Provide an exit access corridor through the fourth floor finished goods storage room for each exit access point, with 1 hr. Fire resistance rating or approved NFPA 13 sprinkler system. | Corrected | Jul 24 2016 | On 25/08/16: In progress. On 03/11/16: No action has been taken yet. On 9/1/2017: No action has been taken yet. On 6/04/2017: Corrected. Office area has been shifted from 4th floor. On 25/07/2017: Corrected as per previous follow-up. On 6-11-2017: Corrected as per 7th follow-up. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected as per previous follow-ups. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 28 | The ground floor air compressors in Shed-1 were not separated by fire-rated construction. In one location, the air compressors were open to the factor floor and unseparated from the adjacently located generators. In the other location, the air compressors were not separated due to openings and non-rated doors. | Separate the air compressors by a minimum 1-hr fire-rated construction for non-high rise and 2-hr fire rated construction for high rise. Seal and/or protect all openings to maintain the required fire separations. When located to the exterior of a building, 3m (10 ft.) separation is required. Provide proper ventilation and consult a qualified engineer. | Corrected | May 24 2016 | On 25/08/16: Corrected On 03/11/16: Corrected On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 24.04.2018: Corrected as per previous follow-up inspections. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected as per previous follow-up inspections. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 29 | The two (2) sixth floor boilers and one (1) second floor boiler in Unit-2 were not separated by fire-rated construction due to openings, a non-rated door and penetrations. The ground floor boilers in Shed-1 were not separated by fire-rated construction and open to the factory floor. The boilers were not separated from the adjacently located generators. | Separate the boilers by a minimum 1-hr fire-rated construction for non-high rise, and 2-hr fire rated construction for high rise. Seal and/or protect all openings to maintain the required fire separations. When located to the exterior of a building, 3m (10 ft.) separation is required. Provide proper ventilation and consult a qualified engineer. | Corrected | May 24 2016 | On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected as per previous follow-ups. On 6-11-2017: Corrected as per previous follow-up. On 24.04.2018: Corrected as per previous follow-up inspections. Note: Fire door was found held open by external force. On 05.02.2019: Corrected. On 18-11-2019: Corrected as per previous follow up. Unprotected opening has been found in boiler room. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected as per previous follow up. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 30 | Rooms used for combustible storage are not separated by fire rated construction. Specifically, the storage rooms on the eighth (cut panel stock) and fourth (finished goods godown) floors of Unit-2. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. | Corrected | Jun 24 2016 | On 25/08/16: Corrected. No store room has been found on 8th floor. On 4th floor, pile dimension area is maintaining. On 03/11/16: Corrected. No dedicated store room found in the noted location but available on 4th floor which is not fire separated with office area and raised as new finding. On 6/04/2017: Corrected. Storage room has been shifted to 4th floor. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected as per previous follow-ups. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 31 | The Unit-2, northwest and northeast exit stairs are unenclosed and not separated from work areas and other spaces by fire-rated construction on the mezzanine level and ground floor. The Unit-3, northwest and southeast exit stairs are unenclosed and not separated from work areas by fire-rated construction on the first and ground floors. | The exit stair enclosure shall be provided with a minimum 1-hr fire resistance rating for buildings with 3 or fewer stories and a minimum of 2- hr fire resistance rating for buildings 4 or more stories. | Done. Separation has been ensured by fire rated door. | Jun 24 2016 | On 25/07/2017: It was found same as it was before. Fire door has been found damaged in most of the places. On 6-11-2017: Proper closure and latching of fire doors are not anticipated. Missing accessories. On 24.04.2018: Not corrected. In some double leaf fire doors, one part was found held open by external forces. Some parts of fire door was found missing and door closure was found not working properly. On 05.02.2019: Not corrected yet. Interfacing shall be checked during T & Cx. On 18-11-2019: Fire door installation is almost completed. Few unprotected opening has been found. Interfacing shall be checked during T & C. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 32 | All exit stairs were not separated from work areas and other spaces on each floor by fire rated construction. | Provide minimum 1-hr rated doors for buildings with 3 or fewer stories and 1.5-hr fire rated doors for buildings that are 4 or more stories. Seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. Once fire doors are installed, every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets ACCORD standard 6.8.3.1. | Done. Separation has been ensured by fire rated door. | Jun 24 2016 | On 6-11-2017: Comment is as per 8th follow-up. On 24.04.2018: Not corrected. In some double leaf fire doors, one part was found held open by external forces. Some parts of fire door was found missing and door closure was found not working properly. On 05.02.2019: Interfacing of installed fire doors shall be checked during T & Cx. On 07-11-2019: Some doors were missing accessories such as vision panel etc. Panic bars were loose for some doors. Some doors did not seal properly. Factory shall maintain doors such that they are functional at all times. On 26-10-2021: Corrected based on the site observations. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 33 | An unsealed penetration (hydrant piping) was located in the Unit-2, northwest exit stair enclosure on the rooftop. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | Corrected | Jun 24 2016 | On 9/1/2017: Corrected. Still some penetrations observed during inspection. On 6/04/2017: Corrected. On 25/07/2017: Corrected as per previous follow-up. Note: Installation of sprinkler system is going on. On 05.02.2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected as per previous follow-ups. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 34 | The Unit-2, fourth floor finished goods storage room discharges directly to the northwest and northeast exit stair enclosures. | Openings from exit enclosure to storage rooms shall be provided with a vestibule with fire rated construction and openings. Provide a 1.5-hr. fire rated door on the exit stair side and a 1-hr. fire rated door on the storage room side. Ensure that the fire rating of the vestibule construction matches that of the exit stair enclosure. | Corrected | Jun 24 2016 | On 9/1/2017 :Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected as per previous follow-ups. Issue is merged with finding no. 61. On 05.02.2019: Follow issue no 61. On 07-11-2019: Refer to Issue# 61. On 26-10-2021: Refer to Issue# 61. On 03/11/2022: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 35 | Areas used for combustible storage open to the factory are not separated by fire rated construction. Specifically, these areas were located on the seventh, sixth and second floor of Unit-2, the fifth, fourth and second floor of Unit-3 and throughout the ground floor of all buildings. | Provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.45m (8ft.) and maximum area of 23m2 (250 ft2) - If sprinkler protected: maximum height of 3.66m (12ft.) and maximum area of 93m2 (305ft2) Separate areas of unenclosed combustible storage by a minimum clear distance of 3m (10ft.). | We have arrange storage area properly | Mar 28 2016 | On 6/04/2017: Issue has been reopened. On 25/07/2017: Not corrected yet. Defined storage area has not been found within limit. On 6-11-2017: Comment is as per 8th follow-up. On 24.04.2018: It was found same as last follow-up inspection. On 05.02.2019: Not corrected yet. On 07-11-2019: Huge stack of storage has been found during follow up inspection On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 36 | The industrial dryer and stentor machine in Shed -1 were not separated by fire-rated construction and open to the factory floor. | Separate the industrial dryer and stentor machine by a minimum 2-hr fire-rated construction. Seal and/or protect all openings to maintain the required fire separations. Provide proper ventilation and consult with a qualified engineer. | Corrected | Mar 28 2016 | On 03/11/16: Corrected On 9/1/2017 :Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected as per previous follow-up inspections. On 05.02.2019: Corrected as per previous follow up inspection. On 18-11-2019: Corrected as per previous follow up inspection. On 26-10-2021: Corrected as per previous follow up inspection. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 37 | Building did not have stair designation signs or occupant load signs. Emergency evacuation plans were provided in some locations, but not at all required locations. | Provide stair designation signs, occupant load signs and emergency evacuation plans at required locations. | Corrected | Mar 28 2016 | On 9/1/2017 :Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 38 | Egress doors and gates with locking features are provided at building exits, exit stairs, along egress routes and at exit discharge in various locations throughout all buildings. All doors and gates were open and unlocked during the inspection. | Remove locking features from all egress gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101 and ACCORD standard 6.8.2. | Corrected | Feb 28 2016 | On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 39 | The exit capacity of the Unit-2 mezzanine level (293), primarily used for dining, was not adequate for the reported maximum occupant load (500). | Reduce occupant load immediately to not more than available exit capacity (293). Provide additional exits in the future to increase exit capacity. | Corrected | Feb 28 2016 | On 9/1/2017 :Corrected. On 6/04/2017: Corrected. Dinning place has been shifted to building 4 & 6. On 25/07/2017: Corrected. Dining has been shifted to another location. On 6-11-2017: Corrected. On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 40 | Collapsible gates and sliding doors are provided at building exits, exit stairs, along egress routes and at exit discharge. | Replace all sliding gates and collapsible doors along the means of egress with side hinged, swinging egress doors in accordance with ACCORD standard 6.8.1. | Corrected | Feb 28 2016 | On 9/1/2017 :Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 1 Month | Corrected
Initial Inspection |  | 41 | The width of an egress aisle on the eighth floor of Unit-2 was less than 36-in. | Provide minimum aisle widths of 36-in. | Corrected | May 24 2016 | On 9/1/2017 :Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 42 | Handrails are not provided on both sides of each exit stair for Unit -2 and Unit-3. | Provide handrails on both sides of the exit stair. New handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in.) | Corrected | Mar 28 2016 | On 9/1/2017 :Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 43 | The Unit-2, northeast exit stair and Unit-3 northwest and southeast exit stairs discharge inside the building on the ground floor to production areas. After interior discharge, the egress path of the Unit -3 southeast exit stair currently passes through a hazardous materials / flammable liquid storage room that is reportedly owned by another factory. Based off observations, the Unit-3 northwest exit stair already has another, non fire resistive exit stair being constructed to the exterior of the building. | Provide sprinkler protection for discharge floor in accordance with NFPA 13. Modify stair to discharge directly outside or provide 2- hr fire-rated exit passageway leading directly outside (vestibules to separate any storage areas). After the new stair for the Unit-3 northwest exit stair is constructed, ensure that all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft., are sealed to provide a minimum 1-hr fire separation. | Corrected | Jul 24 2016 | On 6-11-2017: Partially corrected. One discharge path has been separated. But the other path is exposed to dying shed opening and substation area. On 24.04.2018: It was found same as last follow-up inspection. On 05.02.2019: Corrected as fire door has been installed and provide an safe exit. On 18-11-2019 : Corrected as per previous follow up. On 26-10-2021: Corrected as per previous follow up. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 6 Months | Corrected
Initial Inspection |  | 44 | The fire alarm system in all buildings is antiquated, not a listed system and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. The new fire alarm system should be interconnected between all three buildings. | Done. Alarm system is ACTIVE, wafting for T&C by ACCORD | Jun 24 2016 | On 6/04/2017: In progress. On 25/07/2017: Installation work is going on. On 6-11-2017: T&Cx verification shall be done by Accord. On 24.04.2018: Design has been reviewed from Accord and installation is going on. On 05.02.2019: Installed fire alarm system shall comply NFPA-72 and T & C VI shall be done by ACCORD. On 18-11-2019: Factory has informed that they have rectified all issues regarding their alarm system. The system shall be in compliance with NFPA 72. Accord will verify through Testing & Commissioning inspection On 30/11/2021: T&CVI found that the fire alarm & detection system is required final verification on-site. See detailed T&CVI Report. On 17.01.2022: The system is approved on the Final Verification Inspection. On 03/11/2022: Corrected. On 05/04/2023: Corrected as per last FVI. On 23-Oct-25: Corrected. | Design within 4 months, install within 9 months | Corrected
Initial Inspection |  | 45 | The required no smoking signs were not present in any of the factory buildings. | Smoking is prohibited in any garment factory building or separate storage building. Signs shall be posted in Bengali and English at all building entrances. If the factory creates a designated smoking area outside the building, information of these areas will be posted on the signs. | Corrected | Feb 28 2016 | On 9/1/2017 :Corrected. On 6/04/2017: Corrected On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected as per previous follow up inspection. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 1 Month | Corrected
Initial Inspection |  | 46 | Activation of the fire alarm system by a manual fire alarm station in Unit-2 and Unit-3 provides automatic occupant notification only for the respective building. In Shed-1, activation of the fire alarm system by a manual alarm station provides occupant notification only for occupants within audible range of the individual station. | Configure the new, addressable fire alarm system to initiate automatic occupant notification on all floor levels of all buildings to facilitate whole-building evacuation upon any manual fire alarm station activation. | Done. Alarm system is ACTIVE, wafting for T&C by ACCORD | Jun 24 2016 | On 25/08/16: It’s an integrated part of fire alarm system. On 03/11/16: It’s an integrated part of fire alarm system. On 9/1/2017 : It’s an integrated part of fire alarm system. On 6/04/2017: It’s an integrated part of fire alarm system. On 25/07/2017: It is an integrated part of fire alarm system. On 6-11-2017: T&Cx verification shall be done by Accord. On 24.04.2018: It is an integrated part of fire alarm system. On 05.02.2019: It is an integrated part of fire alarm system. On 18-11-2019: It’s an integrated part of fire alarm system. On 30-11-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 1 Month | Corrected
Initial Inspection |  | 47 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10. | Corrected | Apr 28 2016 | On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 48 | Inspection, testing and maintenance for the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with NFPA 72. | Corrected | Jun 24 2016 | On 6/04/2017: Corrected. On 25/07/2017: Corrected as per previous follow-up. On 6-11-2017: Corrected as per previous follow-up. On 24.04.2018: Corrected as per previous follow-up inspections. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 49 | Inspection, testing and maintenance of the standpipe system is not in accordance with NFPA 14. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 14. | Corrected | Jul 24 2016 | On 25/07/2017: Corrected as per previous follow-up. On 6-11-2017: Corrected as per previous follow-up. On 24.04.2018: Corrected as per previous follow-up inspections. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 50 | Visible notification was not provided for the all buildings in accordance with NFPA 72. | Provide visible notification for the building in accordance with NFPA 72. | Done. Alarm system is ACTIVE within visible notification, waiting for T&C by ACCORD | Jun 24 2016 | On 9/1/2017: It’s an integrated part of fire alarm system. On 6/04/2017: It’s an integrated part of fire alarm system. On 25/07/2017: It is an integrated part of fire alarm system. On 6-11-2017: T&Cx verification shall be done by Accord. On 24.04.2018: It is an integrated part of fire alarm system. On 05.02.2019: It is an integrated part of fire alarm system. On 18-11-2019: It’s an integrated part of fire alarm system. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 51 | Fire department connection is not provided. | Provide fire department connection in accordance with ACCORD standard 5.5.4. | Corrected | Apr 28 2016 | On 6/04/2017: Corrected, however it’s an integrated part of standpipe system. On 25/07/2017: Corrected as per previous follow-up. However, it is an integrated part of fire fighting system. On 6-11-2017: Corrected as per previous follow-up. On 24.04.2018: Corrected as per previous follow-up inspections. On 05.02.2019: Corrected. On 18-11-2019: It is an integrated part of the fire fighting system. On 26-10-2021: Follow the issue no-52. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 52 | The required standpipe system is not installed in accordance with the ACCORD standard. | Install a new standpipe system in accordance with ACCORD standard 5.4 and NFPA 14. A class III system shall be installed in buildings with the highest occupiable floor 10 m (33 ft.) above grade or more. A class I system shall be permitted in buildings protected throughout by an approved automatic sprinkler system. | Done. The standpipe system is active, waiting for T&C by ACCORD | Jul 24 2016 | On 9/1/2017: Installation work is going on. On 6/04/2017: Installation work is going on. On 25/07/2017: Installation work is going on. On 6-11-2017: T&Cx verification shall be done by Accord. On 24.04.2018: Design has been reviewed from Accord and installation is going on. On 05.02.2019: Installed fire pump has been found in negative suction. Installation of fire pump shall comply NFPA-20. On 18-11-2019: The system shall be in compliance with NFPA 14 & 20. Accord will verify through Testing & Commissioning inspection. On 30/11/2021: T&CVI found that the standpipe system is required final verification on-site. See detailed T&CVI Report. On 17.01.2022: The system is approved on the Final Verification Inspection. On 03/11/2022: Corrected. On 05/04/2023: Corrected as per last FVI. On 23-Oct-25: Corrected. | 6 Months | Corrected
Initial Inspection |  | 53 | No fire detection system is installed in Shed-1. The existing interconnected detectors in Unit-2 and Unit-3 activate independently of each other. | Provide automatic smoke detection throughout all buildings that is tied into a single fire alarm system, in accordance with NFPA 72. | We have installed sprinkler system instead of detection system. The system is ACTIVE now. | Jul 24 2016 | On 6/04/2017: Installation work is going on. On 25/07/2017: Installation work is going on. On 6-11-2017: No visible progress observed. Factory has a plan to install sprinkler protection system. On 24.04.2018: Design has been reviewed from Accord and installation is going on. On 05.02.2019: In progress. On 18-11-2019: Work is in progress. It is an integrated part of the fire alarm system. On 30-11-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 9 Month | Corrected
Initial Inspection |  | 54 | Lighted exit signage was not provided to the Unit-2 northwest and northeast exit stairs on the rooftop and along a path of egress from the Unit-2, fourth floor office area to the exit stairs. | Provide exit signs above all building exits to the exterior, all doors to the exit stairs and along all paths of travel where a change of direction is not obvious. | Corrected | Apr 28 2016 | On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 1 Month | Corrected
Initial Inspection |  | 55 | Exit signage was not illuminated (burned out, broken, etc.) in multiple locations throughout the buildings. | Regularly inspect all exit signage and replace/install lights as needed to illuminate signs. The source of illumination shall provide not less than 50 lix at the illuminated surface with a contrast of not less than 0.5. Approved self luminous signs which provide evenly illuminated letters having a minimum luminance of 0.2 cd/m^2 may also be used. | Corrected | Apr 28 2016 | On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 1 Month | Corrected
Initial Inspection |  | 56 | Inspection, testing and maintenance for the emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | Corrected | Apr 28 2016 | On 25/08/16: Corrected. On 03/11/16: Corrected On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Corrected. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Initial Inspection |  | 57 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along all egress routes in all buildings. | Test the emergency lighting system on each floor and provide additional emergency fixtures to supply adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and along exit discharge paths and a minimum 2.5 lux along exit access aisles. | Corrected | May 24 2016 | On 03/11/16: Corrected but shall be increased for unit-3 and shed. On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected as per previous follow-ups. The factory shall ensure proper illumination for emergency lighting system. On 6-11-2017: Corrected. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 58 | NEW FINDING (4th Follow up): Unit: 2# The high-rise building has an occupied floor greater than 23m (75 ft) and is not provided with automatic sprinkler protection. Note: Design has been reviewed by Accord already. Installation is on-going. | Provide/ Complete installation of automatic sprinkler protection throughout the building in accordance with NFPA 13. | Done. Sprinkler has been installed and Alarm system is ACTIVE, waiting for T&C by ACCORD | Nov 25 2016 | On 9/1/2017: Installation work is going on. On 6/04/2017: Installation work is going on On 25/07/2017: Installation of sprinkler system is going on. On 6-11-2017: Not completed yet. On 24.04.2018: Design has been reviewed from Accord and installation is going on. On 05.02.2019: T & Cx VI shall be done by ACCORD. On 07-11-2019: The system shall be in compliance with NFPA 13, 14 & 20. Accord will verify through Testing & Commissioning inspection. On 30/11/2021: T&CVI found that the sprinkler system is not approved. See detailed T&CVI Report. On 17.01.2022: T&C VI found that The system is approved. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 59 | NEW FINDING (4th Follow up): Unit: 2# Storage room discharges directly in the exit stair. Location: 2nd floor, Mezzanine. | Separate the hazardous materials / flammable liquid storage room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | Corrected | Oct 25 2016 | On 6/04/2017: Corrected. Removed. On 25/07/2017: Corrected. Storage area has not been found for the mentioned place. On 6-11-2017: Corrected as per previous follow-up. On 24.04.2018: Issue has been reopened. Storage was found during inspection. On 05.02.2019: Corrected as storage was not found during inspection. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 60 | NEW FINDING (4th Follow up): Unit: 1# Unsealed penetrations and openings are located in exit stair enclosures. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | Due to electrical remediation, recently this penetration created, we are sealing the penetration. | Sep 25 2016 | On 6/04/2017: Corrected. On 25/07/2017: Corrected. Note: Installation of sprinkler system is going on. On 6-11-2017: Issue reopened. Penetrations discovered due to hydrant piping work. On 24.04.2018: It was found same as last follow-up inspection. On 05.02.2019: Penetration has been found during inspection. On 07-11-2019: Corrected. None found during inspection. On 26-10-2021: Corrected On 03/11/2022: Stair-2 of Unit-1 and stair-1 of Unit-3 on ground floor were found unsealed due to electrical cable risers, BBT risers and other pipe risers penetration. On 05/04/2023: Corrected. Sealed. On 23-Oct-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 61 | New Finding (5th Follow-Up): Rooms used for combustible materials are not properly fire separated. Location: Ground and 1st floor (Unit-1), 4th floor of unit-2. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.45m (8ft.) and maximum area of 23m2 (250 ft2) - If sprinkler protected: maximum height of 3.66m (12ft.) and maximum area of 93m2 (305ft2) Separate areas of unenclosed combustible storage by a minimum clear distance of 3m (10ft.). | Corrected | Dec 12 2016 | On 24.04.2018: Not corrected. Fire door has been installed but fire door was found being repaired without proper authentication and fire door closure was found not working properly. On 05.02.2019: Installed fire doors were not properly functional. On 18-11-2019: Corrected. On 07-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 62 | New Finding (5th Follow-Up): Generator and boiler is not properly fire separated. Location: Dyeing Shed. | Separate the generator room by 2-hr fire rated construction and boiler rooms by a minimum 1-hr fire-rated construction for non-high rise, and 2-hr fire rated construction for high rise. Seal and/or protect all openings to maintain the required fire separations. When located to the exterior of a building, 3m (10 ft.) separation is required. Provide proper ventilation and consult a qualified engineer. | We are correction the issued by sealing properly | Dec 12 2016 | On 25/07/2017: Corrected as per previous follow-ups. On 6-11-2017: Issue reopened. Internal separation is not proper. On 24.04.2018: Not corrected. Unsealed penetrations were found during inspection. On 05.02.2019: Corrected. On 18-11-2019: Issue re-opened. Unprotected opening has been found in boiler and generator room which need to be sealed properly. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 63 | New Finding (5th Follow Up): None of the stair for unit-3 and the north-east and north-west stair for unit-2 is properly enclosed by fire rated material on ground floor. Door accessories were missing in many locations. Most of the doors for all units found open during inspection. | Provide minimum 1-hr rated doors for buildings with 3 or fewer stories and 1.5-hr fire rated doors for buildings that are 4 or more stories. Seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. Once fire doors are installed, every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets. | Done. Separation has been ensured by fire rated door. | Dec 12 2016 | On 24.04.2018: Not corrected. Fire doors were found held open by external force and the gap between the bottom of fire door & floor level was not found as per standard. On 05.02.2019: Interfacing of installed fire doors shall be checked during T & Cx. On 18-11-2019: Interfacing will be checked during T&C. Unsealed penetration has been found. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 64 | New Finding (5th Follow-Up): Aisles found block during inspection for some of the floors of unit-2. | All the element of means of egress shall be kept free from obstruction or impediments for all the time. | Corrected | Nov 20 2016 | On 03/11/16: New Finding On 9/1/2017: Corrected. On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Issue has been reopened. Found storage on aisles during inspection. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 65 | New finding(6th follow up):Storage was located in the exit stair discharge path. (unit-1 , 2 & 3) | Remove all storage from exit discharge path | Corrected | Jan 20 2017 | On 9/1/2017: New finding On 6/04/2017: Corrected. On 25/07/2017: Corrected. On 6-11-2017: Corrected. On 24.04.2018: Issue has been reopened. Storage was found on egress path during inspection. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. Removed. On 23-Oct-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 66 | New finding(7th follow up): Dinning area was located in building 4 & 6. Exit stair enclosures are not separated from work areas on each floor by fire-rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire rated doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire rated doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | Fire door has been installed waiting for T&C by ACCORD | Jul 7 2017 | On 6/04/2017: New finding. On 25/07/2017: The factory is working on this issue. On 6-11-2017: Stair separation work is not completed yet. On 24.04.2018: It was found same as last follow-up inspection. On 05.02.2019: Not corrected. On 18-11-2019: Fire door installation has not been completed yet. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 67 | New finding(7th follow up): Day care room was not properly separated by storage room at ground floor. Unit-1. | Needs to minimum 1-hr fire rated separation between storage room and day care room. | Corrected | Jun 7 2017 | On 6/04/2017: New finding. On 25/07/2017: Corrected as per site observation. Childcare room has been shifted to another building. On 6-11-2017: Corrected as per previous follow-up. On 24.04.2018: Corrected as per previous follow-up inspections. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 68 | New finding(7th follow up): Medical room and office was located inside the storage area. | Needs to minimum 1-hr fire rated separation between storage room and other occupancy area. | Corrected | Jul 7 2017 | On 6/04/2017: New finding. On 25/07/2017: Partially corrected. Medical room has been shifted to another building. But office area has not been properly separated from storage area. On 6-11-2017: Corrected. Relocated to MD's old house. On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 69 | New Finding (8th Follow Up): Transformer is not properly separated by fire rated construction with other Occupancies/Areas. Location: Shed-1. | 1. For Non high-rise building: Oil filled transformer shall be separated from other occupancies by a minimum 2-hr fire rated construction (wall, floor, slab etc.). Switch gears and transformer bays shall be separately housed with a 2-hr rated wall in between. Seal all penetrations and openings (door, window etc.) should be protected by 1.5-hr fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. 2. For high-rise building: Oil filled transformer shall be separated from other occupancies by a minimum 4-hr fire rated construction (wall, floor, slab etc.). Switch gears and transformer bays shall be separately housed with a 4-hr rated wall in between. Seal all penetrations and openings (door, window etc.) should be protected by 2-hr fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. 3. Oil filled transformers shall not be housed above ground level Or Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. | Done. We have reinstalled gypsum board at the transformer room. | Sep 25 2017 | On 25/07/2017: New Finding On 6-11-2017: No progress observed. On 24.04.2018: In progress. They have installed gypsum board but fire door installation is not completed yet. On 05.02.2019: Corrected. On 18-11-2019: Issue re-opened. Gypsum board was damaged in one side during follow up inspection. Unsealed penetration has been found. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected as per previous follow-up. On 23-Oct-25: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 70 | New Finding(8th Follow-Up): Unsealed elevator shafts are located inside the working place of Unit-2. | Provide a minimum 2-hr fire rated construction to separate the elevator shaft from each floor level. Seal all penetrations and openings in floors/ceiling assemblies to maintain the fire separation. | Corrected | Sep 25 2017 | On 25/07/2017: New Finding On 6-11-2017: Separation work is in progress. On 24.04.2018: Not corrected. Fire door has been installed but door was found held open by external force. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 71 | New Finding (8th Follow Up): Unsealed penetration of compressor and Shed-3 (production floor) has been observed under same closure. Compressor room is not properly separated by fire rated construction. | Separate the air compressors by a minimum 1-hr fire-rated construction for non-high rise and 2-hr fire rated construction for high rise. Seal and/or protect all openings to maintain the required fire separations. When located to the exterior of a building, 3m (10 ft.) separation is required. | Due to electrical remediation, recently this penetration created, we are sealing the penetration. | Aug 25 2017 | On 25/07/2017: New Finding On 6-11-2017: Corrected. Spatial separation observed. On 24.04.2018: Corrected as per previous follow-up inspections. On 05.02.2019: Corrected. On 18-11-2019: Corrected as per previous follow up. On 26-10-2021: Corrected. On 03/11/2022: Unsealed cable penetrations were found in the Boiler, Generator, Compressor and substation rooms on ground floor. On 05/04/2023: Corrected. Sealed. On 23-Oct-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 72 | New finding in 9th: Parapets or guards are provided on occupiable roof are less than 1067mm (42 inch.) Location: Building 2 | Provide parapets or guards with a minimum height of 1067mm (42 inch.) | Corrected | Jun 12 2017 | NF on 06-11-2017 On 24.04.2018: Corrected as per site observation. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 73 | New Finding (9th FUI):Unsealed penetrations were found in the fire rated floor/ceiling assembly. Location: Building 1 (Cable riser) | Seal the penetrations with listed fire stop material up to full thickness to maintain separation. | Due to electrical remediation, recently this penetration created, we are sealing the penetration. | Jun 12 2017 | NF on 06-11-2017 On 24.04.2018: Not corrected. Found during inspection. On 05.02.2019: Not sealed properly. On 18-11-2019: Corrected. No openings found during follow-up inspection. On 26-10-2021: Corrected On 03/11/2022: Unsealed BBT riser (Unit-1 and Unit-2), electrical cable riser (Unit-3) and old standpipe riser (Unit-3) were found on all floors. On 05/04/2023: Corrected. Sealed. On 23-Oct-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 74 | New Finding (10th Follow-Up): The width of an egress aisle on the eighth floor of Unit-1 was less than 36-in. | Provide minimum aisle widths of 36-in. | Corrected | Jan 5 2018 | On 24.04.2018: NEW FINDING. On 05.02.2019: Not Corrected. On 18-11-2019: Corrected. Aisles were found adequate in width. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 75 | New Finding (10th Follow-Up): Storage was located in the exit stair. Location: Unit-1 | Remove all storage from exit stairs. | Corrected | Jan 5 2018 | On 24.04.2018: NEW FINDING. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. Removed. On 23-Oct-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 76 | New Finding (10th Follow-Up): Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along all egress routes in all buildings. Location: Unit-1,2,3 | Test the emergency lighting system on each floor and provide additional emergency fixtures to supply adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and along exit discharge paths and a minimum 2.5 lux along exit access aisles. | Corrected | May 24 2018 | On 24.04.2018: NEW FINDING. On 05.02.2019: Not Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 77 | New Finding (10th Follow-Up): Exit signage not illuminated during testing (burned out, broken, etc.). Location: Unit-1,2,3, Shed-1. | Regularly inspect all exit signage as per Accord standard and replace/install lights as needed to illuminate signs. | We have already replaced illuminated exit sign. | May 24 2018 | On 24.04.2018: NEW FINDING. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Unilluminated exit signs and non-functional emergency lights (fog lights) were found on several floors of Unit-1 and Unit-2. On 05/04/2023: Corrected. During follow up inspection it was observed that exit signage replaced. On 23-Oct-25: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 78 | New Finding (10th Follow-Up): Directional exit sign not provided. Location: Unit-1 | Lighted directional exit signs shall be placed at entrance to an exit. Additional exit signs shall be placed throughout the facility anywhere the continuation of the egress is not obvious. Lighted directional exit signs shall be provided with either battery backup or uninterruptable power supply systems and shall be continuously illuminated. | Done, directional light has been installed. | May 24 2018 | On 24.04.2018: NEW FINDING. On 05.02.2019: Corrected. On 18-11-2019: Issue reopened. Factory shall install directional sign where required. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 79 | New Finding (10th Follow-Up): The exit discharge paths serving the exit stair-3 were less than 10 ft wide and were not separated from the building interior. Location: Unit-3 | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft., to provide a minimum 1-hr fire separation. | Corrected | May 24 2018 | On 24.04.2018: NEW FINDING. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 80 | New Finding (10th Follow-Up): Manual on-off switch is provided for emergency lighting. Location: Unit-3 | Remove manual on/off switches from emergency lighting units to prevent them from being switched off. | Corrected | May 24 2018 | On 24.04.2018: NEW FINDING. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 81 | New Finding (10th Follow-Up): Building did not have occupant load signs. Location: Unit-3 | Provide occupant load signs at required locations. | Corrected | Jan 5 2018 | On 24.04.2018: NEW FINDING. On 05.02.2019: Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 82 | New Finding (10th Follow-Up): Parapets or guards are not provide in occupiable roof. Location: Unit-3 | Provide parapets or guards with a minimum height of 1067mm (42 inch.). | Corrected | May 24 2018 | On 24.04.2018: NEW FINDING. On 05.02.2019: Not Corrected. On 18-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 83 | New Finding (10th Follow-Up): The praying area in the first floor is not separated from adjacent dyes store area by fire rated construction. Location: Unit-3 | Separate the praying area by a minimum 3-hr fire-rated construction having a direct access to exit stair. Seal and/or protected all openings to maintain the required fire separations. | Corrected | May 24 2018 | On 24.04.2018: NEW FINDING. On 05.02.2019: Corrected. Prayer area is not found during inspection. On 18-11-2019: Corrected. On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 84 | New Finding (12th FUI): Combustible storage was found in Dining room | Remove combustible storage from Dining room | Done. Storage removed from dining | Nov 22 2019 | On 18-11-2019: NEW FINDING On 26-10-2021: Corrected. On 03/11/2022: Corrected. On 05/04/2023: Corrected. On 23-Oct-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 85 | New Finding (14th FUI): LPG/CNG gas cylinders were found in the factory premise. | LPG/CNG cylinders are permitted to be stored in a separate dedicated building on the factory premises within its boundaries if the building meets the following conditions: 1. The storage building must be at least 3 meters away from any other building and boundaries. 2. The exterior walls of the building must have a fire resistance rating of 3 hours using noncombustible construction. 3. Doors and other openings in the exterior walls must be protected with suitable closing devices having a fire protection rating of 3 hours. 4. The building is to be used for no other purpose than the storage of LPG/CNG cylinders. 5. The building must be mechanically ventilated to control the accumulation of flammable vapors. 6. The installations must be approved and accepted by the requirements of the AHJ, Gas supply company regulations, manufacturers/supplier’s instructions/ guidance, CIOB and all other applicable agencies, codes and standards. | Due to service work (welding), The cylinder was used and already has been removed | Mar 2 2023 | On 05/04/2023: Corrected. During follow-up inspection LPG/CNG cylinders were not observed. On 23-Oct-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 86 | New Finding(16th FUI):Chemical storage area is not separated by fire-rated construction having non rated door and unsealed penetrations and openings. Location: 8th floor of the Building-2(9-storied) and 5th & 6th floor of the building-3(7-storied). Non-compliance reason: Unprotected opening. | Provide a 4-hour fire-rated construction barrier to separate the chemical store from the surrounding production area. The 4-hour fire-resistive separation shall have no openings/ no unprotected openings therein and shall provide a fire resistance for at least four hour. Chemical stores shall comply with BNBC 2006, Part 3, Section 2.13. or, Ensure exempt amounts of chemical are located on chemical stores with other occupancy as per Table 3.2.7 (BNBC 2006) | We have reduced printing chemical (pigment) at mentioned floor | Jan 23 2026 | On 23-Oct-2025: New Finding.RPO Comments (10-Feb-2026): It is a fire rated seperation issue so the factory management is required to complete the issue before the next follow-up inspection. | Within 3 months | In Progress
Follow Up Inspection |  | 87 | New finding(16th FUI): It was observed that first floor (claim mezzanine floor) is not separated from ground floor by fire rated construction due to non-rated steel slab/ceiling, column, & beam Location: First floor of the Building-2(9-storied). Non-Compliance: 1. Non-rated steel slab/ceiling, beam, column. 2. First floor area(claim mezzanine )is 6299 SFT. & ground floor area is 13980 SFT. | Mezzanine floor shall not exceed 33.33% of the building plinth area as per BNBC-2006, clause 1.12.6.1. Separate each floors by fire rated construction as per BNBC, Part-3, chapter-3 and Table 3.3.1. 3-hr fire rated separation is required from claimed mezzanine floor (actually first floor) to ground floor other surroundings as well as separation is needed at required number of exit stairs. Or, reduce the 1st floor area (claimed mezzanine) below 33.33% of the building plinth area. | We have engaged consultant to solve the issue based on inspection comments | Apr 23 2026 | On 23-Oct-2025: New Finding. RPO Comments (10-FEB-2026): The factory stated in the monthly CAP update that the issue has not yet been completed and that factory management is currently working on it; therefore, the progress status remains “in progress.” The factory management is required to complete the issue before the next follow-up inspection. | Within 6 months | In Progress
Follow Up Inspection |  | 88 | New Finding(16th FUI): During the inspection, it was observed that some fire doors were normal printed, some fire doors were leaf & exit hardware damaged, some doors were welding. In addition, field modification (Changes made to a listed assembly or component after it has been manufactured) has been observed. Location: North-East side (Exit stair-2) of the Building-2(9-stoired). | Replace/install the non-functional/missing fire door accessories and properly inspect, test & maintain fire door as per NFPA 80. In cases of a field modification, the laboratory with which the product or component being modified is listed shall be contacted through the manufacturer and a written or graphic description of the modifications shall be presented to that laboratory. A written authorization from that laboratory is required. Field modification shall conduct as per NFPA 80. | We will change fire door where required. | Jan 23 2026 | On 23-Oct-2025: New Finding. RPO Comments (10-FEB-2026): The factory stated in the monthly CAP update that the issue has not yet been completed and that factory management is currently working on it; therefore, the progress status remains “in progress.” The factory management is required to complete the issue before the next follow-up inspection. | Within 3 months | In Progress
Follow Up Inspection |  | 89 | New Finding(16th FUI): It was observed that The exit stair enclosures are not separated from work areas and other spaces on each floor by fire-rated construction . Location: East side of the Building-1. Non-Compliance: Unprotected opening on 2nd & first floor. | The exit stair enclosure shall be provided with a minimum 1-hr fire resistance rating for buildings with 3 or fewer stories and a minimum of 2- hr. fire resistance rating for buildings 4 or more stories. Provide 1-hr. fire rated door and seal all penetrations and openings by 1 hr. fire rated fire rated barrier construction for building with 3 or fewer stories. Provide 1.5 hr. fire rated door and seal all penetrations and openings by 2 hr. fire rated fire rated barrier construction for building with 4 or more stories in accordance with section 6.3.1.2 of RSC Technical Guidelines (Standard)¹ V1.0. Provide a fire-resistive rated assembly between the exterior exit stairs and the building up to 10 ft. beyond the end of the stair to achieve the required separation. The rated assembly shall be approved and/or designed by a qualified fire protection engineer. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. Keep proper datasheet & certifications for installed fire doors & accessories on-site for verification. The clearance under the bottom of a door shall be a maximum of 3⁄4 in. (19 mm). | We will take required steps to solve the issue | Jan 23 2025 | On 23-Oct-2025: New Finding. RPO Comments (10-Feb-2026): The factory stated in the monthly CAP update that the issue has not yet been completed and that factory management is currently working on it; therefore, the progress status remains “in progress.” The factory management is required to complete the issue before the next follow-up inspection. | Within 3 months | In Progress
Follow Up Inspection |  | 90 | New Finding(16th FUI): It was observed that A connecting corridor (enclosed) has been constructed between two buildings which is not functioning as a horizontal exit. However, fire/smoke propagation between buildings are not restricted. Location: Between Building-1 & Building-2 on the 3rd floor. | Separate the buildings with a minimum 2-hour fire-rated construction on both sides of the connecting corridor. Opening protection extending up to 10 feet beyond the connecting corridor shall meet section 4.6 of RSC Technical Guidelines (Standard)¹ V1.0 . | We will take required steps to solve the issue and will follow inspection comments | Jan 23 2026 | On 23-Oct-2025: New Finding. RPO Comments (10-Feb-2026): The factory stated in the monthly CAP update that the issue has not yet been completed and that factory management is currently working on it; therefore, the progress status remains “in progress.” The factory management is required to complete the issue before the next follow-up inspection. | Within 3 months | In Progress
Follow Up Inspection |  | 91 | New Finding(16th FUI): Chemical store(Building-4) is not separated from production(Building-3) on ground floor by fire rated construction. Location: South side at ground floor of the Building-3. Non-Compliance: Unprotected opening(Painted door). | Provide a 4-hour fire-rated construction barrier to separate the chemical store from the surrounding production/combustible storage areas. The 4-hour fire-resistive separation shall have no openings/ no unprotected openings therein and shall provide a fire resistance for at least four hour. Chemical stores shall comply with BNBC 2006, Part 3, Section 2.13. or, Ensure exempt amounts of chemical are located on chemical stores with other occupancy as per Table 3.2.7 (BNBC 2006) | We will take required steps to solve the issue | Jan 23 2026 | On 23-Oct-2025: New Finding. RPO Comments (10-Feb-2026): The factory stated in the monthly CAP update that the issue has not yet been completed and that factory management is currently working on it; therefore, the progress status remains “in progress.” The factory management is required to complete the issue before the next follow-up inspection. | Within 3 months | In Progress

## Electrical
Date
31-Mar-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | M.M. Knitwear Ltd., Ambagh Road, Konabari, Nilnagar, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2015-02-06
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Thermographic scanning of the entire electrical system has not been performed. | Thermographic scanning of the entire electrical system must be performed twice in a year. | Done | Jul 5 2015 | On 28/02/2016: Corrected. | 8 Weeks | Corrected
Initial Inspection |  | 2 | Insulation resistance test of electrical equipment is not performed. | Insulation resistance test of all power cables (up to floor distribution board or SDB) must be performed in a periodic manner and recorded. | Done | Jul 5 2015 | On 28/02/2016: Corrected. On 24/04/2018: Insulation resistance of all power cables shall be measured. | 8 Weeks | Corrected
Initial Inspection |  | 3 | PFI panel not fixed to the foundation and burnt fuses not being replaced. | Fix the panel to the foundation by taking shut down and remove the unused capacitor and fuses. The panel must be clean and free from lint's. | Done | May 31 2015 | On 04/10/2015: Corrected. | 3 Weeks | Corrected
Initial Inspection |  | 4 | Phase separator replaced by fabricated foot mat. | Put purposely made phase separator (rubber type) between two phases; also terminate cables by proper sized cable lugs and cover cable lugs by heat shrinks. | Done | May 17 2015 | On 28/02/2016: Corrected. | 1 Week | Corrected
Initial Inspection |  | 5 | Copper bar being terminated to MCCB terminals. | Remove and replace the copper bar by terminating required size of cables from MCCB to the busbar. Install phase separator provided by the manufacturer. | Done | May 31 2015 | On 04/10/2015: Corrected. | 3 Weeks | Corrected
Initial Inspection |  | 6 | Transformer silica gel is discolored and transformer breather oil cup is empty. | Replace silica gel by a new one. Or dry it under sun and reuse it, if color regains and fill the transformer breather oil cup by transformer oil. | Done | Jun 21 2015 | On 04/10/2015: Corrected. | 6 Weeks | Corrected
Initial Inspection |  | 7 | Arcing horn on HV side bushing not aligned. | Arcing horns must be properly aligned (straight) by keeping the distance of 20-153 mm. Maintain minimum working clearance 0.7 meter around the machine. | Done | Jun 21 2015 | On 04/10/2015: Corrected. | 6 Weeks | Corrected
Initial Inspection |  | 8 | Large exhaust fans in production floors are directly controlled by MCB. | Use Direct On Line (DOL) switch to stop auto stop after power failure and connect each individual fan frames with earth. | Done | May 24 2015 | On 28/02/2016: Corrected. | 2 Weeks | Corrected
Initial Inspection |  | 9 | Cables and wires terminated to uncoordinated MCCB. | Cables and wires must be terminated to the MCCB by properly coordinating or vice versa. | Done | Jun 7 2015 | On 04/10/2015: Corrected. | 4 Weeks | Corrected
Initial Inspection |  | 10 | The lightning risk figure is above 40, but a lightning protection system (LPS) has not been installed yet. | Design and install Lightning Protection System (LPS) in the factory; the LPS designs must be submitted to accord before starting installation. | Done | May 26 2016 | On 28/02/2016: This issue is not done yet. New committed timeline is given till 15-4-16 to close the issue. On 24/04/2016: Factory has LPS drawing and installation process going on. This issue not corrected yet. New committed timeline is given till 26-05-2016. On 25/08/2016: Not Corrected. Existing LPS is not as per standard. Need modification. On 03/11/2016: Corrected. | 16 Weeks | Corrected
Initial Inspection |  | 11 | Hot spot is found inside the panel (typical). | Check the connection and measure the connected load. Replace the MCB if it is needed. | Done | Mar 10 2016 | On 28/02/2016: This issue is not done yet. New committed timeline is given till 10-3-16 to close the issue. On 24/04/2016: Corrected. No hot spot observed at inspection time. On 24/03/2018: Address all generated hot spot in priority basis. | 1 Week | Corrected
Follow Up Inspection |  | 12 | New Finding: Electrical Single Line Diagram (SLD) doesn't comply with existing system. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by accord. |  | May 26 2016 | On 28/02/2016: This issue is not done yet. New committed timeline is given till 15-4-16 to close the issue. On 24/04/2016: Factory has SLD but need modification. On 25/08/2016: Not Corrected. On 03/11/2016: Not Corrected. On 09/01/2017: Not Corrected. On 06/04/2017: Not Corrected. On 25/07/2017: Not Corrected. On 06/11/2017: Not Corrected. Still few panel boards are not included into SLD. Circuit breakers shall be properly identified with cable markers etc. On 24/04/2018: Not Corrected. On 05/02/2019: Not Corrected. On 07/11/2019: Not Corrected. On 12/01/2021: SLD needs modification. Identification not completed yet. On 26/10/2021: Not Corrected. On 03/11/2022: Not Corrected. Significant progress has been observed. Factory almost 90% completed their SLD remediation work, only earthing system has been found mismatch with accepted SLD (ECC layout). On 05/04/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 13 | New Finding: Inadequate space around transformer for performing maintenance work. | Ensure minimum 1.07 m working space around the transformer (and related electrical installations). | Done | May 26 2016 | On 28/02/2016: This issue is not done yet. New committed timeline is given till 15-4-16 to close the issue. On 24/04/2016: Renovation work is going on. New committed timeline is given till 26-05-2016. On 25/08/2016: Corrected. | 6 Months | Corrected
Follow Up Inspection |  | 14 | New Finding: Multiple cables terminated at MCCB terminals /busbar. Again, rusted extension bar used. | Terminate each power cable at single terminal and use proper sized cable lug. Clean/replace rusted busbar. | Done | Apr 15 2016 | On 28/02/2016: This issue is not done yet. New committed timeline is given till 15-4-16 to close the issue. On 24/04/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 15 | New Finding: Battery terminals are left open. | Use insulated rubber cap to cover all the battery terminals. | Done | Nov 15 2015 | On 28/02/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 16 | New Finding: Generator body has been earthed by inadequate/ improper sized (type) cable. | Ensure minimum two earthing connection for generator body (consult with your generator supplier). Generator body must have earth connection with half of phase conductor. Or follow manufacturer/ suppliers recommendation. | Done | Jan 15 2016 | On 28/02/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 17 | New Finding: Cables in store room are encaged in flexible conduits. | Wiring in store room has to be concealed or encaged in rigid conduit (steel G.I. pipe). | Done | Dec 15 2016 | On 28/02/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 18 | New Finding: Oversized circuit breakers or circuit breakers are not adjusted accordingly. | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. | Done | May 26 2016 | On 28/02/2016: This issue is not done yet. New committed timeline is given till 15-4-16 to close the issue. On 24/04/2016: At inspection time oversized breaker observed. So, this issue is not corrected. New committed timeline is given till 26-05-2016. On 25/08/2016: Not Corrected. On 03/11/2016: Not Corrected. On 09/01/2017: Not Corrected. On 25/08/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 19 | New Finding: Earth pit resistance record is unavailable. Again, earth pits are not identifiable. | Identify each earth pit and mark it for periodic maintenance purpose. Again, all earthing systems shall be tested for resistance on any dry day not less than once in every two years and records should be preserved. | Done | May 26 2016 | On 28/02/2016: This issue is not done yet. New committed timeline is given till 30-3-16 to close the issue. On 24/04/2016: This issue is not corrected. New committed timeline is given till 26-05-2016. On 25/08/2016: Corrected. On 24/04/2018: All connections to the earthing system shall have provisions for periodical inspection, and every pit shall have proper identification as per earthing layout. | 3 Months | Corrected
Follow Up Inspection |  | 20 | New Finding: Power cables are bent excessively. | Avoid power cable bending in electrical system; in unavoidable case bend cables without any stress but not less than 135 degree. | Done | Apr 15 2016 | On 28/02/2016: This issue is not done yet. New committed timeline is given till 15-4-16 to close the issue. On 24/04/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 21 | New Finding: Earth lead cable/ Earth Continuity Conductor size is inadequate/undersize. | Resize earth lead cable/ECC for LT panel/MDB/DB; follow BNBC 2006 Part 8 chapter 2 section 2.8 for sizing your earthing cables (usually ECC should be equal to the half of the respective phase cable). | Done | May 26 2016 | On 28/02/2016: This issue is not done yet. New committed timeline is given till 15-4-16 to close the issue. On 24/04/2016: Renovation process is going on. This issue not corrected. New committed timeline is given till 26-05-2016. On 25/08/2016: Corrected. On 12/01/2021: Earthing cable shall not have current. Ensure load side earthing and neutral are segregated from each other. | 3 Months | Corrected
Follow Up Inspection |  | 22 | New Finding: Panel/distribution boxes are inaccessible or can not be opened to perform any maintenance work. | Take necessary initiative thus every panel/ distribution board can be easily accessible. | Done | Apr 10 2016 | On 24/04/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 23 | New Finding: Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | Hang this instruction near all electrical equipment (LT panel, MDB, FDB, DB, SDB) on a visible location. | Done | Apr 10 2016 | On 24/04/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 24 | New Finding: Cable duct/channels are filled with fluffs (lint/dust). | Clean all the cable channels/ducts; then cover them (you may use checkered /perforated plate at the bottom). And after each maintenance, keep record. | Done | May 26 2016 | On 25/08/2016: Not Corrected. On 03/11/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 25 | New Finding: Circuit is drawn from busbar without circuit breaker or any protective means. | For distribution board, along with the main circuit breaker all outgoing circuits shall have individual outgoing circuit breaker. | Done | May 26 2016 | On 25/08/2016: Corrected. No such circuit found during inspection. | 1 Month | Corrected
Follow Up Inspection |  | 26 | New Finding: Thermography scanning is not continued periodically. Last date was 19/08/2015. | Keep a thermography scanning record of your electrical system at least twice a year. | Done | Sep 30 2016 | On 03/11/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding: Hot spots at terminations inside panel. | Identify the overloading, loose connection, unbalanced load which may cause the excessive heat-rise and take action accordingly. However, immediately correct such points. | Done | Sep 30 2016 | On 03/11/2016: Not Corrected. On 09/01/2017: Not Corrected. On 06/04/2017: Not Corrected. On 25/07/2017: Corrected. Not found this time. Regular observation and maintenance is necessary. | 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding: Transformer oil test report is unavailable. | Check the transformer oil condition by performing oil test. Do it once in a year and keep the record. | Done | Sep 30 2016 | On 03/11/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding: Cables in service are joined (splicing) improperly between terminations. | Existing cables with joints must be spliced using butt splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. | Done | Sep 30 2016 | On 03/11/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 30 | New Finding: Light in store room / storage areas is uncovered. | Lights in store room / storage areas shall be covered. | Done | Sep 30 2016 | On 03/11/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: Transformer silica gel is discolored. | Replace silica gel by a new one; or dry it under sun and reuse it, if color regains. | Done | Sep 30 2016 | On 03/11/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 32 | New Finding: (1) Distribution board does not have permanent identification markings (typical). (2) List of circuit or SLD of existing circuits are not available in each electrical panel board. | (1) Provide clear and permanent identification marks in all distribution boards. (2) List of circuit or SLD of existing circuits shall be available for each electrical panel board. | Done | Sep 30 2016 | On 03/11/2016: Not Corrected. Distribution board have identification but SLD was not hung. On 09/01/2017: Not Corrected. On 06/04/2017: Not Corrected. On 25/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: Panel doors are not connected with earth. | All metal panel doors shall have earth connection by at least 4 rm earth cable. | Done | Sep 30 2016 | On 03/11/2016: Corrected. On 24/04/2018: All fencing use to guard transformer shall have earthing connection. | 1 Month | Corrected
Follow Up Inspection |  | 34 | New Finding: LPS is not maintained properly. Components are in non functional state (rusted nut bolts, air terminals, conductors are missing). | Rusted nut bolts shall be replaced by anti-rusted ones. Missing components shall be reinstalled properly. Design has to comply with installation. | Done | May 6 2017 | On 06/04/2017: Not Corrected. Some portion of building 3 is not covered by existing installation. Timeline extended up to 06/05/2017. On 25/07/2017: Not Corrected. Show required design calculation for shed and, install LPS on it considering risk index and engineering calculation. Ensure that installation comply with design and standard. On 06/11/2017: Not Corrected. 1. WTP, Generator houses are not protected. 2. The part-1 of Shed 1 is not fully protected. Proper calculation with drawing is missing. 3. Building-2 (9 storied) has some additional roof on 2 sides of the building after parapet wall. The additional part having 5.5 ft. width is not covered. 4. Hence the design/drawing is not as-built. On 24/04/2018: Not Corrected. On 05/02/2019: Not Corrected. On 07/11/2019: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 35 | New Finding: Cables are not provided with continuous support. | Use rigid conduit /cable tray to support cables at any where to avoid sagging and tension. | Done | Feb 20 2017 | On 06/04/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 36 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Done | Feb 20 2017 | On 06/04/2017: Corrected. On 24/04/2018: Power and signal cable for boilers shall be distributed using proper type insulator to avoid damage of cables. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Inadequate working space around (or in front of) board/panels and access to the board/panels is obstacles. | At least 1.07 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel. | Done | Feb 20 2017 | On 06/04/2017: Corrected. On 24/04/2018: At least 1.07 meter dry working clearance shall be maintained in front of each electrical board/panel. Each electrical panel shall be easily accessible. In case of height its top shall not be higher than 2m from base; and door opening shall be at least 90 degree. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: No working separation between LT panel/s and HT unit/s (transformer, HT switchgear). | A working separation between LT and HT must be ensured. A brick wall will do it; and adequate working clearance (1.07 m) and ventilation must be ensured. | Done | Mar 20 2017 | On 06/04/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 39 | New Finding: Periodicity of transformer oil test (dielectric strength test) survey is not continued. | Transformer oil test (dielectric strength test for oil) shall be done once in a year. It is recommended to do the test from any govt. authority (REB, PDB, DESCO etc.) | Done | Dec 10 2017 | On 24/04/2018: The dielectric strength of oil of all transformer is not measured. On 05/02/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: At cutting section power sockets are hanging or kept on floor. | Power socket has to be installed on rigid support/base securely and at minimum 200 mm above floor level. It cannot be hanged. | Done | Dec 10 2017 | On 24/04/2018: Not Corrected. On 05/02/2019: Not Corrected. On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Hazardous lights in store room / storage areas are uncovered. Some lights are not protected on hazardous location. | Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. | Done | Dec 10 2017 | On 24/04/2018: Provide cover for hazardous light installed both in garments and chemical storage area. On 05/02/2019: Not Corrected. On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Ducts are not covered at the supporting points. Fluffs are found inside the ducts. | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. |  | Dec 10 2017 | On 24/04/2018: Provide cover and keep 20-25% free space in cable tray/duct. On 05/02/2019: Not Corrected. On 07/11/2019: Not Corrected. On 12/01/2021: The issue is not addressed in all places. On 26-Oct-2021: Not Corrected. On 03/11/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: 1.Vertically laid cables are not supported at some locations. Specially behind the LT panels. 2.Trench cables are not supported at location behind LT panels. | Need to support all power cables and protect them from external damages and dusts. |  | Dec 10 2017 | On 24/04/2018: Not Corrected. On 07/11/2019: Not Corrected. On 12/01/2021: The issue still remains in a few places. On 26-Oct-2021: Not Corrected. On 03/11/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | Done | Dec 10 2017 | On 24/04/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: No LOTO (Lock-Out-Tag-Out) policy is introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all using records. | Done | Dec 10 2017 | On 24/04/2018: No policy was documented. Safety training shall have a reflection on site. On 05/02/2019: Not Corrected. On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Distribution board (or equipment) containing multiple power sources does not have any multiple sources sign. | Multiple sources sign shall be posted on or adjacent the equipment and panels to inform personnel who will work on it. The source sign shall be posted in a manner that it will be durable and visible after installation. The source sign may be with or without pictogram/graphic to suit individual requirements. | Done. We have used multiple sign. | May 30 2018 | On 05/02/2019: Not Corrected. On 07/11/2019: Not Corrected. On 12/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: The substation room (equipment rated 1200 A or more) does not have a continuous and unobstructed way of egress travel. | The room shall have an entrance to and egress from (2 ft. X 6 ½ ft.) at each end of the working space if its equipment is rated 1200 A or more and over 6 ft wide. The door(s) needs to be opened in the direction of egress if the door is located less than 25 ft from the nearest edge of the working space(the room shall have only one entrance if the working space depth is double, and the equipment located no closer than the required working space from the edge of the equipment). | Done | May 30 2018 | On 05/02/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Power busbars are installed congested; and power cables touch other phase busbar/s. Phase barrier/separators are missing in MCCBs. | Power bus bar must be installed with adequate clearance (not less than 2.5 inch for LV) between two bars. Cables must not touch opposite bus bars in any case. Phases must be separated by insulator (a rubber type no-flammable materials shall be used for it). | Done | May 30 2018 | On 05/02/2019: Not Corrected. On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Circuit is drawn from bus bar without any protective means (location: all substation). | Each electrical circuit must be drawn from distribution board busbar using a proper type protection arrangement (MCCB/MCB). | In Progress. We are ensuring with protective means the rest area. | May 30 2018 | On 05/02/2019: Not Corrected. On 07/11/2019: Not Corrected. COSs have multiple output. On 12/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Sub station room/working area of distribution board has inadequate illumination. | Adequate illumination in the sub station room and working area of distribution board shall be ensured thus any maintenance can be done comfortably (around 150 lux). | Done | May 30 2018 | On 05/02/2019: Not Corrected. On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Foreign systems have been installed within the dedicated space of equipment/panel board. | Foreign systems cannot be located within the footprint space extending from the floor to a height of 6 ft. above the equipment or to the structural ceiling, whichever is lower. | Done | May 30 2018 | On 05/02/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Inadequate working space around (or in front of) board/panels and access to the board/panels is obstacles. | At least 1.07 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel. | Done | May 30 2018 | On 05/02/2019: Not Corrected. On 07/11/2019: Corrected. Board has been removed. | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: Circuit breaker knob is broken or not operational. | All circuit breaker shall be operational. Replace the faulty circuit breaker with new one. | Done | May 30 2018 | On 05/02/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: Generator room has inadequate ventilation. | Adequate ventilation must be maintained in generator room. Cross/forced ventilation must be ensured. For exhaust fan, the fan diameter must not be less than 18 inch. | Done | May 30 2018 | On 05/02/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding: Multiple cables (came from different electrical consumers) terminated at MCCB terminals. Loop connection has been used powering multiple circuits through MCB/MCCBs. | Each electrical circuit must be terminated at single MCB/MCCB terminals. No loop connection shall be used; each single cable shall be terminated using cable lug (flat/i) at each terminal. Combo bus bar may be used (but incoming cable size must meet the rated capacity). | Done | May 30 2018 | On 05/02/2019: Not Corrected. On 07/11/2019: Corrected. Board has been removed. On 12/01/2021: Multiple, looping at the circuit breaker terminal shall be removed. | 1 Month | Corrected
Follow Up Inspection |  | 56 | New Finding: Panel/distribution board is not firmly fixed with the foundation. | Panel base must be securely fixed to the foundation. With appropriate fastening devices. | Done | May 30 2018 | On 05/02/2019: Not Corrected. On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: No working separation between LT panel/s and HT unit/s. | High voltage equipment with exposed live parts or wiring terminal installed in a low voltage vault/room shall be effectively separated from the space occupied by low voltage equipment by a suitable partition, screen or fence. | Done | May 30 2018 | On 05/02/2019: Not Corrected. On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: MCCB is installed without any enclosure. Distribution Board's top/bottom is left open (typical issue). | Each MCCB/MCB must be enclosed by proper type material. the material must not be more than 18 SWG graded. Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. | Done | May 30 2018 | On 05/02/2019: Not Corrected. On 07/11/2019: Corrected. On 12/01/2021: Panel base plates shall be installed, at all times, and cables entering the panel shall be firmly fixed with a cable gland. | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per cable current ampacity/load current; if adjustment is not possible, replacement will be the only way. |  | May 30 2018 | On 05/02/2019: Not Corrected. On 07/11/2019: Not Corrected. On 12/01/2021: The work is not completed yet. On 26/10/2021: Not Corrected. On 03/11/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: Insulation resistance test of electrical power cables is manipulated. | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | Done | Mar 20 2019 | On 07/11/2019: Corrected. On 12/01/2021: Insulation resistance of all power cables shall be measured. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Exhaust fan body and fan blade enclosure has no earth connection. | Exhaust fan frame and its enclosure in the production area/s shall be connected to earth. | Done | Mar 20 2019 | On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. | Done | Mar 20 2019 | On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Celling fan are installed in a improper height. | Install the celling fan ensuring enough height/use stand fan. | Done | Mar 20 2019 | On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 64 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. |  | Mar 20 2019 | On 07/11/2019: Not Corrected On 12/01/2021: The issue still remains inside the channel. On 26-Oct-2021: Not Corrected. On 03/11/2022: Corrected. No splicing has been observed during inspection. | 1 Month | Corrected
Follow Up Inspection |  | 65 | New Finding: Distribution boards have no clear identification markings. Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible location. Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) must be ensured. | Done | Mar 20 2019 | On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 66 | New Finding: Combustible materials are tied with cable ducts. | Combustible materials shall be removed from electrical system. | Done | Mar 20 2019 | On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 67 | New Finding: Circuit breaker rating is not identifiable. | Replace the old breaker with a new one so that anyone can know the ampacity of the breaker. | Done | Mar 20 2019 | On 07/11/2019: Corrected. On 12/01/2021: Circuit breaker shall be replaced with a new one that does not have capacity information. | 1 Month | Corrected
Follow Up Inspection |  | 68 | New Finding: Power cables are hanging without proper support. | Power cables must be supported by cable tray (ladder where needed). Outdoor arrangement must be covered. | We have ensured proper joining accordingly. | Mar 20 2019 | On 07/11/2019: Not Corrected. On 12/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 69 | New Finding: Hot spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. |  | Mar 20 2019 | On 07/11/2019: Not Corrected. On 12/01/2021: The number of hot spots has been reduced but the issue is not completely removed. On 26-Oct-2021: Not Corrected. On 03/11/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 70 | New Finding: Wiring among different floors using flexible/rigid PVC pipe this arrangement does not have any support for cables. | A cable ladder must be used; if it is routed through outside wall, either the cable ladder must be covered or a cable duct must be used. |  | Mar 20 2019 | On 07/11/2019: Not Corrected. On 12/01/2021: Still need to work on this issue. On 26/10/2021: Not Corrected. On 03/11/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 71 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Done | Mar 20 2019 | On 07/11/2019: Corrected. On 12/01/2021: Wiring shall be done in such a way that temperature from any heat source is not transferred into the cables. | 1 Month | Corrected
Follow Up Inspection |  | 72 | New Finding: Safety program is initiated but has no influence in the factory. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. | We have provided awareness training to electrical person and the are using tools properly. | Mar 20 2019 | On 07/11/2019: Not Corrected. On 12/01/2021: Safety training content need to document. For electrical work insulated tools shall be used. On 26-Oct-2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 73 | New Finding: Flexible PVC pipe is used to cover power and signal cable for boiler. | Power and signal cable for boilers shall be distributed using proper type insulator to avoid damage of cables. | Done | Mar 20 2019 | On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 74 | New Finding: Cables inside distribution board are disorganized. | Cables inside each distribution board shall be well organized to avoid misleading during any troubleshooting. distribution board's form is appreciated. | Done | Mar 20 2019 | On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 75 | New Finding: Cable trench is found wet or filled with water. | Cable trench must be kept always dry, and shall be covered by checkered plate. | Done | Mar 20 2019 | On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 76 | New Finding: HT cable dropping from 11 kv overhead line wire is used instead of drop out fuse. | Replace the wire with standard drop out fuse. | Done | Mar 20 2019 | On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 77 | New Finding: Electric boiler feed pump has inadequate/no earthing connection. | Each electrical installation must have proper earth connection. | Done | Mar 20 2019 | On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 78 | New Finding: Cable tray is overloaded with excessive cables; eventually top cover has no effectiveness. | Proper sized cable tray must be installed; a perforated one is better and 20-25% space in cable tray/duct shall be kept free. |  | Mar 20 2019 | On 07/11/2019: Not Corrected. On 12/01/2021: The channel immediately after the panel board is found overloaded. Outdoor cable tray/ladders shall be covered properly to avoid seasonal effect on cables and its longevity. On 26-Oct-2021: Not Corrected. On 03/11/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 79 | New Finding: Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07 m) around the transformer (and related electrical installations) must be maintained. | We are working to ensure required space. | Mar 20 2019 | On 07/11/2019: Not Corrected. On 12/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 80 | New Finding: Indicator lights, ammeter & voltmeter are mounted without control device. | Indicator lights, ammeter & voltmeter should be connected by control device such as rated fuse or MCB. | Done | Mar 20 2019 | On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 81 | New Finding: Outdoor panel is not properly IP rated. | Outdoor panel shall be properly IP rated. | Done | Mar 20 2019 | On 07/11/2019: Corrected. Panel has been removed. | 1 Month | Corrected
Follow Up Inspection |  | 82 | New Finding: Cable duct/channels are filled with fluffs (lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Done | Mar 20 2019 | On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 83 | New Finding: Oil leakage from transformer has been observed. | Oil leakage from transformer must be stopped and top of transformer must also be kept clean. | Done | Mar 20 2019 | On 07/11/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 84 | New Finding: Wiring inside the storeroom is not secured. | Secure cabling shall be ensured in storeroom (use electrical connection through secure path e.g. GI steel pipe and you may keep switch outside of the room; 50-150 lux shall be ensured in the store/ warehouse depending on its usage rate per day). |  | Dec 31 2019 | On 12/01/2021: Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. On 26/10/2021: Not Corrected. On 03/11/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 85 | New Finding: Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. |  | Dec 9 2021 | On 03/11/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 86 | New Finding: Electrical distribution board/panels are adjacent to water source. Power distribution board is found inside store room. | Electrical distribution board/panels must not be installed within 2.5 meter of any water source. Electrical distribution panel/board should be separated from store room or it could be shifted to outside of the store area. |  | Dec 9 2021 | On 03/11/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 87 | New Finding: Uninsulated busbars used inside electrical distribution panel. | Electrical busbar need to be insulated with proper type of insulating materials. In this case it may be used by heat shrink insulating rubber boots | We have already ensured insulated busbar inside the electrical distribution panel. | Dec 3 2022 | On 05/04/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 88 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | We have already rearranged equipment to correct the issue. | Dec 3 2022 | On 05/04/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 89 | New Finding: Uncovered/perforated type cable tray/PVC pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Done. We have removed electrical wiring from that area. | May 9 2023 | On 31/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 90 | New Finding: Insulation resistance test of electrical power cables is not performed for all cables. | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). |  | Mar 5 2024 | On 02/07/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 91 | New Finding: Outdoor cables are not covered to protect from weather effect. | Outdoor cable tray/ladders shall be covered properly to avoid seasonal effect on cables and its longevity. |  | Mar 5 2024 | On 02/07/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 92 | New Finding: Individual protection is found oversized where motor load more than 376 W. | Every electric motor having a rating exceeding 0.376 kW shall be provided with individual control equipment incorporating means of protection against overcurrent. |  | May 8 2026 |  | 2 Months | In Progress

## Boiler
Date
31-Mar-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | M.M. Knitwear Ltd., Ambagh Road, Konabari, Nilnagar, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2022-09-19
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 11921 | No emergency stop push switch was available near the entrance outside of the boiler room. | An emergency stop push switch must be installed outside of the boiler room near the entrance door. | Done. We have already installed emergency switch outside of the boiler room near the entrance door. | Jan 22 2024 | On 16-Jul-25: Corrected. | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 2 | BB 7858 | No emergency stop push switch was available near the entrance outside of the boiler room. | An emergency stop push switch must be installed outside of the boiler room near the entrance door. | Done. We have already installed emergency switch outside of the boiler room near the entrance door. | Jan 22 2024 | On 16-Jul-25: Corrected. | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 3 | BB 7045 | No emergency stop push switch was available near the entrance outside of the boiler room. | An emergency stop push switch must be installed outside of the boiler room near the entrance door. | Done. We have already installed emergency switch outside of the boiler room near the entrance door. | Jan 22 2024 | On 16-Jul-25: Corrected. | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 4 | BB 11921 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Done. We have makred for low low water level beside the gauge glass. | Jan 22 2024 | On 16-Jul-25: Corrected. | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 5 | BB 7858 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Done. We have makred for low low water level beside the gauge glass. | Jan 22 2024 | On 16-Jul-25: Corrected. | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 6 | BB 7045 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Done. We have makred for low low water level beside the gauge glass. | Jan 22 2024 | On 16-Jul-25: Corrected. | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 7 | BB 7858 | Necessary technical documents (except boiler operational & maintenance logbook, flue gas analysis report) are not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, boiler operational & maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of boiler. | Done. We have already collected all required documentation. | Jan 22 2024 | On 16-Jul-25: Corrected. | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 8 | BB 7045 | Necessary technical documents (except boiler operational & maintenance logbook, flue gas analysis report) are not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, boiler operational & maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of boiler. | Done. We have already collected all required documentation. | Jan 22 2024 | On 16-Jul-25: Corrected. | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 9 | BB 11921 | Necessary technical documents (except boiler operational & maintenance logbook, flue gas analysis report) are not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, boiler operational & maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of boiler. | Done. We have already collected all required documentation. | Jan 22 2024 | On 16-Jul-25: Corrected. | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 10 | BB 7045 | Visual flame monitoring glass is broken/out of order. | The visual flame monitoring glass shall be replaced with an appropriate one. | Done. We have already replaced visual flame monitoring glass. | Dec 22 2023 | On 16-Jul-25: Corrected. | 1 MONTH | Corrected
Initial Inspection | External visual inspection | 11 | BB 11921 | Fuel line connection is not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | Done. We have already fuel line connections teminated outside of the boiler room | Jan 22 2024 | On 16-Jul-25: Corrected. | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 12 | BB 7045 | Fuel line connection is not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | Done. We have already fuel line connections teminated outside of the boiler room | Jan 22 2024 | On 16-Jul-25: Corrected. | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 13 | BB 7858 | Steam line connection is not terminated properly | Any unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | Done. We have already insulated steam line properly. | Jan 22 2024 | On 16-Jul-25: Corrected. | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 14 | BB 7045 | Steam line connection is not terminated properly | Any unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | Done. We have already insulated steam line properly. | Jan 22 2024 | On 16-Jul-25: Corrected. | 2 MONTHS | Corrected
Followup Inspection | Functional test inspection | 15 | BB 7045 | New Finding: The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. |  | Aug 16 2025 |  | 1 MONTH | In Progress
Followup Inspection | Functional test inspection | 16 | BB 7858 | New Finding: The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. |  | Aug 16 2025 |  | 1 MONTH | In Progress