## Structural
Date
18-Apr-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Mango Tex Limited, Hossain Plaza 2 ,Tungabari, ashulia,Savar Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2025-09-23
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | High stress in the foundation, considering BNBC prescribed floor live loads, which require immediate design review (Production Building). | As part of the DEA, the building engineer is required to review the design, loads, and foundation stresses. | We will conduct an immediate design review (production building) for the high stresses in the foundation, considering the BNBC specified floor live loads. | Dec 31 2025 | The timeline is acceptable. Submit the necessary documents to RSC for review within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 2 | High stress in the foundation, considering BNBC prescribed floor live loads, which require immediate design review (Production Building). | Verify the in-situ concrete strength of the footing. Also, confirm the concrete test report of the retrofitted column. | We will verify the in-situ concrete strength of the footing. Also, we will confirm the concrete test report of the retrofitted column. | Dec 31 2025 | The timeline is acceptable. Submit the necessary documents to RSC for review within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 3 | High stress in the foundation, considering BNBC prescribed floor live loads, which require immediate design review (Production Building). | Produce and actively manage the loading plan according to the floor, column & foundation capacity. | We will create and proactively manage the loading plan according to the capacity of the floor, column and foundation. | Dec 31 2025 | The timeline is acceptable. Submit the necessary documents to RSC for review within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 4 | High stress in the foundation, considering BNBC prescribed floor live loads, which require immediate design review (Production Building). | Implement remediation work after acceptance from RSC. | We will implement the renovation work after receiving it from RSC. | Apr 30 2026 | The timeline is acceptable. | within 6 months | In Progress
Initial Inspection |  | 5 | High stress in the foundation, considering BNBC prescribed floor live loads, which require immediate design review (Production Building). | Implement floor load plan. | We will implement the floor load plan. | Apr 30 2026 | The timeline is acceptable. Submit the necessary documents to RSC for review within this timeline. | within 6 months | In Progress
Initial Inspection |  | 6 | The load plan and design report don’t comply with BNBC 2006 (Production Building). | The building engineer is required to update the live load plan as per BNBC 2006. | We will update the live load plan as per the Building Engineer's BNBC 2006. | Dec 31 2025 | The timeline is acceptable. Submit the necessary documents to RSC for review within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 7 | Discrepancy/missing information in the as-built (Production Building). | The building engineer is required to survey the whole structure and produce an accurate & detailed as- built drawing. | We will have a structural engineer survey the entire structure and create an accurate and detailed construction drawing. | Dec 31 2025 | The timeline is acceptable. Submit the necessary documents to RSC for review within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 8 | Discrepancy/missing information in the as-built (Production Building). | Remove the undocumented steel frame from the roof. | We will remove the uncertified steel frame from the roof. | Dec 31 2025 | The timeline is acceptable. Submit the necessary evidence to RSC within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 9 | Crack and dampness on the wall (Production Building). | Identify all areas and repair cracks with a suitable method. | We will mark all the areas and repair the cracks using appropriate methods. | Dec 31 2025 | The timeline is acceptable. Submit the necessary evidence to RSC within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 10 | Crack and dampness on the wall (Production Building). | Identify all areas and repair dampness with a suitable method. | We will identify all areas and repair the damp conditions using appropriate methods. | Dec 31 2025 | The timeline is acceptable. Submit the necessary evidence to RSC within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 11 | Non-structural elements found unbraced/unanchored (Production Building). | The building engineer is required to brace/anchor all non-structural elements. | All non-structural components will be attached/connected by our building engineer. | Dec 31 2025 | The timeline is acceptable. Submit the necessary evidence to RSC within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 12 | Water ponding/vegetation on the roof slab (Production Building). | Remove vegetation, apply a proof layer, and improve the drainage system on the roof slab. | We will remove vegetation, apply a resistant layer, and improve drainage on the roof slab. | Dec 31 2025 | The timeline is acceptable. Submit the necessary evidence to RSC within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 13 | Stacking of construction material on the roof slab (Production Building). | The building engineer is required to remove the construction material from the roof slab. | We will remove the piles of construction materials (production buildings) on the roof slabs. | Dec 31 2025 | The timeline is acceptable. Submit the necessary documents to RSC for review within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 14 | Column plaster damaged due to trolley impact (Production Building). | Repair damaged plaster and provide a column guard. | We will repair damaged plaster and provide a column guard. | Dec 31 2025 | The timeline is acceptable. Submit the necessary evidence to RSC within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 15 | Cut off truss/inadequate member size and connection, Shed-1 (Utility Shed-1). | Insert the cut-off members into the truss. | We will insert the cut parts into the truss. | Dec 31 2025 | The timeline is acceptable. Submit the necessary evidence to RSC within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 16 | Cut off truss/inadequate member size and connection, Shed-1 (Utility Shed-1). | The building engineer is required to check the member and connection adequacy as part of the safety check report, submit it to RSC for review. | We will have the building engineer test the adequacy of members and connections as part of the safety inspection report, which we will submit to the RSC for review. | Dec 31 2025 | The timeline is acceptable. Submit the necessary documents to RSC for review within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 17 | Cut off truss/inadequate member size and connection, Shed-1 (Utility Shed-1). | Implement remediation work after acceptance from RSC. | We will implement the renovation work after receiving it from RSC. | Apr 30 2026 | The timeline is acceptable. | within 6 months | In Progress
Initial Inspection |  | 18 | Inadequate member size and connection of the steel part (Shed-2: Utility Shed-2). | The building engineer is required to check the member and connection adequacy as part of the safety check report, submit it to RSC for review. | We will have the building engineer test the adequacy of members and connections as part of the safety inspection report, submitting it to the RSC for review. | Dec 31 2025 | The timeline is acceptable. Submit the necessary documents to RSC for review within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 19 | Inadequate member size and connection of the steel part (Shed-2: Utility Shed-2). | Implement remediation work after acceptance from RSC. | We will implement the renovation work after receiving it from RSC. | Apr 30 2026 | The timeline is acceptable. | within 6 months | In Progress
Initial Inspection |  | 20 | Crack on the brick wall (Shed- 2: Utility Shed-2). | The building engineer is required to repair cracks with a suitable method. | We will have the cracks repaired by a building engineer using appropriate methods. | Dec 31 2025 | The timeline is acceptable. Submit the necessary evidence to RSC within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 21 | Inadequate member size and connection (Shed-3: Security & Doctors' Room). | The building engineer is required to check the member and connection adequacy as part of the safety check report, submit it to RSC for review. | We will have the building engineer test the adequacy of members and connections as part of the safety inspection report, submitting it to the RSC for review. | Dec 31 2025 | The timeline is acceptable. Submit the necessary documents to RSC for review within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 22 | Inadequate member size and connection (Shed-3: Security & Doctors' Room). | Implement remediation work after acceptance from RSC. | We will implement the renovation work after receiving it from RSC. | Apr 30 2026 | The timeline is acceptable. | within 6 months | In Progress
Initial Inspection |  | 23 | Dampness and vegetation on the brick wall of Shed-3 (Security & Doctors' Room). | Remove vegetation and repair dampness with a suitable method. | We will remove the plants and repair the moisture in an appropriate manner. | Dec 31 2025 | The timeline is acceptable. Submit the necessary evidence to RSC within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 24 | Slab supported on a 125 mm thick brick wall (Fire Pump Room). | The building engineer is required to check the adequacy of the brick wall. | We will have the building engineer check the adequacy of the brick walls. | Dec 31 2025 | The timeline is acceptable. Submit the necessary documents to RSC for review within this timeline. | within 6 weeks | In Progress
Initial Inspection |  | 25 | Slab supported on a 125 mm thick brick wall (Fire Pump Room). | Implement remediation work after acceptance from RSC. | We will implement the renovation work after receiving it from RSC. | Apr 30 2026 | The timeline is acceptable. Submit the necessary documents to RSC for review within this timeline. | within 6 months | In Progress
Initial Inspection |  | 26 | Lack of structural drawing (Shed-1, Shed-2, Shed-3, Fire Pump Room). | The building engineer produces a full set of as-built drawings, including structural drawings. | The building engineer will create a set of fully constructed drawings, including structural drawings. | Dec 31 2025 | The timeline is acceptable. Submit the necessary documents to RSC for review within this timeline. | within 6 weeks | In Progress

## Fire
Date
18-Apr-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Mango Tex Limited, Hossain Plaza 2 ,Tungabari, ashulia,Savar Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2025-09-23
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Rooms used for storage of combustible materials are not separated from the surrounding occupancy(production) Location: First floors of the production building Non-compliance reason: Unprotected opening & installed non-listed fire doors. | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour construction in accordance with section 3.4.2.1.5 of RSC Technical Guideline (Standard). | We will separate rooms used for storing flammable materials from surrounding occupants (production) and build the rooms in accordance with Section 3.4.2.1.5 of the RSC Technical Guidelines. Location: First floors of the production building. | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 2 | Areas used for in-process storage of combustible materials are open to the surrounding occupancy. Location: Ground , 2nd,3rd & 4th floor of the Production building | Provide defined storage areas and limit the storage arrangement as follows: Maximum height of 2.45 m and maximum area of 23 m² and is separated by a minimum 3.0 m (10ft) from other storage areas and they do not exceed 10 percent of the building area of the story in which they occur. or, If sprinkler protected, Maximum height 12 ft (3.66 m) and maximum area of 1000 ft² (93 m²) and separated by a at least 25 ft (7.62 m) and does not constitute more than 10 percent of the building area or 4000 ft² (372 m²) of the sprinklered area, whichever is greater. or, Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | We will separate the spaces used for storing flammable materials from the surrounding residents, in accordance with the technical guidelines of the RSC. Location: Ground, second, third and fourth floors of the production building" | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 3 | Boiler equipment is not properly separated by fire rated construction from the adjacent Building. Location: Shed-2(Utility-2). Adjacent of the production Building. | Boilers or other heat producing equipment shall be separated from other occupancies by a minimum 1-hr fire rated construction (wall, floor, slab etc.). Seal all penetrations and openings (door, window etc.) should be protected by 0.75-hr (45 min) fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. Or Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. Boiler room separation shall meet section 3.4.2.1.2 of RSC Technical Guideline (Standard) . | We will properly separate boilers and other heat-generating equipment from adjacent buildings through fire-resistant construction in accordance with RSC Technical Guidelines . Location: Shed-2(Utility-2). Adjacent of the production Building. | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 4 | The required fire separation distance for Building-01(production) does not comply with the requirements of BNBC 2006 Location: South side, east side & west side of the production building. | The exterior walls shall have a fire resistance and opening protection as specified in BNBC 2006, Tables 3.2.2 and Part 3 Section 2.4.1.3. | We will provide fire prevention and opening protection as specified in BNBC 2006, Table 3.2.2 and Part 3 Section 2.4.1.3 on the external walls of Building-01 (Production). Location: South side, East side and West side of the Production Building." | Apr 30 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 6 Months | In Progress
Initial Inspection |  | 5 | Compressor/heat producing equipment is not properly separated by fire rated construction. Location: Under exit stair on Ground floor of the production building. | Compressor or other heat producing equipment shall be separated from other occupancies by a minimum 1-hr fire rated construction (wall, floor, slab etc.). Seal all penetrations and openings (door, window etc.) should be protected by 0.75-hr (45 min) fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. Or Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. Boiler room separation shall meet section 3.4.2.1.2 of RSC Technical Guideline (Standard) . | "We will properly isolate compressor/heat generating equipment by constructing fire extinguishers. Location: Under the exit stairs on the ground floor of the production building." | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 6 | The fire pump room is not provided with adequate fire separation. Location: Fire pump room Non-compliance reason: Unprotected opening(distance 5 feet) from production on ground floor west side | Provide fire pump room with 2 hr. rated fire separation when building is not fully sprinklered and 1 hr. rated fire separation when the building is provided with automatic sprinklers in accordance with NFPA 13. Or, Physically separate the pump room from the protected building by a minimum of 50 ft. (15.3 m) in accordance with NFPA 20. Provide direct access from the outside or provide a 2-hr enclosed passageway from an enclosed stairway or exterior exit. | We will provide a fire separation system for the fire pump room with adequate fire separation. The pump room shall be constructed at least 50 feet (15.3 meters) from the protected building in accordance with NFPA 20 and shall provide direct access from the outside. Location: Fire Pump Room | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 7 | Storages were found underneath the cutting tables. Location: Ground & 2nd floors of the production building. | Storage underneath the cutting tables shall be kept clear of combustibles at all time, except as provided for miscellaneous storage in accordance with 3.4.2.1.6 or , Where an automatic sprinkler system is installed sprinklers are required to be installed beneath cutting tables greater than 4 ft in width that are used for storage of combustibles. | Done | Jan 31 2026 | Remediation evidence wa not provided. The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 8 | Penetrations through floor/ceiling assemblies are found unsealed. Location: All floor of the production buildings Non-compliance reason: Unseal penetration Through the electrical cable riser | Seal all penetrations and openings in floor/ceiling assemblies by a listed through-penetration fire stop system tested in accordance with ASTM E814 or approved alternative standard to maintain minimum 3-hr./ 2-hr. fire resistance rating. Installation shall be as per manufacturer published installation guideline and the certification authority guideline to ensure the fire-rating in accordance with section 4.7 of RSC Technical Guideline (Standard) Or, Provide a minimum 2-hr fire rated shaft to separate the penetration from each floor if required. | We will seal items that enter through the floor/ceiling assembly. Location: All floors of the manufacturing building | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 9 | Penetrations through floor/ceiling assemblies are found unsealed. Location: All floor of the production buildings Non-compliance reason: Unseal penetration through the Plumbing plastic pipe | Seal all penetrations and openings in floor/ceiling assemblies by a listed through-penetration fire stop system tested in accordance with ASTM E814 or approved alternative standard to maintain minimum 3-hr. fire resistance rating. Installation shall be as per the manufacturer's published installation guidelines and the certification authority guideline to ensure the fire-rating in accordance with section 4.7 of RSC Technical Guideline (Standard) Or, Provide a minimum 2-hr fire rated shaft to separate the penetration from each floor if required. | We will seal items that are inserted through the floor/ceiling assembly. Location: All floors of the manufacturing building | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 10 | Liquefied or compressed gas cylinders were located within the factory without adequate fire separation. Location: North side of production building Available Fire Separation distance: Adjacent of shed-2(boiler room) | Remove the liquefied or compressed flammable gas cylinders. The storage or use of liquefied or compressed flammable gas (LPG/CNG) cylinders within the factory building as per section 3.4.2.1.11 of RSC Technical Guidelines (Standard)¹ V1.0. Or, Factory shall follow the requirements RSC Published "SUPPLEMENTARY PAPER ON TECHNICAL GUIDANCE NOTE FOR USE OF LIQUIFIED OR COMPRESSED FLAMMABLE GAS IN FACTORY PREMISES" to use or store liquefied or compressed flammable gas cylinders in the factory premises. | We will remove liquefied or compressed flammable gas cylinders. We will store or use liquefied or compressed flammable gas (LPG/CNG) cylinders inside the factory building in accordance with Section 3.4.2.1.11 of RSC Technical Guidelines (Standards)¹ V1.0. | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 11 | Dining (E4 occupancy) area is not separated from store (H2 occupancy) with fire rated assemblies. Location: First floor of the production building. | Separate the dining area from other occupancies with 3-hr fire rated construction, provide minimum 3-hr. rated doors for the openings and seal the unprotected penetrations. Provide required exits that lead directly to the street or exit stairwell or leading to a corridor or open space. | We will separate the dining (E4 occupancy) area from the store (H2 occupancy) with a fire escape. Location: First floor of the production building." | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 12 | Unprotected openings in the exterior wall in two consecutive floors lying within 1.5 m and vertical spread of fire is not restricted. Location: West side of the production building | Provide flame barriers as similar as sunshades or cornices or projected wall at least 750 mm from the external face of the exterior wall. The flame barrier shall have a fire resistance rating of not less than three-fourths hour. For Interim Building, BNBC 2006 Part III chapter 3 clause 3.1.7.2 | We will limit the unprotected open space and vertical spread of fire within 1.5 metres of the external walls of two consecutive floors. Location: West side of the production building | Apr 30 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 6 Months | In Progress
Initial Inspection |  | 13 | The day-care room does not separated from other occupancy (Cooking area) Location: Shed-3. Adjacent of production building(Ground floor W-S side ) under same roof. | Separate the day-care from other occupancy ac per Table 3.2.1 (BNBC 2006) | We will separate the daycare room from the other residents (cooking area). Location: Shed-3. Next to the production building under the same roof (ground floor W-S side)." | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 14 | The exit stair enclosures are not separated from work areas and other spaces on each floor by fire-rated construction. Location: All three exit stairs of the production building. Non- compliance : 1. Due to unprotected opening at all floors of the east side stair 2. Non-listed fire doors of the W-N & W-S side of the all stairs | The exit stair enclosure shall be provided with a minimum of 2- hr. fire resistance rating for buildings 4 or more stories. Provide 1.5 hr. fire rated door and seal all penetrations and openings by 2 hr. fire rated fire rated barrier construction for building with 4 or more stories in accordance with section 6.3.1.2 of RSC Technical Guidelines (Standard)¹ V1.0. Provide a fire-resistive rated assembly between the exterior exit stairs and the building up to 10 ft. beyond the end of the stair to achieve the required separation. The rated assembly shall be approved and/or designed by a qualified fire protection engineer. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. Keep proper datasheet & certifications for installed fire doors & accessories on-site for verification. The clearance under the bottom of a door shall be a maximum of 3⁄4 in. (19 mm).. | We will separate the exit stairwells from the work area and other areas on each floor by constructing fireproofing. | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 15 | Unsealed penetrations and openings are located in exit stair enclosures. Electrical cable passing through the exit enclosure. Location(s): W-N side exit stair on ground floor of the production building | No other penetration into and through the exit enclosure except for fire alarm equipment electrical raceway, required exit doors, sprinkler piping, standpipes, and electrical conduit serving the exit enclosure is permitted in accordance with section 6.14.4 of RSC Technical Guidelines (Standard)¹ V1.0. So, relocate the electrical wires/raceways to somewhere else avoiding the exit enclosure, and seal the created unprotected openings with a minimum of 1.5 hours listed/certified fire-rated materials. Installation shall be as per manufacturer published installation guideline and the certification authority guideline to ensure the fire-rating. Or seal the penetration by 2-hr masonry construction. | We will relocate electrical wires/raceways to avoid exit enclosures and seal exposed openings created with a minimum of 1.5 hour listed/certified fire-rated materials. | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 16 | Storage areas rooms and similar normally unoccupied spaces discharges directly into the exit stair enclosure. Location(s): Basement & 1st floor of the production building | Openings from exit enclosure to Storage areas/ basements/ transformer rooms/ generator rooms/ boiler rooms and similar normally unoccupied spaces shall be provided with a vestibule with fire rated construction and openings in accordance with section 6.14.3 of RSC Technical Guidelines (Standard)¹ V1.0. Provide a min 1-hr fire rated door on the exit stair side and a 1.5 hr./1-hr fire rated door on the Store, generator, sub-station room side . Ensure that the fire rating of the vestibule construction matches that of the exit stair enclosure as per RSC Technical Guidelines (Standard)¹ V1.0. section 6.14.3. The minimum width for vestibules shall not be less than 1.1m and length 1.8m. | We will construct fire-fighting structures in open spaces from exit enclosures to storage areas/basements/transformer rooms/generator rooms/boiler rooms and similar generally vacant spaces and install a vestibule in open spaces as per clause 6.14.3 of RSC Technical Guidelines (Standard)¹ V1.0. | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 17 | The egress path along means of egress has interrupted by obstruction/storage/process work Location: Basement , ground floor of the production building | Keep egress paths and stairs clear of storage/obstruction in accordance with section 6.3.9 of RSC Technical Guidelines (Standard)¹ V1.0. Means of egress shall be maintained continuously free and clear of all obstructions or impediments to full instant use in the case of fire or other emergency. No furnishings, decorations, or other objects shall obstruct exits and access to exits. Nothing shall obstruct or impede visibility to exits. | Done | Oct 30 2025 | Remediation evidence was not provided. The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. RPO Comments: On 8-Apr-2026 the factory management reported the remediation completion and shared evidence which were found credible. This item will be verified in the next inspection. | Immediately | Pending Verification
Initial Inspection |  | 18 | Storage were located in the exit stair/stair enclosure. Location: Exit stair-1 ,2 & 3 of the production Building | Remove all storage from exit stairs and egress path in accordance with section 13.8 of RSC Technical Guidelines (Standard)¹ V1.0. Means of egress shall be maintained continuously free and clear of all obstructions or impediments to full instant use in the case of fire or other emergency. No furnishings, decorations, or other objects shall obstruct exits and access to exits. Nothing shall obstruct or impede visibility to exits. | Done | Oct 30 2025 | Remediation evidence was not provided. The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. RPO Comments: On 8-Apr-2026 the factory management reported the remediation completion and shared evidence which were found credible. This item will be verified in the next inspection. | Immediately | Pending Verification
Initial Inspection |  | 19 | The egress court is less than 10 ft wide and is not separated from the building interior which is not in accordance with section 6.17.2 of RSC Technical Guidelines (Standard)¹ V1.0. Location: West side of the production building. | Egress courts less than 3050 mm (10 ft) in width (as measured from the building and the adjacent property line) shall be provided with walls having a 1-hr fire resistance rated construction for a distance of 3050 mm (10 ft) above the floor of the court. Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft. to provide a minimum 1-hr fire separation. | We will make egress courts 3050 mm (10 feet) wide (measured from the building and adjacent property lines) and place 1-hour fire-rated walls 3050 mm (10 feet) away from the court floor. We will seal all building entrances and openings along the egress route to a height of 10 feet. | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 20 | Aisles were found missing on several locations throughout the building. Location: First & 2nd of the production building | Provide minimum aisle widths of 36-in. Aisles mark shall be clearly visible. | Done | Dec 31 2025 | Remediation evidence was not provided. The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 month | In Progress
Initial Inspection |  | 21 | Doors along means of egress are provided with non-compliant locking devices. Location: First floor of the production & Main exit gate . | Remove locking devices from all egress devices in accordance with section 6.8.2 of RSC Technical Guidelines (Standard)¹ V1.0. No locks or other devices shall be installed on a means of egress component that would prevent any occupant from having safe egress from the building or structure and doors shall not be locked in the direction of egress under any conditions. All hasps, locks, slide bolts, and other locking devices are prohibited unless meet the following conditions: • Doors may be locked where the latch and lock are disengaged with one motion where the occupant load does not exceed 49 persons. Turning a door handle and disengaging a lock is considered two motions. • Doors may be provided with locking hardware from the ingress side provided that a panic bar is installed on any door with an occupant load exceeding 49 persons. | Done | Oct 30 2025 | Remediation evidence was not provided. The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. RPO Comments: On 8-Apr-2026 the factory management reported the remediation completion and shared evidence which were found credible. This item will be verified in the next inspection. | Immediately | Pending Verification
Initial Inspection |  | 22 | Doors in the means of egress do not have the required minimum width. (Available Width: 36in) Location: All floors of the exit stair-3 east side of the production & pocket gate of the main gate | Doors in a means of egress shall have a minimum width of 1 m (39 in.). in accordance with section 6.5.6.1 of RSC Technical Guidelines (Standard)¹ V1.0. | We will ensure that exit doors are at least 1 metre (39 inches) wide, in accordance with Section 6.5.6.1 of the RSC Technical Guidelines (Standards)¹ V1.0. | Dec 31 2025 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 23 | Egress door serving 50 or more occupants but does not swing in the direction of egress travel. Location: Main Exit gate on ground level of the building. | Modify swing direction of egress doors to the direction of egress travel. Doors serving an occupant load of more than 50 shall swing in the direction (out-ward) of egress travel in accordance with section 6.8.1 of RSC Technical Guidelines (Standard)¹ V1.0. | We will change the swing direction of the exit doors to the direction of departure travel. Doors carrying more than 50 passengers shall swing in the direction of departure travel (outwards) as per Section 6.8.1 of RSC Technical Guidelines (Standards)¹ V1.0. | Dec 31 2025 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 24 | Exit stair(s) terminates the occupants inside the building which does not comply with section 6.17 of RSC Technical Guidelines (Standard)¹ V1.0. Location: Production building Level of Discharge: East side exit stair at ground floor | Exits shall discharge directly to the exterior of the building unless meeting the requirements of 6.17.2 or 6.17.3 as per RSC Technical Guidelines (Standard)¹ V1.0. | We will provide exit stair(s) open to the building, in accordance with Section 6.17 of RSC Technical Guidelines (Standards)¹ V1.0. Location: Production Building. Level of Exit: East Exit Stairs | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 25 | Stair clear width was found less than 60 in. Location: Basement level at West-South side exit stair & east side exit stair all floors. Available Stair Width: 40inch & 46inch. | Stairs shall have a minimum clear width of 60 in. in for all industrial occupancies as per RSC Technical Guideline (Standard) section of 6.5.6 | We will make the minimum clear width of stairs for all industrial occupancies 60 inches, in accordance with RSC Technical Guidelines (Standards) Section 6.5.6. | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 26 | Doors are swing out over aisles. Location: Basement level of the production building. | A landing shall be provided on both sides of doors used in the means of egress to facilitate uninterrupted egress of occupants. Door shall not swing out over stairs. Landings with same width as the stair clear width shall be provided at each level and at intermediate landings. | To facilitate the smooth exit of employees, we will provide landings on both sides of the exit doors. There will be landings of equal width to the stairs at each level and intermediate landings. | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 27 | Fire evacuation maps are not updated as per site condition. Location: Production Building & all other structures. | Update the fire evacuation map and shall be posted at the entrance to each exit stair in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 13.3. | Done | Dec 31 2025 | Remediation evidence was not provided. The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 28 | Building does not have occupant load signs at required locations on all floors. Location: All exit stair of the production Building. | Post the occupant load for every assembly and production floor in a facility in a conspicuous space near the main exit or exit access doorway for the space in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.4.4 . | Done | Dec 31 2025 | Remediation evidence was not provided. The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 month | In Progress
Initial Inspection |  | 29 | Exit signage/directional signage not illuminated during testing (burned out, broken, etc.). Location: Production Building. | Regularly inspect all exit signage/directional signage as per RSC Technical Guidelines (Standard)¹ V1.0. and replace/install lights as needed to illuminate signs. | Done | Dec 31 2025 | Remediation evidence was not provided. The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 30 | Emergency lights not illuminated during testing (burned out, broken, etc.). Location: Production building. | Regularly inspect all emergency lighting system as per RSC Technical Guidelines (Standard)¹ section 13.12 and replace/install lights as needed to illuminate signs. | Done | Dec 31 2025 | Remediation evidence was not provided. The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 31 | Manual on-off switch is provided for exit signage units. Location: Production building. | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. | Done | Dec 31 2025 | Remediation evidence was not provided. The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 32 | Handrails are not provided on both sides of each exit stairs on all floors. Having handrails on one side of said staircase, may pose as a falling hazard during evacuation. Location: All stairs of the production Building. | Provide handrails on both sides of the exit stair. New handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in.). Open guards shall have intermediate rails or pattern such that a sphere 200 mm (8 in.) in diameter cannot pass through any opening up to a height of 865 mm (34 in.). Handrail shall construct in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.12. | We will provide handrails on both sides of every exit staircase on all floors. | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 33 | Parapets are provide less than 42 inch in occupiable roof. Available Height: 40 inch Location: Production Building. | Provide parapets or guards with a minimum height of 1067mm (42 inch.) in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.12 | We will provide a minimum height of 1067 mm (42 inches) parapet or guard in accordance with RSC Technical Guidelines (Standards)¹ V1.0 Section 6.12. | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 34 | Building does not have stair/floor level designation signs at required locations on all floors. Location: Production Building. | Provide stair designation sign at each floor entrance from the stair to the floor in English and Bengali. Signs shall indicate the name of the stair and the floor level. Signs shall be posted adjacent to the door in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.9.3. | We will provide stair/floor level markings at the necessary locations on all floors of the building. | Dec 31 2025 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 35 | Exit sign not provided at exit. Location: All floor of the exit stair-3(east side) of the Production Building & all other structures. | Lighted exit signs shall be placed at entrance to an exit. Additional directional exit signs shall be placed throughout the facility anywhere the continuation of the egress is not obvious. Lighted exit signs shall be provided with either battery backup or uninterruptable power supply systems and shall be continuously illuminated at all times. Exit Sign shall provide in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.11. | We will install illuminated exit signs at exit entrances. | Dec 31 2025 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 36 | Directional signs are not provided where direction of the path of travel to an exit has changed. Location: Production Building. | Illuminated directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.11.3. | We will provide illuminated directional signs indicating changes in direction of travel and exits in accordance with RSC Technical Guidelines (Standards)¹ V1.0 Section 6.11.3. | Dec 31 2025 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 37 | Sliding type doors have provided along means of egress [building exits, along egress routes]. Location: Ground , first & 3rd floors of the Production Building. | Replace all collapsible/sliding/shutter type doors & gates by the side‐hinged swinging type doors in accordance with section 6.8.1 of RSC Technical Guidelines (Standard)¹ V1.0. All doors in a means of egress shall be of the side‐hinged swinging type. Roll--down and sliding gates and shutters shall not be allowed. Doors serving an occupant load of more than 50 shall swing in the direction of egress travel. | We will replace all collapsible/sliding/shutter type doors and gates with side-hinged swinging type doors as per clause 6.8.1 of RSC Technical Guidelines (Standard)¹ V1.0. | Dec 31 2025 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 38 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. Location: Production building & all other structures. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. Illumination on means of egress shall meet in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 10.12.2. | We will comply with the RSC Technical Guidelines (Standards)¹ V1.0 Section 10.12.2 for exit route lighting. | Jan 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 39 | The factory has installed a fire alarm and detection system that requires a detailed review to confirm compliance with NFPA 72 and RSC Technical Guidelines (Standard). Location: All structures | Submit the fire alarm and detection system design to RSC for review. Once the design is reviewed, install and modify the fire detection and alarm system throughout the building in accordance with review comment, RSC Technical Guidelines (Standard) and NFPA 72. After installation the owner shall conduct internal testing and commissioning and then contact the RSC for witness of final acceptance testing. | We will submit the design of the fire alarm and detection system to the RSC for review. Once the design is reviewed, we will install the fire detection and detection system throughout the building in accordance with the review comments, RSC Technical Guidelines (Standards), and NFPA 72. | Apr 30 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Design within 2 Month and modification/ installation with 4Months | In Progress
Initial Inspection |  | 40 | Inspection, testing and maintenance for the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with NFPA 72 and RSC Technical Guidelines (Standard)¹ V1.0.s. | Inspection, testing, and maintenance of fire suppression systems will be performed in accordance with NFPA 72. | May 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month after installation. | In Progress
Initial Inspection |  | 41 | The required no smoking signs are not present in the factory. | Smoking is prohibited in any garment factory building or separate storage building. Signs shall be posted in Bengali and English at all building entrances. If the factory creates a designated smoking area outside the building, information of these areas will be posted on the signs. Smoking sign shall post in accordance with section 13.5 of RSC Technical Guideline (Standard) | We will post signboards in Bengali and English at all entrances. | Dec 31 2025 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 42 | Fire drills are not conducted according to section 13.2 of RSC Technical Guidelines (Standard)¹ V1.0. | Fire drills shall be conducted according to section 13.2 of RSC Technical Guidelines (Standard)¹ V1.0. Fire drills shall be conducted on a monthly basis as outlined in BNBC 2020 Part 4 Appendix A. | We will conduct fire drills as per clause 13.2 of RSC Technical Guidelines (Standards)¹ V1.0. Fire drills will be conducted on a monthly basis as per BNBC 2020 Part 4 Appendix A. | Dec 31 2025 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 43 | It was observed non listed 40mm hose in the factory. So The factory is require listed standpipe system. Standpipe system is requires a detailed review to confirm compliance with NFPA 14,20, 24 and RSC Technical Guidelines (Standard). | Submit the standpipe system drawing to RSC for review. Once reviewed, install or modify the standpipe system throughout the building in accordance with RSC Technical Guidelines (Standard)¹ V1.0. and NFPA 14, 20,22 and 24. After installation the owner shall contact the RSC for witness of conducting the final acceptance testing of the standpipe system. | I will submit the standpipe system drawing to the RSC for review. After review, I will install or modify the standpipe system throughout the building in accordance with RSC Technical Guidelines (Standards)¹ V1.0. and NFPA 14, 20,22, and 24. | Apr 30 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Design within 2 Month and modification/ installation with 4 Months | In Progress
Initial Inspection |  | 44 | Inspection, testing and maintenance of the standpipe system, sprinkler system & fire pump is not in accordance with NFPA 25. | Inspect, test and maintain the standpipe system, sprinkler system & fire pump and keep written records on-site, in accordance with NFPA 25 and RSC Technical Guidelines (Standard)¹ V1.0.s. | Inspection, testing, and maintenance of standpipe systems, sprinkler systems, and fire pumps shall be performed in accordance with NFPA 25. | May 31 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month after installation. | In Progress
Initial Inspection |  | 45 | It was observed only one non-listed Diesel pump installed in the factory premises. So Listed Fire pump installation requires detailed review to confirm compliance with NFPA 20 and RSC Technical Guidelines (Standard)¹ V1.0. Location: Production Building. | Submit as-built drawings, testing records, equipment certification and other relevant documentation to the RSC for review and approval. Submit the standpipe system drawing to RSC for review. Once reviewed, install or modify the standpipe system throughout the building in accordance with RSC Technical Guidelines (Standard)¹ V1.0. and NFPA 14 and 20. The factory management shall contact RSC to conduct the final acceptance testing after the installation, testing & commissioning. | We will install listed fire pumps in compliance with NFPA 20 and RSC Technical Guidelines (Standards)¹ V1.0. | Apr 30 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Design within 2 Month and modification/ installation with 4 Months | In Progress
Initial Inspection |  | 46 | Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with the RSC Technical Guidelines (Standard)¹ V1.0.. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with the RSC Technical Guidelines (Standard)¹ V1.0. Keep written records on-site. | We will regularly inspect, test and maintain exit signs and emergency lighting systems in accordance with RSC Technical Guidelines (Standards)¹ V1.0. | Dec 31 2025 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 month | In Progress
Initial Inspection |  | 47 | Written housekeeping policy was not found, which is required as per RSC Technical Guideline (Standard) section 13.6. | Establish written corporate and plant policies on housekeeping to ensure scheduled cleaning for floor, wall, ceiling, supply and return air ventilation systems. Promptly reschedule skipped cleanings. Provide a documented line of authority for authorizing a cleaning delay and rescheduling. As a general rule the maximum tolerable deposit thickness for loose fluffy lint is 13 mm (½ in.) over a maximum of 46.5 m2 (500 ft2). Limit dense deposits to 6 mm (¼ in.) and oil saturated deposits to 3.2 mm (⅛ in.). | We will establish written housekeeping policies, which will be in accordance with RSC Technical Guidelines (Standards) Section 13.6. | Dec 31 2025 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 month | In Progress
Initial Inspection |  | 48 | Portable fire extinguishers are not installed throughout all facilities. Location: Production Building. | Install fire extinguishers at locations and heights in accordance with section 5.6 of RSC Technical Guideline (Standard) | We will install fire extinguishers at locations and heights in accordance with Section 5.6 of the RSC Technical Guidelines (Standards). | Dec 31 2025 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 49 | Fire extinguishers were found at several areas but placed on floors. Location: Basement & ground floor of the production Building. | The bottom of the fire extinguisher and the floor be less than 4 in.(102 mm).As per NFPA 10 section 6.1.3.8.3 | We will locate all fire extinguishers in accordance with NFPA 10 Section 6.1.3.8.3. | Dec 31 2025 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 50 | Shutter type doors have provided along means of egress [building exits} Location: Shed-1:(Utility 1) | Replace all collapsible/sliding/shutter type doors & gates by the side‐hinged swinging type doors in accordance with section 6.8.1 of RSC Technical Guidelines (Standard)¹ V1.0. All doors in a means of egress shall be of the side‐hinged swinging type. Roll--down and sliding gates and shutters shall not be allowed. Doors serving an occupant load of more than 50 shall swing in the direction of egress travel. | We will replace all collapsible/sliding/shutter type doors and gates with side-hinged swinging type doors as per clause 6.8.1 of RSC Technical Guidelines (Standards)¹ V1.0. | Dec 31 2025 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 51 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records on- site, in accordance with NFPA 10 and RSC Technical Guidelines (Standard)¹ V1.0.s. | We will inspect, test, and maintain portable fire extinguishers in accordance with NFPA 10. | Dec 31 2025 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 month | In Progress

## Electrical
Date
18-Apr-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Mango Tex Limited, Hossain Plaza 2 ,Tungabari, ashulia,Savar Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2025-09-23
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/less reflection in existing SLD. | As-built Electrical Single Line Diagram (SLD) must be prepared by a qualified engineer, including all essential details of the electrical system. This diagram must be reviewed and approved by the RSC. The accepted SLD needs to be implemented at the factory. All cables, all circuits, all terminals, all equipment are required to be identified as per the accepted Single line diagram. |  | Apr 30 2025 | On 15/03/2026: Not Corrected. Factory got acceptance from RSC on 11 February, 2026 but on site implementation not started yet. Approximately 40% progress observed on this issues. | 6 Months | In Progress
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not installed properly including missing air terminal, non-standard materials, no coverage for highest points & earthing pits not yet constructed. | Factory required to be redesign the Lightning Protection System (LPS) as per standard for the entire facility. Once the LPS is properly designed, it must be installed according to the design specifications to ensure effective protection against lightning strikes. |  | Jan 20 2025 | On 15/03/2026: Not Corrected. The drawing requires modification and the LPS structure has not been completed. Additionally, no protection coverage area calculation was found. Approximately 70% progress observed on this issues. | 3 Months | In Progress
Initial Inspection |  | 3 | Safety program is initiated but has no influence in the factory all electrical personnel. | An electrical safety training and awareness program must be established and documented for all electrical personnel. The objective of this program is to cultivate a positive shift in safety attitudes and behaviors among the team. |  | Nov 20 2025 | On 15/03/2026: Not Corrected. Safety training has been conducted; however, no effective influence has been observed among all electrical personnel in the factory. | 1 Month | In Progress
Initial Inspection |  | 4 | No policies for PPE/LOTO (Lock-Out-Tag-Out) are introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement PPE (Personal Protective Equipment) and LOTO (Lock-Out-Tag-Out) policy using LOTO devices to ensure personnel safety during maintenance activities. All LOTO usage records must be maintained for compliance and safety monitoring. |  | Dec 31 2025 | On 15/03/2026: Corrected. | 1 Month | Corrected
Initial Inspection |  | 5 | There is no programmed schedule for periodical inspection & testing of electrical equipment. | Electrical maintenance program shall be developed to include regular inspections and testing of electrical systems, focusing on preventive and proactive measures. | Done | Nov 20 2025 | On 15/03/2026: Corrected. | 1 Month | Corrected
Initial Inspection |  | 6 | Periodicity of transformer oil test (dielectric strength) survey is not continued. | Testing of transformer oil, specifically the dielectric strength test needs to be conducted at least once in a year from government-authorized entities such as BPDB, BREB, PGCB, EGCB, DESCO, DPDC, or any other designated govt. authority. | Done | Nov 20 2025 | On 15/03/2026: Corrected. | 1 Month | Corrected
Initial Inspection |  | 7 | Earth pit resistance record is not available. | All earthing systems must be tested for resistance on a dry day at least once every two years. Records of each earthing test and its results must be available for inspection when required. |  | Nov 20 2025 | On 15/03/2026: Not Corrected. All pit not constructed yet & test report not matched with actual condition. | 1 Month | In Progress
Initial Inspection |  | 8 | Insulation resistance test of electrical power cables is not performed. | Insulation resistance testing of all cables (excluding those less than 25 sq.mm) must be conducted once every two years and documented. This testing may require power shutdown to ensure accurate results and safety. |  | Nov 20 2025 | On 15/03/2026: Not Corrected. Test report not matched with actual condition. | 1 Month | In Progress
Initial Inspection |  | 9 | Thermography scanning report is not available. | Thermography survey of the entire electrical system must be conducted and documented by bi-annual, including real-time and scanned images with recommendations for corrective actions. This helps identify overheating, loose connections, and safety hazards, preventing equipment failure and reducing downtime. | We will conduct and document thermography surveys of the entire electrical system biannually. | Dec 31 2025 | On 15/03/2026: Not Corrected. Test report is outdated. | 1 Month | In Progress
Initial Inspection |  | 10 | Transformer silica gel is discolored. | Discolored silica gel needs to be changed. |  | Dec 31 2025 | On 15/03/2026: Corrected. | 1 Month | Corrected
Initial Inspection |  | 11 | Transformer breather oil cup is empty. | Transformer breather oil cup must be filled up to the oil-mark on the cup. Ensure the tube inside the breather cup is properly submerged in oil. If it's not, air may bypass the oil seal, reducing the effectiveness of moisture control. |  | Dec 31 2025 | On 15/03/2026: Corrected. | 1 Month | Corrected
Initial Inspection |  | 12 | Lint and dust deposited on and around the transformer. | Transformer top and around it shall be kept neat and clean. | Done | Nov 20 2025 | On 15/03/2026: Corrected. | 1 Month | Corrected
Initial Inspection |  | 13 | Inadequate working space around transformer for performing maintenance work. | Adequate working clearance and proper ventilation must be maintained in accordance with RSC technical guidelines. This ensures the safe operation of electrical systems, prevents cross-contamination between LT and HT sections, and enhances overall safety and operational efficiency. Access needs to be restricted to qualified personnel wearing appropriate PPE (Personal Protective Equipment). | We will maintain adequate work clearances and proper ventilation in accordance with RSC technical guidelines. We will limit access to qualified personnel wearing appropriate PPE (Personal Protective Equipment). | Feb 28 2026 | On 15/03/2026: Not Corrected. The factory is recommended to submit the transformer room layout to the RSC office for review. | 4 Months | In Progress
Initial Inspection |  | 14 | Generator terminal box left open to allow cable entry. | Generator terminal box must have a base plate installed, and cables entering the terminal box must be securely fixed with cable glands. | We will place a base plate on the generator terminal box and securely fix the wires entering the terminal box with cable glands. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 2 Months | In Progress
Initial Inspection |  | 15 | Generator output cables laid on the floor without protection and support. | Service cables from the generator must be adequately supported at their respective breaker terminals and laid with the use of a cable tray. | We will adequately support the generator service cables to their respective breaker terminals using a cable tray. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 1 Month | In Progress
Initial Inspection |  | 16 | Lead acid battery terminals are left open. | Lead-acid battery terminals must be covered, and any rust must be thoroughly cleaned to ensure safe and efficient operation. |  | Dec 31 2025 | On 15/03/2026: Corrected. | 1 Month | Corrected
Initial Inspection |  | 17 | Heat shields missing to protect component and operator from excessive heat. | Install heat shields or blankets to protect components and operators from excessive heat on hot surfaces. After providing shield or blankets, ensure proper guards are installed, except on exhaust manifolds, turbocharger housings etc. Consult with the generator supplier, service provider, or expert before proceeding with the installation. | We, in consultation with the generator supplier, service provider or specialist, will install heat shields or blankets to protect parts and operators from excessive heat from hot surfaces and also install exhaust manifolds, turbocharger housings, etc. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 2 Months | In Progress
Initial Inspection |  | 18 | Distribution board's top/bottom is left open (typical issue). | Each electrical distribution board or panel must be sealed to prevent the ingress of fluffs and dust. Adequate ventilation must also be ensured to maintain optimal operating temperatures. Cable glands should be used where required to secure cables and maintain the integrity of the seal. | We will seal each electrical distribution board or panel. We will also ensure adequate ventilation to maintain optimal operating temperatures. We will use cable glands where necessary to keep cables secure and maintain the integrity of the seal. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 2 Months | In Progress
Initial Inspection |  | 19 | Inadequate working clearance around the generator's. | Minimum working space of 1.07 meters around the generator and related electrical installations must be maintained to ensure safety and accessibility. If multiple generators are installed in the same room, a working space of at least 1.07 meters or the width of the larger generator, whichever is greater, must be maintained for safe operation and maintenance. | We will maintain a minimum working space of 1.07 meters around generators and related electrical installations to ensure safety and accessibility. | Feb 28 2026 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 4 Months | In Progress
Initial Inspection |  | 20 | Oil spillage/leakage has been observed in generator room. | Any oil spillage or leakage around the generator must be promptly stopped, and the generator area must be kept dry at all times to prevent hazards and maintain safe operation. | Done | Nov 20 2025 | On 15/03/2026: Corrected. | 1 Month | Corrected
Initial Inspection |  | 21 | Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | CPR instructions must be posted near all electrical installations (such as LT panels, MDBs, FDBs, DBs, and SDBs) in a clearly visible location. | Done | Nov 20 2025 | On 15/03/2026: Corrected. | 1 Month | Corrected
Initial Inspection |  | 22 | Distribution panel & board is installed without proper grout. | Distribution panels and boards must be installed with proper grouting to ensure a stable and secure foundation, minimizing the risk of movement or vibration that could affect the operation of electrical components. | We will install distribution panels and boards with proper grouting. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 2 Months | In Progress
Initial Inspection |  | 23 | Cables inside distribution board are disorganized. | Cables inside each distribution board must be well-organized to prevent confusion during troubleshooting and maintenance activities. Proper cable management helps ensure clear identification of circuits and reduces the risk of errors. The use of a structured distribution board form is appreciated as it further aids in system clarity and documentation, improving safety and efficiency. | We will organize the cables inside each distribution board to avoid confusion during troubleshooting and maintenance activities. We will ensure clear identification of the correct cable management circuit. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 2 Months | In Progress
Initial Inspection |  | 24 | The working space in front of the panel is uneven. | Ensure the grade, floor, or platform in the required working space is clear, level, and flat throughout its entire depth and width to facilitate smooth operation and prevent any trip hazards. | We will improve the work area in front of the panel so that the required work area grade, floor or platform is clean, level across the full depth and width so that work can be done smoothly and the risk of collisions is avoided. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 2 Months | In Progress
Initial Inspection |  | 25 | Hot spots have been observed at some points. | Hot spots throughout the entire electrical system must be eliminated to ensure safety and prevent potential equipment failures or hazards and reduce downtime and repair costs. | We will eliminate hotspots in all electrical systems. We will install standard equipment in areas where hotspots have been identified. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 1 Month | In Progress
Initial Inspection |  | 26 | Distribution boards have no clear identification markings. | Clearly mark all distribution boards, switchboards, sub-main boards, and switches for identification. | We will clearly mark all distribution boards, switchboards, sub-main boards and switches for identification. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 2 Months | In Progress
Initial Inspection |  | 27 | Meters and other electrical devices (Ammeter, Voltmeter) not installed on the main electrical equipment. | Different types of meters and other electrical devices must be installed within the electrical distribution board or panel. This includes devices for monitoring, control and protection, ensuring accurate measurement and efficient management of the electrical system. | We will install various types of necessary meters and other electrical devices within the electrical distribution board or panel. These include devices for monitoring, control and protection, ensuring accurate measurements and efficient management of the electrical system. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 2 Months | In Progress
Initial Inspection |  | 28 | Phase barrier/separators are missing in circuit breaker. | Phases must be separated by insulators made from non-flammable rubber-type materials to prevent electrical short circuits and enhance safety. | We will separate the phases with insulators made of non-flammable rubber-like materials to prevent electrical short circuits and increase safety. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 1 Month | In Progress
Initial Inspection |  | 29 | Electrical distribution box/panels are full of fluffs (lint/dirt). | Each electrical distribution board/panel must be sealed to prevent the ingress of fluffs, while ensuring adequate ventilation. | Done | Nov 20 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 1 Month | In Progress
Initial Inspection |  | 30 | Panel doors are not connected with earth. | All metal components within the electrical system must be securely connected to the earth. This earthing is essential to mitigate the risk of electrical shock or electrocution by providing a safe path for fault currents to dissipate. |  | Dec 31 2025 | On 15/03/2026: Corrected. | 1 Month | Corrected
Initial Inspection |  | 31 | Multiple cables terminated at the bus bar & breaker using single cable lug. | Each power cable must be terminated at any connection point using single cable lug. | We will terminate each power cable at any connection point using a single cable lug. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 2 Months | In Progress
Initial Inspection |  | 32 | Loop connection has been used powering multiple circuits through circuit breakers. | No loop connections are allowed. Each cable must be terminated with a single cable lug at each terminal. Combo bus bars are permitted if the incoming cable size meets the rated capacity. | We will not connect any loops. each cable will be terminated by inserting one cable into each terminal. If the incoming cable size meets the specified capacity, we will use combo bus bars. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 2 Months | In Progress
Initial Inspection |  | 33 | Cables joint or tapping do not have adequate insulation and mechanical strength. | Cable joints shall be made through porcelain/PVC connectors with PIB tape wound around the joint in respect of conductivity, insulation, and mechanical strength. | We will make the cable joints using porcelain/PVC connectors and wrap the joints with PIB tape for conductivity, insulation, and mechanical strength. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 1 Month | In Progress
Initial Inspection |  | 34 | Power sockets are kept on floor/hung without support. | Power sockets must be securely installed on rigid supports or bases, positioned at a minimum height of 200 mm above the floor level. | We must place power sockets securely on a solid support or base, which should be at least 200mm above floor level. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 2 Months | In Progress
Initial Inspection |  | 35 | Cable duct/channels are filled with fluffs (lint/dust). | Cable channels and ducts must be kept clean and sealed to prevent any ingress of dust and debris. | We will keep cable channels and conduits clean and sealed to prevent dust and debris from entering. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 1 Month | In Progress
Initial Inspection |  | 36 | Panel/Distribution boxes are inaccessible or cannot be opened to perform any maintenance work or inadequate clearance. | Each electrical distribution board or panel must be easily accessible, maintaining a minimum working clearance of 1 meter (or equal to the width of the board/panel, whichever is greater). The panel's height must not be exceed 2 meters, and the bottom must be at least 0.45 meters above from the floor or working platform (for wall-mount panel). The board/panel door must open at least 90 degrees to ensure safe and efficient operation and maintenance. | We will make each electrical distribution board or panel easily accessible, maintaining a minimum working clearance of 1 meter (or equal to the width of the board/panel, whichever is greater). Keep the height of the panel within 2 meter and keep the bottom at least 0.45 meters above the floor or work platform (for wall-mounted panels). Keep the board/panel doors open at least 90 degrees to ensure safe and efficient operation and maintenance. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 2 Months | In Progress
Initial Inspection |  | 37 | Circuit is drawn from bus bar without any protective means. | Each electrical circuit must be drawn from the distribution board busbar with an appropriate protective device, such as an MCCB (Molded Case Circuit Breaker) or MCB (Miniature Circuit Breaker) to ensure safety and prevent electrical faults. | We will terminate each electrical circuit from the distribution board busbar with a suitable protective device, such as an MCCB (molded case circuit breaker) or MCB (miniature circuit breaker), to ensure safety and prevent electrical faults. | Dec 31 2025 | On 15/03/2026: Not Corrected. No progress has been observed during the inspection. | 1 Month | In Progress
Follow Up Inspection |  | 38 | New Finding: Transformer body earthing (equipment earthing) cable is inadequate. | The size of the earth cable shall be determined according to BNBC or the Adiabatic method. The number of earth pits shall be calculated based on acknowledged standards to ensure effectiveness. |  | Apr 15 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 39 | New Finding: Outdoor cable is not covered to protect from the weather effects. | All power cables exposed to weather shall have cover unless it is specified for outdoor wiring. |  | May 15 2026 |  | 2 Months | In Progress
Follow Up Inspection |  | 40 | New Finding: Generator room is filled with debris & flammable liquid(or used as temporary storage). | The generator room must be kept neat and clean at all times, with no storage items present. This helps ensure safe operation, reduces safety hazards, and allows for easy access to equipment during maintenance or emergencies. |  | Apr 15 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 41 | New Finding: Generator body earthing (equipment earthing) cable is inadequate. | Ensure that the generator is equipped with at least two separate earth pits. The size of the earth cable shall be determined according to BNBC or the Adiabatic method. The number of earth pits shall be calculated based on acknowledged standards to ensure effectiveness. |  | Apr 15 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 42 | New Finding: Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation, with a thickness of at least 3 mm for rubber mats, must be provided at the working area of each electrical installation. Length of the mat shall be equal to 1 meter or the width of the board/panel, whichever is greater. This includes areas of LT panels, MDBs, DBs, SDBs, and other manually operated machinery to ensure safety and prevent electrical hazards. |  | Apr 15 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 43 | New Finding: Uncovered/perforated type cable tray used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. |  | Jun 15 2026 |  | 3 Months | In Progress
Follow Up Inspection |  | 44 | New Finding: Combustible/flammable materials are attached with electrical panel board/BBT/cable channel/duct. | All flammable and combustible materials, including water bottles and other items, must be cleared from electrical cable channels, ducts, and BBTs. Separate storage arrangements for these materials should be implemented. |  | May 15 2026 |  | 2 Months | In Progress
Follow Up Inspection |  | 45 | New Finding: Exhaust fan body and fan blade enclosure are not equipped with earth connection. | Exhaust fan frame and its enclosure in the production area/s shall be connected to earth. |  | May 15 2026 |  | 2 Months | In Progress

## Boiler
Date
18-Apr-2026 | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address
Date of Inspection
Finance Plan Agreed | Yes