## Structural
Date
22-Apr-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Mark Sweater Ltd., Surabari,Kashimpur,Gazipur,Bangladesh, Gazipur, Dhaka
Date of Inspection |  | 2015-03-01
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Locally heavy floor loading in some storage areas | Factory Engineer to investigate if the applied loading can be safely carried by the slabs, beams and by the columns. | Completed | May 31 2016 | On 10 Feb, 2016 : The factory has prepared load plan. They should submit the load plan to ACCORD for approval. Previous time line was 31/12/2015 On 19 Oct, 2016 : This issue has been covered under DEA. DEA was accepted on 17 Feb 2016 and physically verified during inspection. On 05 Jun, 2017: Corrected in the previous follow up report. Factory engineer has carried out engineering assessment report, which was accepted by Accord on 17 Feb, 2016 On 16 Nov 2017: Found corrected in previous inspection. A allowable load plan was prepared by the factory which was accepted to ACCORD on 17 Feb 17. During inspection, Loads were measured and found within allowable limits(63 psf). On 05-Dec-2022: Corrected from the previous inspection. Load plan along with EA was produced and accepted by the Accord on 17 Oct 2016. On 29-May-2025: Corrected previously. | within 6-months) | Corrected
Initial Inspection |  | 2 | Locally heavy floor loading in some storage areas | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | Completed | May 31 2016 | On 10 Feb, 2016 : The factory has prepared load plan. They should submit the load plan to ACCORD for approval. Uncontrolled loading observed in 7th floor. Previous time line was 31/12/2015 On 19 Oct, 2016 : Load Plan has been prepared and incorporated in DEA. DEA was accepted on 17 Feb., 2016. During inspection live load observed within the limit specified by DEA. Load plan was posted. On 05 Jun, 2017: Corrected in the previous follow up report. Load plan had been accepted by Accord along with engineering assessment report. Floor load was found satisfactory, as per accepted load plan. Load plan was posted on the wall. On 16 Nov 2017: Found corrected in previous inspection. A allowable load plan was prepared by the factory which was accepted to ACCORD on 17 Feb 17. During inspection, Loads were measured and found within allowable limits (63 psf). On 05-Dec-2022: Corrected from the previous inspection. Floor loading was found below the accepted live load limit (63 psf on floor & 116 psf on storage) On 29-May-2025: Corrected previously. Floor loading was found within the accepted load limit (42 to 115 psf). | within 6-months) | Corrected
Initial Inspection |  | 3 | Stability Bracings of the cable holder structure is missing | Steel support frame -design to be reviewed by the Building Engineer | Completed | May 31 2016 | On 10 Feb, 2016 : Factory has done remedial work as per their consultant's recommendation. They should submit the assessment report to ACCORD for review. Previews timeline : 31/12/2015 On 19 Oct, 2016 : Covered under DEA. DEA was accepted on 17 Feb, 2016. As per DEA new bracings to be installed in the cable holder structure. Factory is required to complete the installation immediately. On 05 Jun, 2017: Steel supporting frame has been analysis by factory engineer and submitted to Accord along with Engineering assessment report for review. EA had been accepted by Accord on 17 Feb, 2016. As per recommendation few bracing are required to be installed, The factory has installed bracing but not according to the accepted drawing. The factory is required to install bracing as per accepted retrofitting drawing. On 16 Nov 2017: Factory engineer reviewed the stability of bracing of the cable holder which was covered in DEA. As per DEA recommendation, factory installed bracing as per retrofitting drawing. On 05-Dec-2022: Corrected from the previous inspection. Steel support frame was reviewed and accepted by the Accord on 17 October 2016. On 29-May-2025: Corrected previously. | within 6-months) | Corrected
Initial Inspection |  | 4 | Stability Bracings of the cable holder structure is missing | Stability bracings to be implemented to ensure an appropriate lateral stability system | Completed | May 31 2016 | On 10 Feb, 2016 : Factory has done remedial work as per their consultant's recommendation. They should submit the assessment report to ACCORD for review. Previews timeline : 31/12/2015 On 19 Oct, 2016 : Covered under DEA. DEA was accepted on 17 Feb, 2016. As per DEA new bracings to be installed in the cable holder structure. Factory is required to complete the installation immediately. On 05 Jun, 2017: Steel supporting frame has been analysis by factory engineer and submitted to Accord along with Engineering assessment report for review. EA had been accepted by Accord on 17 Feb, 2016. As per recommendation few bracing are required to be installed, The factory has installed bracing but not according to the accepted drawing. The factory is required to install bracing as per accepted retrofitting drawing. On 16 Nov 2017: Factory engineer reviewed the stability of bracing of the cable holder which was covered in DEA. As per DEA recommendation, factory installed bracing as per retrofitting drawing. On 05-Dec-2022: Corrected from the previous inspection. Stability bracing was installed to the cable holder structure. On 29-May-2025: Corrected previously. | within 6-months) | Corrected
Follow Up Inspection |  | 5 | New finding-1: Damage in exterior column, tie-beam due to vehicle impact and interior partition walls due to trolley impact in Building-1 | Repair the damage areas and provide adequate barrier to avoid further impact from the vehicle and trolley. | Completed | Jan 16 2023 | On 05-Dec-2022: Damage observed in exterior column, tie-beam due to vehicle impact and interior partition walls due to trolley impact in Building-1. The factory is required to repair the damage areas and provide adequate barrier to avoid further impact from the vehicle and trolley. On 29-May-2025: Damaged areas have been repaired, and steel barriers were provided around the columns and walls to avoid further impact from vehicle/trolley. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 6 | New finding-2: Dampness on stair, toilet zone brick walls and crack on stair waist slab edge in Building-1. | Qualified building engineer is required to investigate the reason of dampness and cracks & prepare an investigation report with proper remedial actions. The factory is required to repair the crack and damp areas according to investigation report. | Completed | Jan 16 2023 | On 05-Dec-2022: Dampness observed on stair and toilet zone brick walls and crack on stair waist slab edge in Building-1. Qualified building engineer is required to investigate the reason of dampness and cracks and prepare an investigation report with proper remedial actions. The factory is required to repair the crack and damp areas according to investigation report. On 29-May-2025: Dampness and cracks were repaired as per the recommendation of the investigation report. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 7 | New finding-3: Dampness throughout the Building-3. | As per the suggestion of qualified engineer, the factory is required to repair the damp areas. | Completed | Jan 16 2023 | On 05-Dec-2022: Dampness observed throughout the Building-3. As per the suggestion of qualified engineer, the factory is required to repair the damp areas. On 29-May-2025: Dampness were found repaired. | (within 6 weeks) | Corrected

## Fire
Date
22-Apr-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Mark Sweater Ltd., Surabari,Kashimpur,Gazipur,Bangladesh, Gazipur, Dhaka
Date of Inspection |  | 2015-02-20
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Diesel fuel storage was located inside the generator room. | Remove all diesel fuel storage from the generator room and relocate to the exterior such that the diesel fuel storage is at least 10 ft. from required egress paths. If located along egress paths or in a utility building, provide the diesel fuel storage with 2- hr fire rated construction. There shall be no diesel fuel storage in a factory production building. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected as per previous follow-up. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 2 | Unsealed electrical shafts are located in all the fire-rated floor and ceiling assemblies except the ground floor. | Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor level and seal all penetrations in floor and ceiling assemblies to maintain the fire separation. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected as per previous follow-ups. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected as per previous follow-up. On 12/01/2021: Corrected as per previous follow-up. On 29/03/2023: Corrected as per previous follow up. On 17-Sep-25: Refer to Issue No. 49. | Within 3 months | Corrected
Initial Inspection |  | 3 | The fire pump room is not provided with adequate fire rated separation in the utility building. | Provide fire pump room with 2 hr. rated fire separation when not sprinklered and 1 hr. rated fire separation when provided with automatic sprinklers, in accordance with NFPA 20. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected as per previous follow-up. On 12/01/2021: Corrected as per previous follow-up. On 29/03/2023: Corrected as per previous follow up. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | The industrial dryers are not separated by fire rated construction on the fourth floor | Separate the industrial dryer room by a minimum 2-hr fire rated construction. Seal and protect all openings to maintain the required fire separations. Provide proper ventilation and consult with a qualified engineer. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected as per previous follow-up. On 12/01/2021: Corrected as per previous follow-up. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 5 | Areas used for combustible storage open to the factory are not separated by fire rated construction on second and fourth floors. | Provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.45m (8ft.) and maximum area of 23m2 (250 ft2) - If sprinkler protected: maximum height of 3.66m (12ft.) and maximum area of 93m2 (305ft2). Separate areas of unenclosed combustible storage by a minimum clear distance of 3m (10ft.). | Corrected | May 10 2016 | On 20.03.2017: No action has been taken yet. Storage area has been found in prayer room. On 02.07.2017: In progress. On 19/11/2017: It has been found same as before. On 23/05/2018: Dining was used as storage. On 04/03/2019: Corrected. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Refer to Issue No. 52 | Within 3 months | Corrected
Initial Inspection |  | 6 | Exit stairs are not separated from work areas and other spaces on each floor by fire rated construction. | Provide minimum 1-hr rated doors for buildings with 3 or fewer stories and 1.5-hr fire rated doors for buildings that are 4 or more stories. Seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. Once fire doors are installed, every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets ACCORD standard 6.8.3.1. | Completed | May 10 2016 | On 04/03/2019: Fire door is provided however S-E and S-W stair is not enclosed from building interior on ground and 1st floor level. Electric cable channel also located in stair enclosure, shall be removed. On 02/01/2020: In progress. Fire door has been installed at all exit doors. Factory shall adjust coordination of their double leaf doors. The doors were not properly smoke sealed. The gap underneath the doors should not exceed the allowable 19mm. (CH) 09-Feb-2020: Factory asked time extension till 15 Feb 2020 to complete remediation work. Time extension not accepted. Follow Accord recommended timeline. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Refer to Issue No. 51 | Within 3 months | Corrected
Initial Inspection |  | 7 | Unsealed penetrations and openings are located in all the fire rated floor and ceiling assemblies except the ground floor. | Seal all penetrations and openings in floor and ceiling assemblies to maintain the fire separation. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected as per previous follow up. On 12/01/2021: Corrected as per previous follow-up. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 8 | Unsealed penetrations and openings are located in the north west exit stair enclosure on the ground floor. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | Corrected | May 10 2016 | On 20.03.2017: Corrected. On 02.07.2017: Corrected as per previous follow-ups. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 9 | The boiler and compressor rooms are not separated by fire rated construction due to openings and nonrated doors on second floor and utility building. | Separate the boiler and compressor room by a minimum 1-hr fire-rated construction for non-high rise, and 2-hr fire rated construction for high rise. Seal and protect all openings to maintain the required fire separations. When located to the exterior of a building, 3m (10 ft.) separation is required. Provide proper ventilation and consult a qualified engineer. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected as per previous follow-up. On 12/01/2021: Corrected as per previous follow-up. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 10 | Rooms used for combustible storage are not separated by fire rated construction on ground, first, second, fourth and seventh floors. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.45m (8ft.) and maximum area of 23m2 (250 ft2) - If sprinkler protected: maximum height of 3.66m (12ft.) and maximum area of 93m2 (305ft2) Separate areas of unenclosed combustible storage by a minimum clear distance of 3m (10ft.). | Corrected | May 10 2016 | On 20.03.2017:No action has been taken yet. On 02.07.2017: Found same as before. On 19/11/2017: Civil work is on going. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 11 | Building did not have stair designation signs and occupant load signs at floor entrances. | Provide stair designation signs, occupant load signs and emergency evacuation plans at required locations. | Corrected | Apr 6 2016 | On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 12 | Egress doors and gates with locking features are provided at building exits, exit stairs and along egress routes. All gates and doors were not open and unlocked during the inspection. | Remove locking features from all egress doors and gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101 and ACCORD standard 6.8.2. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 13 | Storage and obstructions were located in the egress paths on first, fifth and sixth floors. | Keep egress paths and stairs clear of storage and obstructions. | Corrected | Apr 6 2016 | On 19.10.2016: Corrected. On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 14 | Storage was located in the south east exit stair on the sixth, fifth and ground floors and in south west and north west exit stairs on the ground floors. | Remove all storage from exit stairs and egress paths. | Corrected | Apr 30 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected as per previous follow-ups. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. Staircases and exit discharges were found clear of any obstructions. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 15 | Collapsible gates and sliding doors are provided at building exits, exit stairs and along egress routes. | Replace all gates and sliding oors along the means of egress with side-hinged, swinging egress doors in accordance with ACCORD standard 6.8.1. | Corrected | Apr 6 2016 | On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 16 | North east and north west exit stairs serve more than 5 stories and do not have required reentry provisions. | Every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets ACCORD standard 6.8.3.1. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 17 | The day-care room does not meet ACCORD standard 3.4.2.1.1. on the ground floor. | Day-care shall be located on the ground floor with a maximum travel distance of 9 m (30 ft) or located one story above level of exit discharge with direct access to an exit enclosure. If the above is not possible provide a minimum 2-hr fire rated exit corridor between the day-care room and exit stair with ACCORD approval. | Corrected | Apr 6 2016 | On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 18 | Dead-end aisles exceed 30 m (100 ft.) on the sixth floor. | Reconfigure the egress arrangement to reduce the maximum dead-end distance to not more than 30 m (100 ft.). | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 19 | Handrails are not provided on both sides of all the exit stairs. | Provide handrails on both sides of the exit stair. New handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in.) | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected as per previous follow-ups. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 20 | The high-rise building has an occupied floor greater than 23m (75 ft.) and is not provided with automatic sprinkler protection. The large occupant loads, heavy fuel loading and anticipated extended egress times warrant sprinkler protection | Provide automatic sprinkler protection throughout the building in accordance with NFPA 13. | Corrected | May 10 2016 | On 02/01/2020: T&C Documents Assessment Visit conducted & found system is not ready for functional T&C VI. (CH) 09-Feb-2020: Factory asked time extension till 15 Feb 2020 to complete remediation work. Time extension not accepted. Follow Accord recommended timeline. (CH) 11-Mar-2020:Pre-T&CVI documents is Pending Review . (CH) 31-May-2020:Pre-T&CVI documents is Pending Submission . (RCH) 03-Sep-2020:Pre-T&CVI documents Pending Submission . (RCH)16-Nov-2020:Pre-T&CVI documents submitted on 15 Nov 2020 which is under review. On 12/01/2021: Sprinkler system is approved according to T&CVI. For details see the T&CVI report. On 29/03/2023: Corrected. During the inspection the pump was found functional. On 17-Sep-25: Corrected. | Design within 6 months, install within 12 months | Corrected
Initial Inspection |  | 21 | The required no smoking signs are not present in the factory | Smoking is prohibited in any garment factory building or separate storage building. Signs shall be posted in Bengali and English at all building entrances. If the factory creates a designated smoking area outside the building, information of these areas will be posted on the signs. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 22 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10. | Corrected | Apr 6 2016 | On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 23 | Inspection, testing and maintenance for the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with NFPA 72. | Corrected | Apr 6 2016 | On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 24 | Inspection, testing and maintenance of the fire pump system is not in accordance with NFPA 20. | Inspect, test and maintain the fire pump system and keep written records on-site, in accordance with NFPA 20. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 25 | Inspection, testing and maintenance of the automatic sprinkler system is not in accordance with NFPA 25. | Inspect, test and maintain the automatic sprinkler system and keep written records onsite, in accordance with NFPA 25. | Corrected | Apr 6 2016 | On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 26 | Inspection, testing and maintenance of the standpipe system is not in accordance with NFPA 14. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 14. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 27 | Visible and audible notification was not provided for the building in accordance with NFPA 72. | Provide visible and audible notification for the building in accordance with NFPA 72. | Completed | Apr 25 2016 | On 19/11/2017: It is integrated part of fire alarm system. On 23/05/2018: It is integrated part of fire alarm system. On 04/03/2019: It is integrated part of fire alarm system. On 02/01/2020: It is integrated part of fire alarm system. On 12/01/2021: Fire Alarm system is approved according to T&CVI. For details see the T&CVI report. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 28 | Fire pump did not meet ACCORD standard 5.5.1 and 5.5.1.1. | Update current fire pump or provide a new fire pump that meets ACCORD standard 5.5. | Corrected | May 10 2016 | On 02/01/2020: It is integrated part of fire protection system. (CH) 11-Mar-2020: Pending Review Pre-T&CVI documents. (CH) 31-May-2020:Pre-T&CVI documents is Pending Submission. (RCH) 03-Sep-2020:Pre-T&CVI documents is Pending Submission . (RCH)16-Nov-2020:Pre-T&CVI documents submitted on 15 Nov 2020 which is under review. On 12/01/2021: Fire Pump is approved according to T&CVI. For details see the T&CVI report. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 29 | Exit signs were placed in areas that were not exits almost on all the floors. | Remove exit signs from noted areas to avoid confusion from actual exits. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 30 | Exit signage was not provided at south east exit stair entrance on the sixth floor and south west exit stair on the second floor. | Provide exit signs above all building exits to the exterior, all doors to the exit stairs and along all paths of travel where a change of direction is not obvious. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 31 | Exit signage not illuminated on third, fourth, fifth and seventh floors. | Regularly inspect all exit signage and replace and install lights as needed to illuminate signs. The source of illumination shall provide not less than 50 lux at the illuminated surface with a contrast of not less than 0.5. Approved self luminous signs which provide evenly illuminated letters having a minimum luminance of 0.2 cd/m^2 may also be used. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 32 | Emergency lighting did not function in test mode on the seventh floor. Emergency lights are burnt out on the north east exit stair and ground floor. | Regularly test the emergency lighting system on each floor and replace or repair lights as needed | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 33 | Manual on-off switches are provided for emergency lighting and exit signage units on the body of the units and on the IPS Battery units. | Remove manual on/off switches from emergency lighting and IPS units to prevent them from being switched off. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 34 | Inspection, testing and maintenance for the emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 35 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes on the factory floors and exit stairs. | Test the emergency lighting system on each floor and provide additional emergency fixtures to supply adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and along exit discharge paths and a minimum 2.5 lux along exit access aisles. | Corrected | Apr 6 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 36 | New Finding(1st Follow-Up): Liquefied or compressed gas cylinders were located within the factory on the ground floor. | The storage or use of liquefied or compressed flammable gas cylinders shall be prohibited with in the factory building | The factory has constructed a new LPG storage area and relocated all LPG cylinders from the factory building to the designated LPG store. | May 10 2016 | On 12/01/2021: Corrected. During follow-up inspection no storage or use of liquefied or compressed flammable gas cylinder found. On 29/03/2023: Corrected. Not Found. On 17-Sep-25: Issue is re-opened. Construction work of new single storied LPG room was on-going where Liquefied or compressed gas cylinders were kept without ensuring required fire separation. The room housing only gas canisters shall be enclosed in a 2-hour fire resistant, non-combustible construction, inclusive of providing fire doors and protection of all openings, penetrations & ducts to maintain the 2-hour fire resistance /fire separation. The building must be mechanically ventilated to control the accumulation of flammable vapors. RPO Comments: On 6-Jan-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Immediately | Pending Verification
Follow Up Inspection |  | 37 | New Finding (3rd Follow-up): The northeast & northwest exterior exit stair is not properly separated from the building. | Exterior exit stairs shall be separated from the building with a rating requirement of 1 hr. fire rating for 3 or fewer stories or 2 hr. fire rating for 4 or more stories. The rating of the exterior wall shall extend 3.05 m (10ft) beyond the ends of the stair structure. | Corrected | May 30 2016 | On 20.03.2017: Corrected. Windows have been closed by brick wall. On 02.07.2017: Corrected as per previous follow-ups. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. Unsealed penetrations within 10ft of the staircases are sealed from the inside with fire rated construction. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 38 | New Finding (3rd Follow-up): The fire alarm system is antiquated, not a listed system , and does not provide alarm and notification with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | Corrected | May 30 2016 | On 02/01/2020: T&C Documents Assessment Visit conducted & found system is not ready for functional T&C VI. (CH) 11-Mar-2020: Pending Review Pre-T&CVI documents. (CH) 31-May-2020:Pre-T&CVI documents is Pending Submission . (RCH) 03-Sep-2020:Pre-T&CVI documents is Pending Submission . (RCH)16-Nov-2020:Pre-T&CVI documents submitted on 15 Nov 2020 which is under review. On 12/01/2021: Fire Alarm system is approved according to T&CVI. For details see the T&CVI report. On 29/03/2023: Corrected. During the inspection The panel was found normal and healthy, but the detector were found with cover in Utility building. On 17-Sep-25: Corrected. | Within 2 months (Design already reviewed from Accord) | Corrected
Follow Up Inspection |  | 39 | New Finding (4th follow-up): The fire pump room is not provided with adequate fire rated separation in the utility building. | Provide fire pump room with 2 hr. rated fire separation when not sprinklered and 1 hr. rated fire separation when provided with automatic sprinklers, in accordance with NFPA 20. | Corrected | Sep 3 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. Proper separation is required. On 02/01/2020: Corrected as per previous inspection. On 12/01/2021: Corrected as per previous follow-up. On 29/03/2023: Corrected as per previous follow up. The fire pump room is not separated from stair case of utility building. On 17-Sep-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 40 | New Finding (4th follow-up): Storage and obstructions were located in the egress paths on first, fifth and sixth floors. | Keep egress paths and stairs clear of storage and obstructions. | Corrected | Aug 10 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. None found. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. . | Immediately | Corrected
Follow Up Inspection |  | 41 | New Finding (4th Follow-Up): North east and north west exit stairs serve more than 5 stories and do not have required reentry provisions. | Every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets ACCORD standard 6.8.3.1. | Corrected | Sep 3 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. Provided. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 42 | New Finding (4th Follow-Up): Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10. | Corrected | Aug 10 2016 | On 15.12.2016: Corrected On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017:Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 43 | New Finding (4th Follow-Up): The required no smoking signs are not present in the factory | Smoking is prohibited in any garment factory building or separate storage building. Signs shall be posted in Bengali and English at all building entrances. If the factory creates a designated smoking area outside the building, information of these areas will be posted on the signs. | Corrected | Aug 15 2016 | On 15.12.2016: Corrected as per site observation. On 20.03.2017: Corrected. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 44 | New Finding (6th Follow-Up): In the North-East and North-West exit stairs of the building at all floors the staircase landing is blocked by fire door's leaf. | Need to shift the fire door, so that the staircase landing will be free for emergency exit. | Corrected | Feb 28 2017 | On 20.03.2017: Corrected. Fire door has been relocated. On 02.07.2017: Corrected. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 45 | New Finding (7th follow-up):Unsealed penetrations and openings are located in exit stair enclosures. Location(s): South-west exit stair. | Seal all penetrations and openings in the wall of exit enclosure walls (full thickness of the wall) by fire rated materials to maintain the fire resistance rating. | Corrected | Apr 21 2017 | On 20.03.2017: New finding. On 02.07.2017: In progress. All sorts of unprotected openings/penetrations shall be sealed by proper fire rated construction. On 19/11/2017: Corrected. On 23/05/2018: Corrected. On 04/03/2019: Corrected based on previous follow ups. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 46 | New Finding (8th follow-up): Storage and obstructions were located in the egress paths and exit stair case. | Keep egress paths and stairs clear of storage and obstructions. | Corrected | Jul 10 2017 | New Finding (8th follow-up) On 19/11/2017: Corrected. On 23/05/2018: Aisles were used as storage in several places. On 04/03/2019: Corrected. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 47 | New Finding: Adequate aisles is not provided on 5th floor. | Aisles shall be provided with a minimum unobstructed clear-width of 0.9 m (36 in.) throughout the factory. | The factory has aisles with an unobstructed clear width of 0.9 m in the linking sections as well as throughout the factory. | May 2 2019 | On 04/03/2019: New Finding. On 02/01/2020: Corrected. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Issue is re-opened. Aisle mark is not found in linking and mending section on 5th floor. RPO Comments: On 6-Jan-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 months | Pending Verification
Follow Up Inspection |  | 48 | New Finding: Dining and prayer room at 7th floor is not separated from other areas by 2 hr fire rated construction. | Separate the dining room by a minimum 2-hr fire-rated construction having two direct access to exit stair/out side of the building. Seal and/or protected all openings to maintain the required fire separations. | The factory cleared temporary storage from the areas of dining and prayer areas. On the other hand prayer and dining areas totally saparated from other areas by required separation. | May 2 2019 | On 04/03/2019: New Finding. On 02/01/2020: Corrected. Factory has separated occupancies with fire door and fire rated construction. On 12/01/2021: Corrected. On 29/03/2023: Corrected. On 17-Sep-25: Issue is Re-opened. Dining room is not separated from temporary storage area. RPO Comments: On 6-Jan-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 months | Pending Verification
Follow Up Inspection |  | 49 | New Finding (15th FUI): Penetrations through floor/ceiling assemblies are found unsealed. Location: Electrical Shaft S-W side on 1st to 7th floor in Main Production Building Non-compliance reason: Unprotected opening and annular space around electrical cables | Seal all penetrations and openings in floor/ceiling assemblies by a listed through-penetration fire stop system tested in accordance with ASTM E814 or approved alternative standard to maintain minimum 3-hr. fire resistance rating. Installation shall be as per manufacturer published installation guideline and the certification authority guideline to ensure the fire-rating in accordance with section 4.7 of RSC Technical Guideline (Standard) Or, Provide a minimum 2-hr fire rated shaft to separate the penetration from each floor if required. | The facility has appointed a qualified engineer to carry out the required corrective measures. The work is currently in progress and is expected to be completed by 16 August 2026 | Dec 17 2025 | On 17-Sep-25: New Findings. RPO Comments on 22-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 Months | In Progress
Follow Up Inspection |  | 50 | New Finding (15th FUI): Unsealed penetrations and openings are located in exit stair enclosures. Electrical cable raceway or other utility lines (Plumbing UPVC pipes) passing through the exit enclosure in main production building. Location(s): (i) Electrical cable raceway vertical penetration on 7th floor in S-E stair-2 enclosure; (ii) Electrical cable raceway horizontal penetration on 4th, 5th & 6th floor in S-W Stair-1 enclosure (iii) UPVC plumbing lines (Vertical Penetration) on 1st floor in S-E stair-2 enclosure. & (iv) SDB and IPS located on ground floor staircase in security building | No other penetration into and through the exit enclosure except for fire alarm equipment electrical raceway, required exit doors, sprinkler piping, standpipes, and electrical conduit serving the exit enclosure is permitted in accordance with section 6.14.4 of RSC Technical Guidelines (Standard)¹ V1.0. So, relocate the electrical wires/raceways to somewhere else avoiding the exit enclosure, and seal the created unprotected openings (horizontal) with a minimum of 1.5 hours listed/certified fire-rated materials. Installation shall be as per manufacturer published installation guideline and the certification authority guideline to ensure the fire-rating. Or seal the horizontal penetration by 2-hr masonry construction. Seal all vertical penetrations and openings in floor/ceiling assemblies by a listed through-penetration fire stop system tested in accordance with ASTM E814 or approved alternative standard to maintain minimum 3-hr. fire resistance rating. Installation shall be as per manufacturer published installation guideline and the certification authority guideline to ensure the fire-rating in accordance with section 4.7 of RSC Technical Guideline (Standard) | The facility has appointed a qualified engineer to implement the required corrective measures. Several issues have already been addressed, while the remaining works are in progress and are expected to be completed by 16 August 2026. | Dec 17 2025 | On 17-Sep-25: New Findings. RPO Comments on 22-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 Months | In Progress
Follow Up Inspection |  | 51 | New Finding (15th FUI): The exit stair enclosures are not separated from work areas and other spaces on ground and 1st floor by fire-rated construction. Location: S-W Stair-1 Enclosure and S-E Stair-2 Enclosure on ground and 1st floor in Main Production Building | The exit stair enclosure shall be provided with a minimum 1-hr fire resistance rating for buildings with 3 or fewer stories and a minimum of 2- hr. fire resistance rating for buildings 4 or more stories. Provide 1-hr. fire rated door and seal all penetrations and openings by 1 hr. fire rated fire rated barrier construction for building with 3 or fewer stories. Provide 1.5 hr. fire rated door and seal all penetrations and openings by 2 hr. fire rated fire rated barrier construction for building with 4 or more stories in accordance with section 6.3.1.2 of RSC Technical Guidelines (Standard)¹ V1.0. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. Keep proper datasheet & certifications for installed fire doors & accessories on-site for verification. The clearance under the bottom of a door shall be a maximum of 3⁄4 in. (19 mm). | The facility has appointed a qualified engineer to carry out the required corrective measures. The work is currently in progress and is expected to be completed by 16 August 2026. | Dec 17 2025 | On 17-Sep-25: New Findings. RPO Comments on 22-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 Months | In Progress
Follow Up Inspection |  | 52 | New Finding (15th FUI): Areas used for in-process storage of combustible materials are open to the surrounding occupancy. Location: Dumping spaces in linking, trimming and mending section on 4th floor in Main Production Building. | Provide defined storage areas and limit the storage arrangement as follows: Maximum height of 2.45 m and maximum area of 23 m² and is separated by a minimum 3.0 m (10ft) from other storage areas and they do not exceed 10 percent of the building area of the story in which they occur. or, If sprinkler protected, Maximum height 12 ft (3.66 m) and maximum area of 1000 ft² (93 m²) and separated by a at least 25 ft (7.62 m) and does not constitute more than 10 percent of the building area or 4000 ft² (372 m²) of the sprinklered area, whichever is greater. or, Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | The factory cleared all combustible materials from the open area and is keeping them in the designated storage area as per the guidelines. | Nov 17 2025 | On 17-Sep-25: New Findings. RPO Comments: On 6-Jan-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 Months | Pending Verification

## Electrical
Date
22-Apr-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Mark Sweater Ltd., Surabari,Kashimpur,Gazipur,Bangladesh, Gazipur, Dhaka
Date of Inspection |  | 2015-02-20
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Electrical Single Line Diagram (SLD) is unavailable. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by Accord. | Corrected | May 16 2016 | On 10/02/2016: Drawing is available, but drawing is less informative. Make SLD properly & get it reviewed by Accord. New committed timeline is 31-03-2016 to close this issue. On 06/04/2016: After modification submit SLD to Accord. New timeline to solve the issue is 16th May, 2016. On 03/08/2016: Not corrected. SLD is not updated after review and not amended properly. On 19/10/2016: Not corrected. The drawing is not as built. On 15/12/2016: Not corrected. On 20/03/2017: Not corrected. SLD is not as built. Also need some correction. On 02-07-2017: Corrected. | 12 Weeks | Corrected
Initial Inspection |  | 2 | Thermographic scanning of the entire electrical system has not been performed. | Thermographic scanning of the entire electrical system must be performed twice in a year. | Completed | Sep 30 2015 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 8 Weeks | Corrected
Initial Inspection |  | 3 | Insulation resistance test of electrical equipment is not performed. | Insulation resistance test of all power cables (up to floor distribution board or SDB) must be performed in a periodic manner and recorded. | Completed | Sep 30 2015 | On 16/08/2015: Corrected at Accord 1st follow-up. | 8 Weeks | Corrected
Initial Inspection |  | 4 | Earth pit resistance record is unavailable. | Perform earth pit resistance test once a year. | Completed | Feb 29 2016 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 8 Weeks | Corrected
Initial Inspection |  | 5 | Transformer Oil Test report is unavailable. | Check the transformer oil condition by performing oil test, this must be done twice a year and recorded. | Completed | May 20 2015 | On 16/08/2015: Corrected at Accord 1st follow-up. | 8 Weeks | Corrected
Initial Inspection |  | 6 | Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present near all electrical equipment. | Hang first aid and CPR instructions near all electrical equipment (LT panel, MDB, FDB, DB, SDB) in a visible location. | Completed | Dec 31 2015 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 8 Weeks | Corrected
Initial Inspection |  | 7 | Maintenance records don’t reflect actual factory circumstances; the records do not mention all electrical equipment/ machineries. | Maintenance Manager or Safety Officer must keep accurate records and ensure that they reflect actual factory day to day operations. | Completed | Dec 31 2015 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 8 Weeks | Corrected
Initial Inspection |  | 8 | HT cables laid on substation room concrete floor. | Use a cable tray or install cable trench to ensure adequate support and protection. This must not be routed/ supported through the equipment working clearance area. | Completed | Apr 29 2015 | On 16/08/2015: Corrected at Accord 1st follow-up. | 5 Weeks | Corrected
Initial Inspection |  | 9 | HT service cable is not supported on transformer body (fins) near the termination. | Install cable riser or ladder to support the cable. | Completed | Apr 29 2015 | On 16/08/2015: Corrected at Accord 1st follow-up. | 3 Weeks | Corrected
Initial Inspection |  | 10 | Transformer silica gel is discolored and transformer breather oil cup is empty. | Replace silica gel by a new one; or dry it under sun and reuse it, if color regains, and, fill the transformer breather oil cup with transformer oil. | Completed | Dec 31 2015 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 3 Weeks | Corrected
Initial Inspection |  | 11 | Generator body has been earthed by inadequate/ improper sized (type) cable. | Ensure minimum two earthing connection for generator body (consult with your generator supplier). | Completed | Apr 29 2015 | On 16/08/2015: Corrected at Accord 1st follow-up. | 3 Weeks | Corrected
Initial Inspection |  | 12 | Generator body has no earth connection. | Ensure minimum two earthing connection for generator body (consult with your generator supplier). | Completed | Apr 29 2015 | On 16/08/2015: Corrected at Accord 1st follow-up. | 1 Week | Corrected
Initial Inspection |  | 13 | Generator output cables are not supported and protected (typical issue). | Ensure adequate protection for power cables by arranging cables in covered cable tray/riser and cable trench, ensure that there are no obstacles around generator. | Completed | Dec 31 2015 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 5 Weeks | Corrected
Initial Inspection |  | 14 | No/Inadequate rubber (insulation) mat on the working area of distribution board/panel (typical issue). | Put electrical insulation (rubber mat) on the working area of each electrical installation (Transformer/LT panel/ MDB/DB/SDB/other manual operated machineries). | Completed | May 20 2015 | On 16/08/2015: Corrected at Accord 1st follow-up. | 3 Weeks | Corrected
Initial Inspection |  | 15 | No identification and signs for electrical panels. | Provide identification in front every electrical panel. Include voltage level on the notice and any precautions if required for special case. | Completed | Dec 31 2015 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 3 Weeks | Corrected
Initial Inspection |  | 16 | Circuit diagrams are not hung on the panels (typical issue). | Provide/hang circuit diagrams of panels/ boards in every panel. | Completed | Apr 10 2016 | On 06/04/2016: Corrected. On 10/02/2016: Hang circuit diagrams of each panel in front of it when SLD will be reviewed by Accord. New committed timeline is 10-04-16 to close this issue. | 5 Weeks | Corrected
Initial Inspection |  | 17 | Panel/Distribution Board's top/bottom is left open (typical issue). | Seal each panel/ distribution board's top/bottom; and use cable glands holding/ supporting cables. | Completed | May 15 2016 | On 10/02/2016: This issue is not corrected yet. New committed timeline is 15-05-2016 to close this issue. On 06/04/2016: Not corrected. On 03/08/2016: Not corrected. On 19/10/2016: Corrected. | 8 Weeks | Corrected
Initial Inspection |  | 18 | Phase barrier/separator not installed (typical issue). | Put a purposely made phase separator (rubber type) between two phases; also terminate cables by proper sized cable lugs and cover cable lugs by heat shrink. | Completed | Feb 29 2016 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 5 Weeks | Corrected
Initial Inspection |  | 19 | Panel doors are not connected with earth (typical issue). | All metal panel doors must have an earth connection of at least 4 rm earth cable. | Completed | Sep 10 2015 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 5 Weeks | Corrected
Initial Inspection |  | 20 | Panels not securely fixed to the foundation. The brick foundation is damaged. | Panel base must be securely fixed to the foundation, with appropriate fastening devices. Panel base frame may be used on foundation to mount the panel. | Completed | Sep 30 2015 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 3 Weeks | Corrected
Initial Inspection |  | 21 | Cables are not supported properly. Cable terminals may be in tension (typical issue). | Use cable riser/ladder to support cables at anywhere to keep cable out of tension. | Completed | Sep 30 2015 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 3 Weeks | Corrected
Initial Inspection |  | 22 | Cable trench is opened and left uncovered. | Provide cover made of non-combustible material, preferably metallic checkered plate, to protect cable insulation from physical damage as well as prevent entering debris, dust and lint. | Completed | Mar 31 2016 | On 06/04/2016: Corrected. On 10/02/2016: This issue is not corrected yet. New committed timeline is 31-03-16 to close this issue. | 3 Weeks | Corrected
Initial Inspection |  | 23 | Remaining gaps/opening around the BBT passing through wall and floor are left open (typical issue). | Seal all the penetrations using appropriate fire rated material and ensure the Bus Bar Trunking (BBT) does not get damaged during sealing work. | Completed | Feb 29 2016 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 5 Weeks | Corrected
Initial Inspection |  | 24 | Power cables entering to or exiting distribution board/panel are not properly fixed (typical issue). | Power cables entering or exiting the distribution board/panel must be fixed through panel base/top plate using cable glands (metal/PVC). Cable trays/ladders may be used to support the cables. | Completed | Sep 30 2015 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 8 Weeks | Corrected
Initial Inspection |  | 25 | Cables laid on floor cable tray in stabilizer room are not protected (typical issue). | Use adequate cover, preferably metal sheet, to cover the floor tray on top to ensure mechanical protection from falling object or stepping of occupants onto it. | Completed | Mar 20 2016 | On 06/04/2016: Corrected. On 10/02/2016: Cover the cable tray by metallic sheet. New committed timeline is 20-03-16 to close this issue. | 8 Weeks | Corrected
Initial Inspection |  | 26 | Overhead cable/wiring channel have too many cables (overloaded). | Replace the cable tray with a wider one; or use additional cable trays to distribute cables keeping 20-25% of the tray area free. Overhead cable/ wiring channels may be closed. | Completed | Feb 29 2016 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 5 Weeks | Corrected
Initial Inspection |  | 27 | Cable duct/channels have excessive lint/dust . | Clean all the cable channels/ducts and cover them with (checkered/ perforated plates may be used for the bottom). | Completed | Mar 31 2016 | On 06/04/2016: Corrected. On 10/02/2016: Factory must establish a periodical program for cleaning all the cable ducts & all cable ducts must be covered. New committed timeline is 31-03-16 to close this issue. | 3 Weeks | Corrected
Initial Inspection |  | 28 | Battery terminals are left open. | Use insulated rubber cap to cover all the battery terminals. | Completed | Mar 10 2016 | On 06/04/2016: Corrected. On 10/02/2016: Use appropriate insulated rubber cap for battery. New committed timeline is 10-03-16 to close this issue. | 1 Week | Corrected
Initial Inspection |  | 29 | Large exhaust fans controlled by MCB (typical issue). | Use Direct On Line (DOL) switch to stop auto start after power failure and connect each individual fan frame with earth. | Completed | Apr 22 2015 | On 16/08/2015: Corrected at Accord 1st follow-up. | 4 Weeks | Corrected
Initial Inspection |  | 30 | Factory has installed Lightning Protection System, but couldn’t show any drawing. | Design as built drawing and share it with Accord to get further guidelines. | Completed | May 16 2016 | On 10/02/2016: This issue is not corrected yet. New committed timeline is 31-03-2016 to close this issue. On 06/04/2016: LPS drawing needs modification to install. New timeline to solve the issue is 16th May, 2016. On 03/08/2016: Not corrected. Drawing has done. On 19/10/2016: Not corrected. On 15/12/2016: Corrected. | 12 Weeks | Corrected
Follow Up Inspection |  | 31 | New Finding: Electric safety training program is not initiated/conducted. | Electrical safety training and awareness program for the electrical personal and workers must be initiated and recorded. | Completed | Sep 16 2015 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 1 Month | Corrected
Follow Up Inspection |  | 32 | New Finding: Power cables are bent excessively. | Avoid power cable bending in electrical system; in unavoidable case bend cables without any stress but not less than 135 degree. | Completed | Feb 29 2016 | On 10/02/2016: Corrected at Accord 2nd follow-up. Excessive bending was found in only PFI panel. Monitor the temperature in bending point. | 2 Months | Corrected
Follow Up Inspection |  | 33 | New Finding: Multiple cables terminated at MCCB terminals/bus bar. | Terminate each power cable at single terminal and use proper sized cable lug. | Completed | May 16 2016 | On 10/02/2016: This issue is not corrected yet. New committed timeline is 31-03-2016 to close this issue. On 06/04/2016: New timeline to solve the issue is 16th May,16. On 03/08/2016: Not corrected. On 19/10/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 34 | New Finding: Loop connection has used powering multiple MCBs/ MCCBs. | Eliminate loop cables; use single cable for each MCBs/MCCBs. You may use bus bar to avoid multiple termination. | Completed | Sep 16 2015 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 1 Month | Corrected
Follow Up Inspection |  | 35 | New Finding: No/improper cable glands used. | Power cables entering to or exiting from distribution board/panel must be fixed through panel base/top plate using precise cable glands (metal/PVC). | Completed | Oct 16 2015 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 2 Months | Corrected
Follow Up Inspection |  | 36 | New Finding: Unterminated wire is kept inside the electrical panel/cable tray. | All unterminated wires shall be removed. | Completed | Oct 16 2015 | On 10/02/2016: Corrected at Accord 2nd follow-up. Such issue was not found at the time of inspection. | 2 Months | Corrected
Follow Up Inspection |  | 37 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/undersize. | Resize earth lead cable/ECC for LT panel/MDB/DB; follow BNBC 2006 part 8 chapter 2 section 2.8 for sizing your earthing cables (usually ECC should be equal to the half of the respective phase cable). | Completed | May 16 2016 | On 10/02/2016: This issue is not corrected yet. New committed timeline is 25-03-2016 to close this issue. On 06/04/2016: New timeline to solve the issue is 16th May,16. On 03/08/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 38 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly. | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. | Completed | May 16 2016 | On 06/04/2016: New timeline to solve the issue is 16th May, 2016. On 10/02/2016: This issue is not corrected yet. New committed timeline is 25-03-16 to close this issue. On 03/08/2016: Not corrected. On 19/10/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 39 | New Finding: Cables passing through wall/floor slab are not protected at the entry/exit point(s). | Cables passing through permanent wall/floor slab must be protected. Seal the opening by fire rated material protecting power cables thus no smoke can pass through this barriers. | Completed | Feb 29 2016 | On 10/02/2016: Corrected at Accord 2nd follow-up. | 2 Months | Corrected
Follow Up Inspection |  | 40 | New Finding: Multiple cables connected in the bus bar through single lugs. | Each cable must be connected in the bus bar through single lugs. | Completed | May 16 2016 | On 10/02/2016: This issue is not corrected yet. New committed timeline is 31-03-2016 to close this issue. On 06/04/2016: New timeline to solve the issue is 16th May,16. On 03/08/2016: Not corrected. On 19/10/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 41 | New Finding: Fuse used as isolator and operated manually while the circuit is energized. | Replace fuse with circuit breaker or equip circuit breaker on both sides of the HRC fuse and operate while the circuit is not live and fix it in a cabinet/board. | Completed | Nov 16 2015 | On 10/02/2016: Corrected at Accord 2nd follow-up. Fuse is used in only one place (suggested by supplier) in a special type protective case. No need to replace it by breaker. | 3 Months | Corrected
Follow Up Inspection |  | 42 | New Finding: One phase/ two phase used in a three phase MCCB. | Use single pole/double pole instead of three phase MCCB. | Completed | May 12 2016 | On 06/04/2016: New timeline to solve the issue is 16th May,16. On 03/08/2016: Corrected. No such issue has been found. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Thermography scanning report is outdated. | Keep a thermography scanning record of your electrical system at lease twice a year. | Completed | Sep 3 2016 | On 19/10/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Transformer Oil Test report is available but not updated. | Check the transformer oil condition by performing oil test. Do it once in a year and keep the record. | Completed | Sep 3 2016 | On 19/10/2016: Not corrected. On 15/12/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: There is no programmed schedule for periodical inspection & testing of electrical equipment. | Develop an electrical maintenance program that includes inspections and testing of the electrical systems (preventive, proactive and breakdown maintenance). | Completed | Sep 3 2016 | On 19/10/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Safety program is initiated but has no influence. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. After the training, there should be exam to evaluate the influence of the training program. | Completed | Mar 9 2016 | On 19/10/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Light in store room/ storage areas is uncovered. | Lights in store room/ storage areas shall be covered. | Completed | Sep 3 2016 | On 19/10/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: No working separation between LT panel/s and HT unit/s (Transformer, HT switchgear). | A working separation between LT and HT must be ensured. A brick wall will do it; and adequate working clearance (1.07 m) and ventilation must be ensured. | Completed | Dec 20 2016 | On 15/12/2016: Not corrected. On 20/03/2017: Not corrected. On 02/07/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 49 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/ undersize. | Earth lead cable/ Earth Continuity Conductor (ECC) must be resized by half of the phase cable. Cable size shall be selected depending on the CB's response time and phase cables' size. | Completed | Jan 25 2016 | On 20/03/2017: Not corrected. On 02/07/2017: Not corrected. On 19/11/2017: Not corrected. ECC is inadequate. On 23/05/2018: Not corrected. On 05/02/2019: Not corrected. On 12/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Multiple cables connected at the bus bar and MCCB terminal. | Each power cable must be terminated at any point using single cable lug. | Completed | Jan 25 2016 | On 20/03/2017: Not corrected. On 02/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Distribution board's top/bottom is left open (typical issue). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. | Completed | Aug 15 2017 | On 19/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Hot spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Completed | Jul 15 2017 | On 19/11/2017: Corrected. No such issue was found during inspection. | 1 Week | Corrected
Follow Up Inspection |  | 53 | New Finding: Generators (182 KVA & 1000 KVA) have no interlocking capabilities. | There must be an interlock arrangement for protecting electrical system from any electrical fault. | Completed | Sep 16 2017 | On 19/11/2017: Not corrected. Both generators are connected through single ACB. On 23/05/2018: Not corrected. Only circuit breaker has been installed but interlocking system is not established. On 05/02/2019: Not corrected. On 12/01/2021: Corrected. Factory has disconnected 182 kVA genset from the system. | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: Earth pit resistance test is not recorded for all the pits. | Adequate number of earth pits must be ensured (if it's lower in numbers) and record must be made accordingly. | Completed | Aug 15 2017 | On 19/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding: Field information has no/less reflection in existing SLD. | Electrical SLD must be updated properly; all the required information must be mentioned there; and it shall be reviewed by ACCORD. | Completed | Jun 30 2018 | On 05/02/2019: Not corrected. On 12/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 56 | New Finding: Insulation resistance test report is generated without conducting any physical survey (fake report). | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | Corrected | Jun 30 2018 | On 05/02/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ Busbar. | Each electrical circuit must be terminated at single MCB/MCCB terminals. | Completed | Jun 30 2018 | On 05/02/2019: Not corrected. On 12/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: Loop connection has been used powering multiple circuits through MCB/MCCBs. | No loop connection shall be used; each single cable shall be terminated using cable lug (flat/I) at each terminal. Combo bus bar may be used (but incoming cable size must meet the rated capacity). | Completed | Jun 30 2018 | On 05/02/2019: Not corrected. On 12/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per cable current ampacity/load current; if adjustment is not possible, replacement will be the only way. | Completed | Jun 30 2018 | On 05/02/2019: Not corrected. On 12/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: Lights in the store room/ storage areas are uncovered/unprotected. | Lights in the store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. And a secure cabling shall be ensured. | Completed | Jun 30 2018 | On 05/02/2019: Not corrected. On 12/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Distribution board's/ TOB/generator terminal output box's top/bottom is left open (typical issue). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. | Completed | Jun 30 2018 | On 05/02/2019: Not corrected. On 12/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Unterminated live wire is kept inside the electrical panel/cable tray. | All the unterminated live power cables must be removed as soon as possible. | Corrected | Jun 30 2018 | On 05/02/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Manually operated machines (may have chance to be touched by operator/user) have no earth connection. | Manually operated each machine (may have chance to be touched by user/operator) must have earth connection. Cable selection shall be made per CB response and circuit's power demand. | Corrected | Jun 30 2018 | On 05/02/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 64 | New Finding: Electrical power cables are not identified properly. | Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables used in the system according to SLD. | Corrected | Jun 30 2018 | On 05/02/2019: Not corrected. On 12/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 65 | New Finding: Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07 m) around the transformer (and related electrical installations) must be maintained. | Corrected | Mar 5 2019 | On 12/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 66 | New Finding: Incoming power cable connected to panel board without any circuit breaker. | Provide incoming circuit breaker thus power can be cut off from a single point. | Corrected | Mar 5 2019 | On 12/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 67 | New Finding: Safety program is initiated but has no influence in the factory all electrical personnel. | Electrical safety training and awareness program for all electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. | Corrected | Feb 22 2023 | On 07/02/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 68 | New Finding: Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. | Corrected | Feb 22 2023 | On 07/02/2024: Not corrected. Some progress has been observed but bending still observed in few panels. RPO Comments: On 19-May-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 12/09/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 69 | New Finding: Transformer oil condition is not good according to test report. | Change the oil or centrifuge it. Then check the transformer oil condition by performing oil test. If the result is satisfactory then do it once in a year and keep the record. | Corrected | Feb 22 2023 | On 07/02/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 70 | New Finding: Field information has less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. | Work is in progress | Apr 20 2024 | On 12/09/2024: Not corrected. The factory sent the SLD to the RSC for review. The SLD is now under the review process. RPO Comments on 11-Dec-2024: the factory management reported the remediation completion. This item will be verified in the next inspection. On 09/07/2025: Not corrected. Factory has got SLD accepted from RSC on 26 September 2024. Progress has been observed in field (approx. 50%). Proper as build SLD has not been found as per accepted SLD. Mismatch has been observed in several places including cable identification missing, earthing layout mismatch, oversize CB, conductor information mismatch etc. RPO Comments: On 8-Jan-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. On 12/04/2026: Not corrected. Overall, approximately 65% progress has been observed. However, a few mismatches have been identified, such as earthing information mismatch for the 1000 kVA diesel generator, ECC missing in the MDB-generator, inadequate transformer neutral, oversized circuit breaker in the LT panel, missing cable identification in the LT panel, and improperly identified neutral cables in a few DBs. | 2 Months | In Progress
Follow Up Inspection |  | 71 | New Finding: Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07 m) around the transformer (and related electrical installations) must be maintained. | The factory has been relocated, and the equipment, materials, and cable trays have been rearranged to ensure a minimum working space of 1.07 m around the transformer area. | Apr 20 2024 | On 12/09/2024: Not corrected. The factory sent the transformer room layout to the RSC. It is now under the review process. On 09/07/2025: Not corrected. Factory has got layout accepted from RSC on 23 September 2024. Progress has been observed as space has been found proper in three side. But space is not proper in LT side and cables on the floor creating obstacle. On 12/04/2026: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 72 | New Finding: Insulation resistance record (cable information) doesn't match with field. | Field information must be reflected in the record. Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | Corrected | Mar 20 2024 | RPO Comments: On 19-May-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 12/09/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 73 | New Finding: PVC pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Corrected | Mar 20 2024 | RPO Comments: On 19-May-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 12/09/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 74 | New Finding: Lightning Protection System (LPS) is not installed properly. (Utility building LPS not as per standard, metal bonding missing, drawing inadequate, risk index calculations for all structures missing). | Factory shall redesign Lightning Protection System (LPS) as per standard and install accordingly. | Corrected | Mar 20 2024 | RPO Comments: On 1-Aug-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 12/09/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 75 | New Finding: Circuit breaker has no capacity information. | Each circuit breaker must have its own capacity information. | Corrected | Mar 20 2024 | RPO Comments: On 19-May-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 12/09/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 76 | New Finding: Combustible materials are attached with cable duct/channels. | Cable channels/ducts must be kept neat and clean; these must be free from all kind of combustible materials. | Corrected | Mar 20 2024 | RPO Comments: On 19-May-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 12/09/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 77 | New Finding: Lightning Protection System (LPS) is not installed in security building, where the risk index equal or greater than 40 (according to BNBC). | For factory buildings with a Risk Index of 40 or higher, a comprehensive Lightning Protection System (LPS) required to be designed as per standard for the entire facility. Once the LPS is properly designed, it must be installed according to the design specifications to ensure effective protection against lightning strikes. | The factory assigned a qualified LPS designer to prepare a proper Lightning Protection System (LPS) design and installed the Lightning Protection System (LPS) in accordance with the approved design, as per BNBC requirements. | Oct 9 2025 | RPO Comments: On 8-Jan-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. On 12/04/2026: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 78 | New Finding: Distribution boxes is inaccessible or cannot be opened to perform any maintenance work or inadequate clearance. | Each electrical distribution board or panel must be easily accessible, maintaining a minimum working clearance of 1 meter (or equal to the width of the board/panel, whichever is greater). The panel's height must not be exceed 2 meters, and the bottom must be at least 0.45 meters above from the floor or working platform (for wall-mount panel). The board/panel door must open at least 90 degrees to ensure safe and efficient operation and maintenance. | Work is in progress | Jun 12 2026 |  | 2 Months | In Progress