## Structural
Date
15-Apr-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Matrix Styles Ltd., Degerchala, National University Gazipur, Bangladesh-1704, Gazipur
Date of Inspection |  | 2015-03-08
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Highly-stressed column below water tank | Factory Engineer to review design, loads and columns stresses in area identified above. | Corrected | Mar 12 2016 | ON 24-Feb-2016:This issue will cover in DEA. Factory have submitted DEA on 29th-Oct-2016. Review mail has sent from Accord on 12th Jan,2016.Factory requires to submit revised DEA within 12th-March-2016.Previous timeline was 15-Feb-2016 ON 02- Nov-2016: This issue will be covered by EA. Factory has submitted EA to ACCORD on 27- Oct-2016 which is under review. On 04-May-2017: This issue is covered in EA. Factory has submitted EA to Accord which has been approved on 12 February 2017. On 24-May-2022: Corrected from previous follow up inspection. This issue had been covered in EA report. Factory got EA re-acceptance from ACCORD on 10-May-2018. On 08-Dec-2024: Corrected previously. On 07-Apr-2026: Previously corrected. During inspection, an undesignated small room adjacent to the north stair at the roof level, and an undesignated dining room were found on the 5th floor. The effect of the change was checked and found satisfactory. Factory is required to keep updated drawings on site. | (within 6-weeks) | Corrected
Initial Inspection |  | 2 | Highly-stressed column below water tank | Verify insitu concrete stresses by 100mm dia. cores from min. 4 no. columnsat ground floor level. | Corrected | Mar 12 2016 | ON 24-Feb-2016:Concrete cores have taken from structural elements(Beam, Column). ON 02-Nov-2016: Core has been taken from beams and columns to verify concrete strength. During inspection, Original core test report was found On 04-May-2017: Core test has been done. Factory provided original core test report during inspection. Core location was verified. On 24-May-2022: Corrected from previous follow up inspection. Core test had been done as a part of EA. Factory got EA re-acceptance from ACCORD on 10-May-2018. During inspection original core test report was available onsite. On 08-Dec-2024: Corrected previously. On 07-Apr-2026: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 3 | Highly-stressed column below water tank | Review water tank usage and if necessary implement an overflow to limit fill height in water tank. | Corrected | Mar 12 2016 | ON 24-Feb-2016:This issue will cover in DEA. Factory have submitted DEA on 29th-Oct-2016. Review mail has sent from Accord on 12th Jan,2016.Factory requires to submit revised DEA within 12th-March-2016.Previous timeline was 15-Feb-2016. ON 02-Nov-2016:This issue will be covered by EA. Factory has submitted EA to ACCORD on 27- Oct-2016 which is under review. On 04-May-2017: This issue is covered in EA. Factory has submitted EA to Accord which has been approved on 12 February 2017. On 24-May-2022: Corrected from previous follow up inspection. This issue had been covered in EA report. Factory had installed automatic sensor to restrict overflow. On 08-Dec-2024: Corrected previously. Factory had installed automatic sensor to restrict water flow. On 07-Apr-2026: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 4 | Discrepancy in structural drawings | Factory Engineer to amend as-built drawings to indicate the extent of brick chip aggregate used in construction. | Corrected | Mar 12 2016 | ON 24-Feb-2016:This issue will cover in DEA. Factory have submitted DEA on 29th-Oct-2016. Review mail has sent from Accord on 12th Jan,2016.Factory requires to submit revised DEA within 12th-March-2016.Previous timeline was 15-Feb-2016. ON 02-Nov-2016:This issue will be covered by EA. Factory has submitted EA to ACCORD on 27- Oct-2016 which is under review. On 04-May-2017: This issue is covered in EA. Factory has submitted EA to Accord which has been approved on 12 February 2017. On 24-May-2022: Corrected from previous follow up inspection. This issue had been covered in EA report. Factory got EA re-acceptance from ACCORD on 10-May-2018. On 08-Dec-2024: Corrected previously. On 07-Apr-2026: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 5 | Discrepancy in structural drawings | Make any other minor amendments to structural drawings to accurately reflect the as-built state (e.g. one additional column on west elevation) | Corrected | Mar 12 2016 | ON 24-Feb-2016:This issue will cover in DEA. Factory have submitted DEA on 29th-Oct-2016. Review mail has sent from Accord on 12th Jan,2016.Factory requires to submit revised DEA within 12th-March-2016.Previous timeline was 15-Feb-2016. ON 02-Nov-2016:This issue will be covered by EA. Factory has submitted EA to ACCORD on 27- Oct-2016 which is under review. On 04-May-2017: This issue is covered in EA. Factory has submitted EA to Accord which has been approved on 12 February 2017. On 24-May-2022: Corrected from previous follow up inspection. As built drawings were prepared as a part of EA. Factory got EA re-acceptance from ACCORD on 10-May-2018. On 08-Dec-2024: Corrected previously. On 07-Apr-2026: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 6 | Uncontrolled loading on 3rdfloor | Factory Engineer to assess load capacity for each floor. | Corrected | Mar 12 2016 | ON 24-Feb-2016: Uncontrolled loading has reduced. However load was found below 42 psf in storage areas at 3rd & 1st floor. After approval of DEA, factory requires to maintain final load plan. Before that Factory requires to maintain load below 42 psf.Previous timeline was 15-Feb-2016. ON 02-Nov-2016: During inspection, no load plan was observed. Loading was found less than 42 psf. Factory was suggested to submit load plan to ACCORD as soon as possible. On 04-May-2017: Factory has given notice that they will not use building 2 any longer. During inspection the building was found vacant. On 24-May-2022: Corrected from previous follow up inspection. Factory had provided a declaration letter that they are not using building-2 anymore. On 08-Dec-2024: Corrected previously. The factory had provided a declaration letter stating that they are no longer using building 2. It was found outside of the factory premises. On 07-Apr-2026: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 7 | Uncontrolled loading on 3rdfloor | Implement load plan at each level. | Corrected | Mar 12 2016 | ON 24-Feb-2016: Uncontrolled loading has reduced. However load was found below 42 psf in storage areas at 3rd & 1st floor. After approval of DEA, factory requires to maintain final load plan. Before that Factory requires to maintain load below 42 psf.Previous timeline was 15-Feb-2016. ON 02-Nov-2016: During inspection, no load plan was observed. Loading was found less than 42 psf. Factory was suggested to submit load plan to ACCORD as soon as possible On 04-May-2017: Factory has given notice that they will not use building 2 any longer. During inspection the building was found vacant. On 24-May-2022: Corrected from previous follow up inspection. Factory had provided a declaration letter that they are not using building-2 anymore. On 08-Dec-2024: Corrected previously. The factory had provided a declaration letter stating that they are no longer using building 2. It was found outside of the factory premises. On 07-Apr-2026: Previously corrected. | (within 6-months) | Corrected
Follow Up Inspection |  | 8 | New finding-1: 3-storied utility building-1 & 3-storied utility building-2 were found in the factory premises. | Factory engineer is required to prepared as built drawing along with design report and submit it to RSC accordingly. | In Progress | Jul 5 2022 | On 24-May-2022: During inspection newly constructed 3-storied utility building-1 & 3-storied utility building-2 were found in the factory premises. No documents available onsite. So, factory engineer is required to prepared as built drawing along with design report and submit it to RSC accordingly. On 08-Dec-2024: Factory has sent the documents to RSC on 9 December 2024 via email which is currently under review for submission. On 07-Apr-2026: Engineering Assessment (EA) of the Utility Building-1, Utility Building-2, with the proposed steel stair was accepted from RSC on 8 January 2026. For Utility Building-1, during the inspection, the grid line of the column/floor beam was found to be slightly different along grid 2/4, although the change doesn't affect the analysis result. Also, the core location was not found as per the accepted core layout. Subsequently, the factory engineer updated the drawing (in soft copy). Factory is required to keep an updated drawing (hard copy on site). For Utility Building-2, the as-built drawing couldn't be verified due to a lack of access to the 1st and 2nd floors (no stairs/ladder). In addition to that, one core from the column was not found, and core locations were not found as per the core layout. Factory is required to make arrangements to access the upper floors on the next inspection. Further, mark all core locations and update the core layout. Progress Status: 80% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 9 | New finding-2: 3-storied utility building-1 & 3-storied utility building-2 were found in the factory premises. | Complete remedial works if arising from design report after reviewed by RSC. | In Progress | Nov 24 2022 | On 24-May-2022: Any remedial actions arising from design report is required to be carried out by factory after acceptance of design report. On 08-Dec-2024: Any remediation work raised from the design report is required to be implemented after getting acceptance of design report. On 07-Apr-2026: As per the accepted EA, the factory was required to complete all retrofitting work at the Utility Building-2 by 1 April 2026, but till the inspection date, the factory had not completed the retrofitting work. (Only the construction of the proposed stair up to the pedestal column is completed). Progress Status: 30% | (within 6 months) | In Progress
Follow Up Inspection |  | 10 | New finding-3: Hairline crack on 5th floor beam and brick wall at several locations (Building-1). | The building engineer is required to identify all locations and repair the crack with a suitable method. | In Progress | Jan 20 2025 | On 08-Dec-2024: During inspection hairline crack was observed on 5th floor beam and brick wall (Building-1). The building engineer is required to identify all locations and repair the crack with a suitable method. On 07-Apr-2026: The factory has not repaired the cracked areas at all places. Progress Status: 20% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 11 | New finding-4: Corrosion on stair landing (Utility Building-2). | Provide rust-proof paint on steel members. | Corrected | Jan 20 2025 | On 08-Dec-2024: During inspection corrosion was observed on stair landing (Utility Building-2). Provide rust-proof paint on steel members. On 07-Apr-2026: The factory has provided rust proof paint on exposed rebar. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 12 | New finding-5: Non-structural storage racks were found not anchored/braced (Building-1). | Anchor/brace non-structural storage racks. | In Progress | Jan 20 2025 | On 08-Dec-2024: During the inspection, the non-structural storage racks were found not anchored/braced (Building-1). Anchor/brace non-structural storage racks. On 07-Apr-2026: The factory has anchored/braced nonstructural elements at most of the places. Anchor/brace all nonstructural elements. Progress Status: 70% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 13 | New finding-6: Undocumented structure (Security & Prayer room-Single storied RC structure plus Shed -area approximately 400 sft). Lack of as-built drawing. | Produce as-built drawing and keep on site. | Corrected | Jan 20 2025 | On 08-Dec-2024: During inspection, an undocumented structure was found on factory premises (Security & Prayer room-Single storied RC structure plus Shed -area approximately 400 sft) . As-built drawing was not available for this structure. The building engineer is required to produce as-built drawings and keep them on site. On 07-Apr-2026: As-built drawing was available on site and found satisfactory. | (within 6 weeks) | Corrected

## Fire
Date
15-Apr-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Matrix Styles Ltd., Degerchala, National University Gazipur, Bangladesh-1704, Gazipur
Date of Inspection |  | 2015-03-07
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Exit access corridors are not provided with 1 hr. fire resistance rating or approved NFPA 13 sprinkler system on ground floor. | Provide exit access corridors with 1 hr. fire resistance rating or approved NFPA 13 sprinkler system. | Corrected. See Pictorial Evidence. | Jun 21 2016 | 24/02/2016: Still no action has been taken. It is found same as it was before. 21/04/2016: No action has been taken yet. On 02/11/2016: No action has been taken yet. As per factory information factory will separate this corridors after receiving fire doors. Fire doors shipment has been done. On 5-1-2017: Same as before. On 30/03/2017: It was found same as it was before. On 11/07/2017: Work is in progress. On 02/07/2018: Not corrected. On 25/04/2019: Still in progress. On 18-Feb-2024: Corrected | Within 3 months | Corrected
Initial Inspection |  | 2 | Areas used for combustible storage open to the factory are not separated by firerated construction on 2nd and 3rd floors. | Provide defined storage areas and limit the storage arrangement as follows: Maximum height of 2.45m (8ft.) and maximum area of 23m2 (250 ft2) AND Separate areas of unenclosed combustible storage by a minimum clear distance of 3m (10ft.). | Corrected. 8th Follow-up Date:-02/07/2018 | May 21 2016 | 24/02/2016: Still no action has been taken. It is found same as it was before. 21/04/2016: In progress. Storage were found at several floors. On 02/11/2016: Store area has been found at 1st floor. On 5-1-2017: At 5th floor. On 30/03/2017: Store rooms are not separate from work area on 4th & 5th floor. On 11/07/2017: In progress. Factory shall follow the recommended store arrangement. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 3 | The exit stair enclosures are not separated from work areas and other spaces on each floor by fire-rated construction on all the floors. | The exit stair enclosure shall be provided with a minimum of 2-hr fire resistance rating for buildings 4 or more stories. | L/C against fire rated door has been opened at 08/09/16. See Pictorial Evidence. | Jun 21 2016 | 21/04/2016: In progress. They have installed most of the fire doors except for the one at office and at the building -2 where here is dinning. On 02/11/2016: Factory has completed civil work to seal openings & penetrations and factory has installed fire doors at exit stairs at six storied building but third party certified seal has not been found on hinge. It is required to submit all the third party certificates of fire doors and its equipment's. If fire doors are required to be held open for functional reasons then fire doors are required to interface with the fire alarm system. On 5-1-2017: Enclosure is created of required rating. On 30/03/2017: Corrected as per previous follow up. Factory has sealed exit stair enclosure penetrations. On 11/07/2017: Corrected as per previous follow up. On 02/07/2018: Corrected as per previous follow up. On 25/04/2019: Corrected as per previous follow up. On 18-Feb-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | The exit stairs are not separated from work areas and other spaces on each floor by firerated construction. | Provide minimum 1.5-hr fire rated doors for buildings that are 4 or more stories. Seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automaticclosing devices tied to the fire alarm system. Once fire doors are installed, every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets ACCORD standard 6.8.3.1. | Corrected. See Pictorial Evidence. | Jun 21 2016 | On 02/11/2016:Factory has installed fire doors at exit stairs at six storied building but third party certified seal has not been found on hinge. It is required to submit all the third party certificates of fire doors and its equipment's. If fire doors are required to be held open for functional reasons then fire door is required to interface with the fire alarm system. On 5-1-2017: Fire doors are not interfaced yet. On 30/03/2017: Factory has installed fire door in exit but interfacing is not done yet as per recommendation. On 11/07/2017: Fire rated door was found installed but interfacing work is still pending. Factory was keeping the doors open through some external sources. Besides fire door installation work is still pending at north-west exit stair on ground floor. On 02/07/2018: In progress. Interfacing work is going on. Fire door installation work is still pending at north-west exit stair on ground floor. On 25/04/2019: Fire doors were found open through some external sources. Besides south-exit stair were not properly separated from ground floor. Unseal penetration observed in north-west exit stair. On 18-Feb-2024: Corrected. Fire doors were found functional. | Within 3 months | Corrected
Initial Inspection |  | 5 | Building did not have stair designation signs, occupant load signs and emergency evacuation plans at required locations on all the floors. | Provide stair designation signs, occupant load signs and emergency evacuation plans at required locations. | Done | May 21 2016 | 21/04/2016: Partially corrected. They have both stair designation sign and evacuation plan. But the occupant load is not pasted in the stair wall of each floor. On 02/11/2016: Only floor level and emergency evacuation plan has been found during follow up inspection. On 5-1-2017: Corrected. On 30/03/2017: Corrected as per previous follow up. Note: Factory shall update stair designation sign. On 11/07/2017: Corrected. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Immediately | Corrected
Initial Inspection |  | 6 | Fire drills are not performed as required by ACCORD standard. | Fire drills shall be conducted on a quarterly basis in accordance with ACCORD standard 13.2. | Still we are in set up position. All set up will be available soon. After that we will make actual fire drills. | Apr 21 2016 | 24/02/2016: Still no action has been taken. It is found same as it was before. 21/04/2016: Corrected. On 02/11/2016: Corrected. It is required to update the fire drill conducted events as well as records. On 5-1-2017: Corrected. On 30/03/2017: Corrected as per previous follow up. On 11/07/2017: Corrected. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Immediately | Corrected
Initial Inspection |  | 7 | Egress doors and gates with locking features are provided at exit discharge on ground floor. All gates were open and unlocked during inspection. | Remove locking features from all egress doors and gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101 and ACCORD standard 6.8.2. | It's for Building 2, we have already requested to release that building as we don't have any operation in that building. | Apr 28 2016 | 24/02/2016: Locking features has been found in ground floor . 21/04/2016: In progress. All the locking features has been removed except for the interior exit discharge of the building-2. On 02/11/2016: Corrected. Locking feature has not been found at building-1 and building-2 has not been found in operations. On 5-1-2017: Corrected. On 30/03/2017: Corrected. During follow up inspection non-compliant locking features were not found in egress routes exit doors/gates. On 11/07/2017: Corrected. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Immediately | Corrected
Initial Inspection |  | 8 | Storage was located in the egress path on ground, 2nd and 3rd floors. | Keep egress paths and stairs clear of storage. | Corrected | May 21 2016 | 24/02/2016: Storage has been found in ground floor egress corridor. 21/04/2016: In progress. Storage were located in the egress discharge of building 2. On 02/11/2016: Corrected. Egress path has been found free from storage. On 5-1-2017: Corrected. On 30/03/2017: Corrected. During follow up inspection storage was not found in exit stair enclosure and egress paths. On 11/07/2017: Corrected. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Immediately | Corrected
Initial Inspection |  | 9 | Storage was located in the exit stair on ground floor. | Remove all storage from exit stairs and egress paths. | We will keep exit stairs and egress paths clear of storage. | Apr 21 2016 | On24/02/2016: Storage has been found inside exit enclosure. Electrical panel has been removed. 21/04/2016: Corrected. Solenoid valves have been found in the exit stairs enclosure bottom. On 02/11/2016: Corrected. Small electrical system has been found underneath of east side exit stair which is required to remove. On 5-1-2017: Corrected. On 30/03/2017: Corrected. During follow up inspection storage was not found in exit stair enclosure and egress paths. On 11/07/2017: Corrected. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Immediately | Corrected
Initial Inspection |  | 10 | Collapsible gates are provided at exit discharge on ground floor. | Replace all gates along the means of egress with sidehinged, swinging egress doors in accordance with ACCORD standard 6.8.1. | It's for Building 2, we have already requested to release that building as we don't have any operation in that building. | Apr 28 2016 | 24/02/2016: Shutter has been found in both exit discharge which is required to remove immediately. 21/04/2016: In progress. All on compliant gates have been removed except for the main gate at building-2. On 02/11/2016: Corrected. Non-compliant gate has not been found at building-1 and building-2 has not been found in operations. On 5-1-2017: Corrected. On 30/03/2017: Corrected. During follow up inspection non-compliant doors/gates were not found in egress routes. On 11/07/2017: Corrected. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 11 | The width of egress aisles is less than 36-in on 3rd floor. | Provide minimum aisle widths of 36-in. | Done | May 21 2016 | 24/02/2016: Aisle widths of 36-in has been found blocked by storage. 21/04/2016: In progress. Aisles were not found at certain place of storage. On 02/11/2016: Proper aisles has not been found at 5th floor. On 5-1-2017: Corrected. On 30/03/2017: Corrected. On 11/07/2017: Corrected. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 12 | Exit stairs serve more than 5 stories and do not have required reentry provisions on all the floors. | Every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets ACCORD standard 6.8.3.1. | Since there is no need of installing fire doors. So there will be no problem with Re-Entry. Everybody can move one stair to another stair easily. And there are no locking system in any exit stair on each floor. | Apr 21 2016 | 24/02/2016: Factory is in progress providing re-entry system in fire rated door . 21/04/2016: Corrected On 02/11/2016: Corrected. On 5-1-2017: Corrected. On 30/03/2017: Corrected as per previous follow up. On 11/07/2017: Corrected. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 13 | Northwest and southeast exit stairs discharge inside the building in store area and production area on ground floor. | Provide 2-hr fire-rated exit passageway leading directly outside (vestibules to separate any storage areas). | Corrected. See Pictorial Evidence. | Jun 21 2016 | 24/02/2016: Still no action has been taken. Need to separate bonded storage and working area. . 21/04/2016: No action has been taken. On 02/11/2016: No action has been taken yet. As per factory information factory will start this job after receiving fire doors. Fire doors shipment has been done. On 5-1-2017: Not started yet. On 30/03/2017: It was found same as it was before. On 11/07/2017: Work is in progress. On 02/07/2018: Work is in progress. On 25/04/2019: Unseal opening and penetrations were observed. On 18-Feb-2024: Corrected. Factory shall keep the corridor free of temporary storages. | Within 6 months | Corrected
Initial Inspection |  | 14 | There is no fire alarm currently installed. | Install a new, listed addressable fire alarm system in accordance with NFPA 72. | New FADS drawing has been reviewed and approved by RSC. LC and shipment of the related products has done. Hopefully, we will get the products by end of Feb-26. We will start the work accordingly. | May 21 2016 | On 24/02/2016: Rectification work has been started. Need to complete the works as per ACCORD recommendation. 21/04/2016: In progress. They have installed the system. The system needs to be tested and commissioned. As built drawing must be present at site. On 02/11/2016: Accord reviewed design was found on site during follow up inspection. Factory has installed the fire alarm system but certification label has not been found on installed cable. It is required to submit certificates for all equipment of fire alarm system. On 5-1-2017: Installation is done. Factory has to prove the acceptance of alarm cable. Backup power for panel needs to be ensured. On 30/03/2017: Fire alarm system drawing has been reviewed by Accord. Modification work is in progress. On 11/07/2017: Reviewed design was available. Interfacing work is still pending. On 02/07/2018: Work is going on. On 25/04/2019: Installation work almost completed. Reviewed design was available. On 09/02/2023: T&CVI found that fire alarm and detection system is not Approved. See details in the T&CVI report. On 18-Feb-2024: Factory is waiting for T&CVI. On 12/06/2024: T&CVI found that, the FADS system is not approved. Please see the T&CVI report for details. RPO Comments: On 22-Feb-2026 the design documents FADS have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design by 2-May-2026. | Design within 4 months, install within 9 months | In Progress
Initial Inspection |  | 15 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10. | We inspect, test and maintain the portable fire extinguishers and keep written records onsite. | Apr 21 2016 | 24/02/2016: ITM shall be as per ACCORD standard. 21/04/2016: Corrected On 02/11/2016: Corrected. It is required to maintain this checklist for all fire extinguishers. On 5-1-2017: Corrected. On 30/03/2017: Corrected as per previous follow up. On 11/07/2017: Corrected. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 16 | Fire department connection is not provided. | Provide fire department connection in accordance with ACCORD standard 5.5.4. | Need more time since all set up are in progress. | Jul 13 2015 | 24/02/2016: FDC has been provided. Corrected. 21/04/2016: Corrected. On 02/11/2016: Corrected. On 5-1-2017: Corrected. On 30/03/2017: Corrected as per previous follow up. On 11/07/2017: Corrected as per previous follow up. On 02/07/2018: Corrected as per previous follow up. On 25/04/2019: Corrected as per previous follow-up. On 18-Feb-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 17 | Once fire alarm is installed provide fire alarm ITM. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with NFPA 72. | Still we are in set up position. We will able to complete it at given time. | Apr 21 2016 | 24/02/2016: Still no action has been taken. It is found same as it was before. 21/04/2016: Corrected On 02/11/2016: Corrected. Factory is maintaining the checklist for the existing system. On 5-1-2017: Corrected. Note: Proper maintenance is not anticipated. On 30/03/2017: Corrected. Factory management is maintaining and keeping existing fire alarm system maintenance records on-site. On 11/07/2017: Corrected. Factory is maintaining a standard checklist for their existing system. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 18 | Once standpipe system is installed provide standpipe ITM. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 14. | Still we are in set up position. We will able to complete it at given time. | Apr 21 2016 | 24/02/2016: ITM will be completed after installation of the standpipe and hose system as per NFPA 14 as rectification of standpipe system has been started as per reviewed design from 21/04/2016: Corrected On 02/11/2016: Corrected. Factory is maintaining the checklist for the existing system. On 5-1-2017: Corrected. On 30/03/2017: Corrected. Factory management is maintaining and keeping existing standpipe system maintenance records on-site. On 11/07/2017: Corrected. Factory is maintaining a standard checklist for their existing system. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 19 | There is currently no standpipe system installed. | Install a new standpipe system in accordance with ACCORD standard 5.4 and NFPA 14. A class III system shall be installed in buildings with the highest occupiable floor 10 m (33 ft.) above grade or more. A class I system shall be permitted in buildings protected throughout by an approved automatic sprinkler system. | Fire Seperation issue: CAP no: 6. Fire rated collar design - Reviewed and approved by RSC. We have finalized the Quotation. Hopefully, the work will start within this week. After completion the work we will send all SUPS related documents to RSC. | May 21 2016 | On 24/02/2016: Still no action has been taken. It is found same as it was before. 21/04/2016: In progress. The as built drawing was not present at site. The system installation has been almost completed. The system needs to be tested and commissioned. On 02/11/2016: Accord reviewed design was found on site during follow up inspection. Factory has installed only electrical driven pump and certification label has not been found on installed pump and equipment. On 5-1-2017: Same as before. On 30/03/2017: Standpipe system drawing has been reviewed by Accord. Still factory has not opened L/C for fire pump. On 11/07/2017: Reviewed design was available. However factory didn't open L/C yet for fire pump. On 02/07/2018: L/C has not been opened for fire alarm system. On 25/04/2019: L/C has been opened for fire protection system. On 18-Feb-2024: Pre-T&C found that the standpipe system is not ready for full T&CVI. Desktop document verification is required. See detail in the Pre-T&C report. On 12/06/2024: T&CVI found that, the SUPS system is not approved. Please see the T&CVI report for details. On 17/04/2025: T&CVI found that SUPS is not approved. See details in T&CVI report. RPO Comments: On 22-Feb-2026 the SUPS T&CVI documents are pending to be submitted to RSC. | Within 6 months | In Progress
Initial Inspection |  | 20 | The building is not provided with any smoke detection. | Provide automatic smoke detection throughout the building, tied into the fire alarm system, in accordance with NFPA 72. | New FADS drawing has been reviewed and approved by RSC. LC and shipment of the related products has done. Hopefully, we will get the products by end of Feb-26. We will start the work accordingly. | May 21 2016 | On 24/02/2016: Rectification of standpipe system as per reviewed design from ACCORD has been started. Moreover two running compressor have been found inside pump room. Need to separate compressors from pump room by 2-hr fire rated separation. 21/04/2016: In progress. It is an integrated part of AFA System. Yet detectors were missing at building 2. On 02/11/2016: It is an integrated part of automatic fire alarm system. On 5-1-2017: Detection system has been installed but final testing shall be done by Accord. On 30/03/2017: It is an integrated part of fire alarm system. On 11/07/2017: It is an integrated part of fire alarm system. On 02/07/2018: It is an integrated part of fire alarm system. On 25/04/2019: It is an integrated part of fire alarm system. On 18-Feb-2024: It is an integrated part of fire alarm system. On 12/06/2024: T&CVI found that, the FADS system is not approved. Please see the T&CVI report for details. RPO Comments: On 22-Feb-2026 the design documents FADS have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design by 2-May-2026. | Within 9 months | In Progress
Initial Inspection |  | 21 | Exit signage were not provided in the building. | Provide exit signs above all building exits to the exterior, all doors to the exit stairs and along all paths of travel where a change of direction is not obvious. | Exit signs above all building exits to the exterior, all doors to the exit stairs and along all paths of travel are done. | May 13 2015 | 24/02/2016: Exit signage has been provided. 21/04/2016: Corrected. The exit sign should have both English and local language. On 02/11/2016: Corrected. It is required to installed exit signage at 5th floor east exit stair. On 5-1-2017: Corrected. On 30/03/2017: Corrected as per previous follow up. On 11/07/2017: Corrected. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 22 | Inspection, testing and maintenance for the emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | Emergency lighting system set up are in progress. We expect to completed this on given time. | Apr 21 2016 | 24/02/2016: Still no action has been taken. It is found same as it was before. 21/04/2016: Corrected On 02/11/2016: Corrected. Factory is maintaining the checklist. On 5-1-2017: Corrected. On 30/03/2017: Corrected. Factory is keeping emergency & exit light maintenance checklist record on-site as per Accord standard. On 11/07/2017: Corrected. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 23 | There was no emergency lighting installed in the factory. | Provide a minimum illumination of 10 lux at the floor level within exit stairs and along exit discharge paths and a minimum 2.5 lux along exit access aisles. | We installed the emergency lighting system. Installation are in progress. We expect to completed on given time. | Apr 21 2016 | 24/02/2016: Still no action has been taken. It is found same as it was before. On 21/04/2016: Corrected. On 02/11/2016: Corrected. It required to increase the light quantity to increase the illumination level. On 5-1-2017: Corrected. On 30/03/2017: Corrected as per previous follow up. Note: Factory shall ensure that emergency light illumination level on aisles are adequate. On 11/07/2017: Corrected. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 24 | NEW FINDING: Unsealed penetrations and openings are located in the fire-rated floor /ceiling assemblies | Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor level. | Corrected. 8th Follow-up Date:-02/07/2018 | May 24 2016 | 24/02/2016: New Finding. 21/04/2016: Partially corrected. The sealing must be done as per Accord Standard. On 02/11/2016: Factory has sealed the penetrations by nonrated materials (rock wool and cock sheet). It is required to seal the penetrations by fire rated materials. On 5-1-2017: Partially corrected. Factory has to provide certification for sealing material. On 30/03/2017: Partially corrected. On 11/07/2017: Partially corrected. Factory was unable to show any certificated of the used product. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 25 | New finding (4th follow up): Fire pump room is not seperated by fire rated construction. | Separate the fire pump room by a minimum 2-hrs fire rated construction. | Corrected. 8th Follow-up Date:-02/07/2018 | Nov 30 2016 | On 2-11-2016: New finding 4th follow up On 5-1-2017: Not started. On 30/03/2017: No action has been taken yet. On 11/07/2017: Fire door installation work is still pending. On 02/07/2018: Corrected. On 25/04/2019: In progress. Open with south-east discharge path on ground floor. On 18-Feb-2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 26 | New finding (4th follow up): Rooms used for storage of combustible materials are not separated from the surrounding occupancy/areas at 5th floor and ground floor. | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour construction. | Corrected. See Pictorial Evidence. | Nov 30 2016 | On 2-11-2016: New finding 4th follow up On 5-1-2017: No action has been taken. On 30/03/2017: It was found same as it was before. On 11/07/2017: Accessories store room on 5th floor is not separated from sample and office section. Fire door installation work is in progress for finished fabric store and bonded ware house on 4th and ground floor. On 02/07/2018: In progress. On 25/04/2019: In progress. Doors were found open through some external sources. Besides double leaf fire doors were not closing properly as door coordinator was not fully functional. On 18-Feb-2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 27 | New finding (4th follow up): The day-care room is located at ground floor which is not separated from store room and does not have direct access to an exit. | 1. Provide a direct access from daycare room to exit stair. [if the daycare is located at 1st floor] or 2. Provide a minimum 2-hr fire-rated exit corridor between the day-care room and exit stair. or 3. Relocate day-care room to ground floor with maximum travel distance of 9m (30 ft). | The Fire rated doors are already in-house. The construction work is going on .The installation will be finished by 15/06/2017.See Pictorial Evidence. | Nov 30 2016 | On 2-11-2016: New finding 4th follow up On 5-1-2017: No action has been taken. On 30/03/2017: No action has been taken. On 11/07/2017: No action has been taken. On 02/07/2018: In progress. On 25/04/2019: Corrected as childcare was not found and factory is using it as pump room. On 18-Feb-2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 28 | New Finding in 5th follow-up: The ground floor air compressor is not separated by fire-rated construction. Location: Ground Floor | Separate the air compressor by a minimum 1-hr fire-rated construction for non-high rise, and 2-hr fire rated construction for high rise. Seal and/or protect all openings to maintain the required fire separations. When located to the exterior of a building, 3m (10 ft.) separation is required. Provide proper ventilation and consult a qualified engineer. | Corrected. 8th Follow-up Date:-02/07/2018 | Mar 5 2017 | On 05/01/2017: NEW FINDING (5TH) On 30/03/2017: No action has been taken. On 11/07/2017: Factory has installed fire door however installation of magnetic door hold device is still pending. Beside unseal penetration was found. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 29 | New Finding (On 30/03/2017): During follow up inspection parapet height was found 31 inches in the main building roof. | Provide parapets or guards for all occupied roofs of a minimum height of 1067 mm (42 in.) as required. | Corrected. 8th Follow-up Date:-02/07/2018 | Apr 29 2017 | New Finding On 11/07/2017: No action has been taken yet. On 02/07/2018: Corrected. On 25/04/2019: Corrected. On 18-Feb-2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 30 | New Finding in 7th Follow-up: Flammable liquid storage (CNG gas cylinder) area is not separated by fire-rated construction (openings, non-rated doors, penetrations). Location: In front of boiler room. | Separate the hazardous materials / flammable liquid storage room by a minimum 2-hr fire-rated construction. Seal and/or protect all openings to maintain the required fire separations | Corrected. 8th Follow-up Date:-02/07/2018 | Aug 11 2017 | New Finding On 02/07/2018: Corrected. On 25/04/2019: Corrected. Not found. On 18-Feb-2024: Corrected. Not found during the inspection. | Within 1 month | Corrected
Follow Up Inspection |  | 31 | New Finding in 9th Follow-up: Dining area is not separated from other occupancies with fire rated assemblies. Location: 5th Floor. | Re-locate the dining area or separate the dining area from other occupancies with 2-hr fire rated construction. | Corrected. Date:-10/10/2019 but accord next time not follow-up. Please See the Pictorial Evidence. | May 25 2019 | New Finding On 18-Feb-2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 32 | New Finding in 9th Follow-up: Manual on-off switch is provided for [emergency lighting / exit signage] units. | Remove manual on/off switches from [emergency lighting /exit signage] units to prevent them from being switched off | Corrected. Date:-10/10/2019 but accord next time not follow-up. Please See the Pictorial Evidence. | May 25 2019 | New Finding On 18-Feb-2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 33 | New finding (11th Follow-up): Elevator shafts directly open into exit enclosure which is a violation of RSC Technical Guidelines (Standard)-6.14.3. Location: South exit stair enclosure of the main production building. | Provide required rating to ensure 2-hr seperation of the elevator shaft. As per 6.14.3 of RSC Technical Guidelines (Standard) V1.0, Openings into an exit enclosure other than unprotected exterior walls shall be limited to those necessary for exit access to the enclosure. An exit stairway shall not be built around a lift shaft unless both of them are located in a smoke proof enclosure and made of a material with fire resistance rating required for the type of construction of smoke proof enclosure. | We have started the work. The Fire doors has been installed for the lift seperation. Some civil work is ongoing. Hopefully the work will be completed by this week. | Jul 13 2024 | On 18-Feb-2024: New finding. RPO Comments on 22-Feb-2026: The factory management has not yet completed their remediation work. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 4 months | In Progress
Follow Up Inspection |  | 34 | New Finding (11th Follow-up): Electrical panels were observed inside the south exit stair enclosure on the ground floor of the main production building. | Remove/relocate the electrical panels from the exit stair enclosure. | Done. Please see the pictorial evidence in attachment. | Apr 13 2024 | On 18-Feb-2024: New finding. RPO Comments: On 20-Feb-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification

## Electrical
Date
15-Apr-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Matrix Styles Ltd., Degerchala, National University Gazipur, Bangladesh-1704, Gazipur
Date of Inspection |  | 2015-03-07
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Electrical Single Line Diagram (SLD) has inadequate information, and thus is unusable. | Prepare an accurate SLD with all necessary information, so any experienced person will then be able to understand the system. | Done | May 30 2016 | On 24/02/16: This Issue is not corrected. New timeline to 30th April, 2016. On 21/04/16: Not Corrected. New committed timeline: May 30, 2016. On 02/11/2016: Still not corrected. On 05/01/2017: Not corrected. One DB drawing is missing and found few mismatch with the existing system, SLD is not updated. On 30/03/2017: Corrected. | 12 Weeks | Corrected
Initial Inspection |  | 2 | Thermographic scanning of the entire electrical system has not been performed. | Thermographic scanning of the entire electrical system must be performed twice in a year. | Done | Jun 13 2015 | On 15/09/15: Corrected. | 8 Weeks | Corrected
Initial Inspection |  | 3 | Insulation resistance test of electrical equipment is not performed. | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this requires a complete power shut off). | Done | Jun 13 2015 | On 15/09/15: Corrected. | 8 Weeks | Corrected
Initial Inspection |  | 4 | Earth Pit resistance record is unavailable. | Record earth pit resistances for all the earth pits, and do it once a year. | Done | Jun 13 2015 | On 15/09/15: Corrected. | 8 Weeks | Corrected
Initial Inspection |  | 5 | Electric safety program is not initiated. | Electrical safety training and awareness program for the electrical personnel and workers must be initiated and recorded. | Done | Feb 1 2016 | On 24/02/16: Corrected. | 8 Weeks | Corrected
Initial Inspection |  | 6 | Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is missing. | Hang this first aid and CPR instructions near all electrical equipment (LT panel, MDB, FDB, DB, SDB) on a visible location. | Done | Jun 13 2015 | On 15/09/15: Corrected. | 8 Weeks | Corrected
Initial Inspection |  | 7 | Maintenance records are unavailable for total electrical installations. | Maintenance Manager or Safety Officer must keep accurate records and ensure that they reflect actual factory day to day operations. | Done | Feb 1 2016 | On 24/02/16: Corrected. | 8 Weeks | Corrected
Initial Inspection |  | 8 | Factory has installed Lightning Protection System, but the layout plan is not sufficiently clear and the design calculations are not available. | Have a qualified engineer to create correct layout drawings for the LPS, then submit LPS design to Accord for approval. | Done | May 30 2016 | On 24/02/16: This Issue is not corrected. New timeline to resolve this issue is 30th April, 2016. On 21/04/16: Not Corrected. New committed timeline: May 30, 2016. On 02/11/2016: Still not corrected. On 05/01/2017: Not corrected. On 30/03/2017: Corrected. | 16 Weeks | Corrected
Initial Inspection |  | 9 | No separation between proposed LT panels and HT units (transformer, HT switchgear). | Make a brick built separation between LT and HT units; ensure that after making separator you have adequate ventilation (cross ventilation) and safe working clearance around each electrical equipment. | Done | May 28 2015 | On 24/02/16: Corrected. | 6 Weeks | Corrected
Follow Up Inspection |  | 10 | New Finding: Cables are hanging without proper support. Cable terminals may be in tension. | Use cable tray/ladder to support cables at any where to keep cable out of tension. | Done | Apr 30 2016 | On 24/02/16:This Issue is not corrected. New timeline to resolve this issue is 30th April, 2016. On 21/04/16: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 11 | New Finding: No cover on the cable trench. | Metallic cover (checkered plate) should be provided on cable trench to prevent the damage of cable insulation or falling of operator. | Done | Apr 30 2016 | On 24/02/16:This Issue is not corrected. Wooden Cover is in use. New timeline to resolve this issue is 30th April, 2016. On 21/04/16: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 12 | New Finding: Generator body has been earthed by one earthing connection. | Ensure minimum two earthing connection for generator body (consult with your generator supplier). | Done | Nov 1 2015 | On 24/02/16: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 13 | New Finding: Cables entering or exiting generator panel are not firmly fixed. | Cables entering panel must be firmly fixed through base plates using cable glands. | Done | Oct 10 2015 | On 24/02/16: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 14 | New Finding: Transformer silica gel is discolored. | Replace silica gel by a new one; or dry it under sun and reuse it, if color regains. | Done | Mar 30 2016 | On 21/04/16: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 15 | New Finding: Excess HT cable length not supported. | Excess length of existing HT cables coiled near panel must be protected and laid safely. | Done | Apr 30 2016 | On 21/04/16: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 16 | New Finding: Large exhaust fans in production floors are directly Controlled by the MCB (typical issue). | Large exhaust fans must be connected through Control device (DOL Starter) such that it will not restart automatically when power is restored. | Done | Apr 30 2016 | On 21/04/16: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 17 | New Finding: Oil leakage has been observed from transformer. | Stop oil leakage from transformer and keep clean top of transformer. | Done | Mar 31 2016 | On 21/04/16: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 18 | New Finding: Phase barrier/ separator has not installed. | Put purposely made phase separator (rubber type) between two phases; also terminate cables by proper sized cable lugs and cover cable lugs by heat shrink. | Done | Mar 30 2016 | On 21/04/16: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 19 | New Finding: Multiple cables terminated at MCCB terminals/ Bus bar. | Terminate each power cable at single terminal and use proper sized cable lug. | Done | Mar 30 2016 | On 21/04/16: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 20 | New Finding: Cables/wires passing through wall not protected and remaining gaps around the cable/wiring not sealed. | Cables/wirings passing through permanent wall must be protected and remaining gaps must be sealed with fire resistant materials. | Done | May 30 2016 | On 21/04/16: Not Corrected. New committed timeline: May 30, 2016. On 02/11/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 21 | New Finding: Panel base plate removed to allow cable entry. | Panel base plate must be installed and cable(s) entering panel must be firmly fixed with cable gland. | Done | Mar 31 2016 | On 21/04/16: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 22 | New findings: Cable duct is left open. | Cover it with the electrical graded materials, clean it at certain interval and keep records of cleaning. | Done | Mar 31 2016 | On 21/04/16: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 23 | New Finding : Unused openings for cable passing on the top of distribution board is left open. | Cover all of the unused openings by insulated rubber caps. | Done | Mar 31 2016 | On 21/04/16: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 24 | New Finding: No separation in the generator room from electrical equipment's which belong to the building owner. | Make a brick built separation up to the ceiling between generator and surroundings; ensure that after making separator you have adequate ventilation (cross ventilation) and safe working clearance around the generator. | Done | May 30 2016 | On 21/04/16: Not Corrected. New committed timeline: May 30, 2016. On 02/11/2016: Still not corrected. On 05/01/2017: Not corrected. Inadequate working clearance around the generators. On 30/03/2017: Not Corrected. On 11/07/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 25 | New Finding: Earth pits are not identifiable & Earth connections are not segregated. | Identify each earth pit and mark it for periodic maintenance purpose. Ensure separate earthing connection for Generator body, transformer body, Electrical system and Lightning Protection System. | Done | May 30 2016 | On 21/04/16: Not Corrected. New committed timeline: May 30, 2016. On 02/11/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 26 | New Finding: Cables in service are joined (splicing) between terminations. | Joints of cable shall be avoided. For unavoidable cases, existing cables with joints must be spliced using butt splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. | Done | May 30 2016 | On 02/11/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding: Cables are laid on floor without any support. | Provide cable tray inside cable drain and cover it by checkered plate. | Done | Nov 30 2016 | On 02/11/2016: Still not corrected. New committed timeline given till 30/11/2016. On 05/01/2017: Not corrected. Cables are hanging without support. On 30/03/2017: Not Corrected. On 11/07/2017: Not corrected. Cables are hanging without support. On 25/10/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding: Metal Channels or any other metal work is not connected with main earth (CPC bonding). | Ensure CPC (Circuit Protective Conductor) bonding for all metal lines and structure where there is risk of getting electrocuted. | Done | Feb 15 2017 | On 05/01/2017: Not corrected. Exhaust fan body and fan blade enclosure has no earth connection. Time extension is given till 15/02/2017. On 30/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding: Transformer body earthing & neutral earthing is inadequate/undersized. | Two separate and distinct earth connection for body & one separate and distinct Neutral earth connection must be provided for Transformer. Neutral must have earth connection with half of phase conductor. Or follow manufacturer/ suppliers recommendation. | Done | Nov 30 2016 | On 05/01/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 30 | New Finding: Hazardous lights in store room/storage areas are uncovered. | Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. | Done | Feb 15 2017 | On 30/03/2017: Corrected. No hazardous lights were found above storage area. | 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: Number of earth pits are inadequate for the factory. | Adequate number of earth pits must be ensured for the factory with proper earth lead and earth electrode size as mentioned in BNBC requirements. mixing all together shall be avoided. | Done | Feb 15 2017 | On 30/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 32 | New Finding: Transformer Silica gel is discolored. | Silica gel shall be changed; or reuse can be done, if color regains after sundry. | Done | Feb 15 2017 | On 30/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (BBT). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Done | Feb 15 2017 | On 30/03/2017: Not Corrected. On 11/07/2017: Not corrected. On 25/10/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 34 | New Finding: Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ Busbar. | Each electrical circuit must be terminated at single MCB/MCCB terminals. | Done | Feb 15 2017 | On 30/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 35 | New Finding: Distribution boards have no clear identification markings. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. | Done | Feb 15 2017 | On 30/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 36 | New Finding: Panel doors are not connected with earth. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | Done | Feb 15 2017 | On 30/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Done | Jul 30 2017 | On 25/10/2017: Corrected. Not found during inspection. | 2 Weeks | Corrected
Follow Up Inspection |  | 38 | New Finding: Field information has less reflection in existing SLD. Electrical power cables are not identified properly. | Electrical SLD must be updated properly when electrical system is modified. Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables used in the system according to SLD. | Done | Aug 10 2018 | On 25/04/2019: Not Corrected. SLD needs modification. On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 39 | New Finding: Hazardous lights in store room/storage areas are uncovered. | Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. | Done | Aug 10 2018 | On 25/04/2019: Not Corrected. On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: Power sockets are hung without proper support. | Power socket has to be installed on rigid support/base securely and at minimum 200mm above floor level. | Done | May 30 2019 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Transformer breather oil cup is empty. | Transformer breather oil cup must be filled up to the oil mark on the cup. | Done | May 30 2019 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Distribution boards, electrical power cables and circuit breakers are not identified properly. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. Proper identification shall be done on power cables, circuit breakers used in the system according to SLD. | Done | May 30 2019 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Power cables entering or exiting from Distribution board/panel are not properly fixed. | Power cables entering or exiting from distribution board/panel must be fixed through Panel base/top plate using proper sized cable glands (metal/PVC). | Done | May 30 2019 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Lead acid battery terminals are left open. | Lead acid battery terminals must be covered/capped and rust must be checked and cleaned. | Done | May 30 2019 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Generator room is filled with debris (or used as temporary storage). | Generator room must be kept neat and clean. | Done | May 30 2019 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Periodicity of thermographic survey is not continued. | Thermography survey shall be conducted on entire electrical system in the facility at least twice in a year. And the remediation suggestions mentioned in the report shall be carried out. | Done | May 30 2019 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per connected load current; if adjustment is not possible, replacement will be the only way. | Done | May 30 2019 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/undersize. | Earth lead cable/ Earth Continuity Conductor (ECC) shall be determined according to BNBC or Adiabatic method (considering CB's response time, fault current & type of earth conductor other factors). | Done | May 30 2019 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Improper termination at busbar. | Heat shrink tube must be properly removed from the termination point before terminating cable on busbar thus there will be no insulation material in between cable lugs and copper busbar. | Done | May 30 2019 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Maintenance movement is obstacle due to uneven height of cable trench in utility area (transformer room). | Work place around transformer (or other electrical installation) must be on same height. | Done | May 30 2019 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: PVC pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Done. Please see pictorial evidence. | Dec 20 2023 | On 09/06/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Inadequate working space around transformer for performing maintenance work. | Adequate working clearance and proper ventilation must be maintained in accordance with RSC technical guidelines. This ensures the safe operation of electrical systems, prevents cross-contamination between LT and HT sections, and enhances overall safety and operational efficiency. Access needs to be restricted to qualified personnel wearing appropriate PPE (Personal Protective Equipment). | In progress | Mar 15 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 53 | New Finding: The 11 kV power cables laid on the substation room floor are creating obstacles in the working areas. | HT cables shall be rerouted avoiding obstacles in the working areas of electrical installations. | In progress | Mar 15 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 54 | New Finding: Outdoor cable is not covered to protect from the weather effects. | All power cables exposed to weather shall have cover unless it is specified for outdoor wiring. | In progress | Mar 15 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 55 | New Finding: PVC/perforated type cable tray used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | In progress | Mar 15 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 56 | New Finding: Electrical equipment are not adequately identified. | All cables, circuits, and equipment must be properly identified in accordance with the as-built Single Line Diagram. | In progress | Mar 15 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 57 | New Finding: Power cables are bent excessively. | Power cables should be installed as straight as possible. In unavoidable cases, bends should not exceed a minimum of 135 degrees to prevent damage and ensure proper electrical conductivity. | In progress | Mar 15 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 58 | New Finding: Safety program is initiated but has no influence (improper safety gloves) in the factory all electrical personnel. | An electrical safety training and awareness program must be established and documented for all electrical personnel. The objective of this program is to cultivate a positive shift in safety attitudes and behaviors among the team. | In progress | Mar 15 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 59 | New Finding: Lightning Protection System (LPS) is not installed properly including air terminals installed below the highest structures, absence of metal bonding where required. | Factory required to be redesign the Lightning Protection System (LPS) as per standard for the entire facility. Once the LPS is properly designed, it must be installed according to the design specifications to ensure effective protection against lightning strikes. | In progress | Mar 15 2026 |  | 1 Month | In Progress

## Boiler
Date
15-Apr-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Matrix Styles Ltd., Degerchala, National University Gazipur, Bangladesh-1704, Gazipur
Date of Inspection |  | 2022-03-07
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 8115 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | Done. Emergency Stop push switch has been installed for both boiler control panel and outside the boiler roo. | Jan 10 2026 | Comments on 08-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 8115 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Done. The Low Low Water Level (LLWL) gauge glass installation and water marking level properly completed. | Jan 10 2026 | Comments on 08-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 8115 | Necessary technical documents (manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, operation and maintenance manual, water treatment design & calculation and water treatment report) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Done. Required all drawing related to boiler has been completed properly. | Jan 10 2026 | Comments on 08-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 8115 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | Done. Boiler Safety Valve outlet line extended direct outside of the boiler room. | Dec 10 2025 | Comments on 08-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 8115 | Boiler registration number plate was not found mounted on the boiler. | Boiler registration number plate shall be made available on the boiler according to the Bangladesh Boiler Act 2022. | Done. Now Boiler Registration number is available on boiler body. | Jan 10 2026 | Comments on 08-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 8115 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | Done. New boiler gauge meter has been installed as per requirement. | Dec 10 2025 | Comments on 08-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 8115 | The safety valve was found to be mounted using a tee/elbow joint. | Safety valves must be mounted directly onto the boiler shell without any branch connections in between. | Done. The Safety valve now properly mounted directly on boiler. | Dec 10 2025 | Comments on 08-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 8 | BB 8115 | Carbon deposition was found in the furnace chamber. | The furnace and inside of the fire tubes should be cleaned periodically to prevent excessive soot build-up. The fuel burner should be adjusted according to the manufacturer's guidelines. | Done. Cleaned the boiler's fire tube and adjusted according to the manufacturer guideline. | Jan 10 2026 | Comments on 08-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | Functional test inspection | 9 | BB 8115 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | Done. The Steam pressure Limiter has been installed and functional. | Dec 10 2025 | Comments on 08-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 10 | BB 8115 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | Done. The Air Pressure Limiter has been installed and properly functional. | Dec 10 2025 | Comments on 08-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 11 | BB 8115 | There was no acoustic or optical alarm when the limiter was activated. | An acoustic with optical alarm should be installed. | Done. The Optical Alarm has been installed for Low Low Water Level and High pressure detection. | Dec 10 2025 | Comments on 08-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification