## Structural
Date
18-Dec-2025 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Mega Couture Ltd. (Previously Mega Denim Ltd. (Extension)), 88/1, B.K Bari, Taltoli, Mirjapur, Gazipur sadar, Gazipur, Gazipur
Date of Inspection |  | 2023-09-10
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Foundation stress exceeds normal design limits. (Building 2), | The building engineer to review design, loads, and foundation stresses. | Facility has Re-submitted the Design documents DEA to RSC on 31-May- 2025 & waiting for review comments | Nov 15 2023 | On 16-Jan-2024: This issue has been covered in Engineering Assessment (EA). Factory has produced EA report as well as load plan and submitted to RSC on 14 January 2024 which is under review. On 08-Dec-2025: The design documents of Building-2 have been reviewed and accepted by RSC on 01 Sep 2025. During the verification, as-built drawings were found consistant with as-built conditions. | within 6-weeks | Corrected
Initial Inspection |  | 2 | Foundation stress exceeds normal design limits. (Building 2) | Produce and actively manage a loading plan for all floor plates within the factory, considering floor, column and foundation capacity. | Facility has Re-submitted the Design documents DEA to RSC on 31-May- 2025 & waiting for review comments | Nov 15 2023 | On 16-Jan-2024: Load plans are produced as a part of EA. The factory has submitted the EA on 14 January 2024 which is under review. During the inspection, load plan (5 kpa at staircase, 4 kpa at finish goods area & 3 kpa at packing section, ready goods, sweing, office area, toilet) was found posted on each floor but the load plan do not comply with BNBC requirements (5 kpa at any type of light storage, staircase & 3kpa at office area, sweing, office area, toilet). The building engineer is required to revise the load plan according to BNBC. On 08-Dec-2025: Load plans have been produced as a part of design report which was accepted by RSC 01 Sep 2025. During inspection, accepted load plan was found posted and floor loading was within the posted load plan. (125 psf on 1st & 2nd floor, 63 psf on 3rd to 5th floor) | within 6-weeks | Corrected
Initial Inspection |  | 3 | Foundation stress exceeds normal design limits. (Building 2) | Complete implementation of any remedial works. | Facility has Re-submitted the Design documents DEA to RSC on 31-May- 2025 & waiting for review comments | Apr 1 2024 | On 16-Jan-2024: Factory has produced EA report as well as load plan and submitted to RSC on 14 January 2024 which is under review. Remedial works required to be carried out after getting acceptance from RSC. (If any) On 08-Dec-2025: According to the accepted design report, no remediation is required. | within 6-months | Corrected
Initial Inspection |  | 4 | Foundation stress exceeds normal design limits. (Building 2) | Continue to implement loading plan. | Facility has Re-submitted the Design documents DEA to RSC on 31-May- 2025 & waiting for review comments | Apr 1 2024 | On 16-Jan-2024: Load plans are produced as a part of EA. The factory has submitted the EA on 14 January 2024 which is under review. During the inspection, load plan was found posted on each floor but the load plan do not comply with BNBC requirements. Factory is required to align the stroage and maintain final loading plan after getting acceptance from RSC On 08-Dec-2025: During inspection, accepted load plan was found posted and floor loading was within the posted load plan. (125 psf on 1st & 2nd floor, 63 psf on 3rd to 5th floor) | within 6-months | Corrected
Initial Inspection |  | 5 | Load plan & material test not comply with BNBC requirements. (Building 2) | The building engineer is required to revise the storage live load limit and related design documents based on BNBC requirement. | Facility has Re-submitted the Design documents DEA to RSC on 31-May- 2025 & waiting for review comments | Nov 15 2023 | On 16-Jan-2024: Load plans are produced as a part of EA. The factory has submitted the load plan along with EA on 14 January 2024. Which is under review. During the inspection, load plan was found posted on each floor but the load plan do not comply with BNBC requirements. The building engineer is required to revise the load plan according to BNBC. On 08-Dec-2025: Load plans have been produced as a part of design report which was accepted by RSC 01 Sep 2025. During inspection, accepted load plan was found posted and floor loading was within the posted load plan. (125 psf on 1st & 2nd floor, 63 psf on 3rd to 5th floor) | within 6-weeks | Corrected
Initial Inspection |  | 6 | Load plan & material test not comply with BNBC requirements. (Building 2) | Verify the insitu material strength by taking 100 mm core from lower tier columns. | Facility has submitted the drawing to RSC on 18 -Mar- 2024 & waiting for review comments. | Nov 15 2023 | On 16-Jan-2024: Factory has taken cores from the column, beam and slab to verify in-situ concrete strength as a part of Engineering Assesment (EA) which is under review. However, during the inspection core cutting layout was available on site and all core location has been verified. On 08-Dec-2025: Previously corrected. | within 6-weeks | Corrected
Initial Inspection |  | 7 | Load plan & material test not comply with BNBC requirements. (Building 2) | Implement the recommendations of design report. | Facility has Re-submitted the Design documents DEA to RSC on 31-May- 2025 & waiting for review comments | Apr 1 2024 | On 16-Jan-2024: The factory is required to carry out necessary remedial works (if required) after acceptance of EA. On 08-Dec-2025: According to the accepted design report, no remediation is required. | within 6-months | Corrected
Initial Inspection |  | 8 | Load plan & material test not comply with BNBC requirements. (Building 2) | Implement floor load plan. | Facility has Re-submitted the Design documents DEA to RSC on 31-May- 2025 & waiting for review comments | Apr 1 2024 | On 16-Jan-2024: Load plans are produced as a part of EA. The factory has submitted the EA on 14 January 2024. Which is under review. During the inspection, load plan did not comply with BNBC requirement. Factory is required to maintain final loading plan after getting acceptance from RSC. On 08-Dec-2025: During inspection, accepted load plan was found posted and floor loading was within the posted load plan. (125 psf on 1st & 2nd floor, 63 psf on 3rd to 5th floor) | within 6-months | Corrected
Initial Inspection |  | 9 | Racks and plastic water tanks not anchored or braced. (Building 2 & 3) | Building is required to adequately anchor/brace all nonstructural elements to resist earthquake forces to comply with the BNBC. | Facility has submitted the drawing to RSC on 18 -Mar- 2024 & waiting for review comments. | Apr 1 2024 | On 16-Jan-2024: During the inspection, it was observed that the racks for both Building 2 and 3 were anchored. Additionally, water tank was not observed in Building 2. On 08-Dec-2025: Previously corrected. | within 6-months | Corrected
Initial Inspection |  | 10 | Inadequate protection in the handrail of the roof parapet. (Building 2) | Building engineer is required to provide more steel members at the handrail to avoid possible falling hazard. | Facility has submitted the drawing to RSC on 18 -Mar- 2024 & waiting for review comments. | Nov 15 2023 | On 16-Jan-2024: During the inspection, it was observed that the handrail of the roof parapet has a sufficient number of steel members, preventing possible falling hazards around the roof. On 08-Dec-2025: Previously corrected. | within 6-weeks | Corrected
Initial Inspection |  | 11 | Column susceptible to vehicle impact. (Building 2) | The factory is required to provide separate barrier around the column to avoid possible vehicle impact. | Facility has submitted the drawing to RSC on 18 -Mar- 2024 & waiting for review comments. | Apr 1 2024 | On 16-Jan-2024: The factory has implemented protective measures by placing a separate barrier, fencing steel members around the column to avoid possible vehicle impact. On 08-Dec-2025: Previously corrected. | within 6-months | Corrected
Initial Inspection |  | 12 | Load plan & material test not comply with BNBC requirements. (Building 3) | The building engineer is required to revise the storage live load limit and related design documents based on BNBC requirement. | Facility has Re-submitted the Design documents DEA to RSC on 31-May- 2025 & waiting for review comments | Nov 15 2023 | On 16-Jan-2024: Load plans are produced as a part of EA. The factory has submitted the load plan along with EA on 14 January 2024. Which is under review. On 08-Dec-2025: Load plans have been produced as a part of design report which was accepted by RSC 01 Sep 2025. During inspection, accepted load plan was found posted and floor loading was within the posted load plan. (125 psf) | within 6-weeks | Corrected
Initial Inspection |  | 13 | Load plan & material test not comply with BNBC requirements. (Building 3) | Verify the insitu material strength by taking 100 mm core from lower tier columns. | Facility has verifyed the insitu meterial strength by taking 100 mm core from lower tier columns & Submitted to RSC dated on 03-Dec-2023 | Nov 15 2023 | On 16-Jan-2024: Factory has taken cores from the column, beam and slab to verify in-situ concrete strength as a part of Engineering Assesment (EA) which is under review. However, during the inspection core cutting layout was available on site and all core location has been verified. On 08-Dec-2025: Previously corrected. | within 6-weeks | Corrected
Initial Inspection |  | 14 | Load plan & material test not comply with BNBC requirements. (Building 3) | Implement the recommendations of design report | Facility has Re-submitted the Design documents DEA to RSC on 31-May- 2025 & waiting for review comments | Apr 1 2024 | On 16-Jan-2024: The factory is required to carry out necessary remedial works (if required) after acceptance of EA. On 08-Dec-2025: According to the accepted design report, no remediation is required. | within 6-months | Corrected
Initial Inspection |  | 15 | Load plan & material test not comply with BNBC requirements. (Building 3) | Implement floor load plan. | Facility has Re-submitted the Design documents DEA to RSC on 31-May- 2025 & waiting for review comments | Apr 1 2024 | On 16-Jan-2024: Load plans are produced as a part of EA. The factory has submitted the EA on 14 January 2024. Which is under review. During the inspection, load plan did not comply with BNBC requirement. Factory is required to maintain final loading plan after getting acceptance from RSC. On 08-Dec-2025: During inspection, accepted load plan was found posted and floor loading was within the posted load plan. (125 psf) | within 6-months | Corrected
Initial Inspection |  | 16 | Lack or parapet wall on the existing roof. (Building 3) | Building engineer is required to provide parapet wall at the existing roof opening to avoid possible falling hazard. | Facility has provided parapet wall at the existing roof opening to avoid possible falling hazard. | Nov 15 2023 | On 16-Jan-2024: During the inspection, it was observed that the factory installed a handrail on the roof parapet with an sufficient number of steel members instead of a parapet wall to avoid possible falling hazards around the roof. On 08-Dec-2025: Previously corrected. | within 6-weeks | Corrected

## Fire
Date
18-Dec-2025 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Mega Couture Ltd. (Previously Mega Denim Ltd. (Extension)), 88/1, B.K Bari, Taltoli, Mirjapur, Gazipur sadar, Gazipur, Gazipur
Date of Inspection |  | 2023-09-10
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Fire Rated construction: BUILDING-2Rooms used for storage of combustible materials are not separated from the surrounding occupancy/areas. Location: Building-2 (Ground Floor & 2nd Floor) | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour construction. | Facility has done maintence of door coordinator, Interfacing with fire alarm system is now functional , Waiting for RSC Verification. | Jan 1 2024 | On 19-Feb-25: The factory has installed fire rated doors to separate the storage rooms on 3rd, 2nd & ground floors, but the installed doors were not closing properly due to poor maintenance of door coordinator on ground floor. RPO Comments: On 30-Apr-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Initial Inspection |  | 2 | Fire Rated construction: Areas used for in-process storage of combustible materials are open to the surrounding occupancy. Location:Building-2 (1st Floor) | Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4 m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. or 3. Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Facility has removed in-process storage areas from packing section. | Jan 1 2024 | On 19-Feb-25: Non-compliant in-process storage areas were found at packing section on 1st floor of building-2. RPO Comments: On 30-Apr-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Initial Inspection |  | 3 | Fire Rated construction: Corridor(s) serving more than 30 occupants is not separated by fire rated construction. Location: Building-2 (Several floor). | 1. Separate the corridor by a minimum 1-hr fire rated construction. Or 2. Provide automatic sprinkler system throughout the story as per NFPA 13 | Facility has separated the corridor by a minimum 1 hr. fire rated construction. | Jan 1 2024 | On 19-Feb-25: Corrected. The corridor has been removed. | Within 3 months | Corrected
Initial Inspection |  | 4 | Means of Egress: The fire doors were found tied by unauthorized means (door wedges, door stopper) and also interfacing with the fire alarm system & door closers were not properly functional during the inspection. Location: Building-2 | Ensure that the fire doors are self-closing and positive latching. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | Facility has fixed handle of the fire door & ensured that the fire doors are self closing & positive latching with proper certification. | Oct 7 2023 | On 19-Feb-25: The handle of the fire door on the 5th floor was found missing, and the door was not closing properly due to poor maintenance of the door coordinator on the 1st floor of Stair-4. Also, the factory needs to collect the datasheets and certificates of the installed doors and keep on site for verify during inspection. RPO Comments: On 30-Apr-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Immediately | Pending Verification
Initial Inspection |  | 5 | Fire Rated construction: Storage/ storage rooms from ground floor discharges directly into the exit enclosures. Location: Building-2 (Ground Floor) | Openings from exit enclosure to storage room, generator, basements, transformer boiler and similar normally unoccupied spaces shall be provided with a vestibule with fire rated construction and openings as per RSC Technical Guidelines (Standard) 6.14.3 . Provide a 1.5 hr. fire rated door on the exit stair side and a 1-hr. fire rated door on the storeroom/storage side. Ensure that the fire rating of the vestibule construction matches that of the exit stair enclosure. | Facility has removed temporary storage from 1st floor & 3rd floor ( Designated for Packing & sewing floor). Facility started the fixing Vestibules with fire-related construction . | Jan 1 2024 | On 19-Feb-25: Vestibules with fire-related construction were not provided. Location: on 1st, 2nd & 3rd floor of building-2. RPO Comments: On 22-Jul-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Initial Inspection |  | 6 | Fire Rated construction: Penetrations through floor/ceiling assemblies are found unsealed. Location: Building-2 (4th Floor) | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by third-party certified fire rated materials to maintain the fire resistance rating. Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. | Facility has sealed all toilet block & electrical cable riser on 1st to 5th floor on building-2. | Jan 1 2024 | On 19-Feb-25: Unsealed floor penetrations were found due to toilet block (plastic plumbing pipe) on ground to 4th floor and electrical cable riser on 1st to 5th floor on building-2. RPO Comments: On 30-Apr-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Initial Inspection |  | 7 | Means of Egress: Doors along means of egress are provided with non compliant locking system. Location: Building-2; Access control devices has been used on the glass door at the end of exit access corridors. | 1. Remove all non compliant locking features from egress doors. 2. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. 3. Doors may be locked where the latch and lock are disengaged with one motion where the occupant load does not exceed 49 persons. 4. Doors may be provided with locking hardware from the ingress side provided that a panic bar is installed on any door with an occupant load exceeding 49 persons. | Facility has removed all non compliant locking features from egress doors. | Oct 7 2023 | On 19-Feb-25: Corrected. Non-compliant locking features were not found with the exit egress doors during inspection. | Immediately | Corrected
Initial Inspection |  | 8 | Fire Rated construction: Egress door serving 50 or more occupants but does not swing in the direction of egress travel. Locations: Glass door at the end of exit access corridors. | Modify swing direction of egress doors to the direction of egress travel. Doors serving an occupant load of more than 50 shall swing in the direction (out-ward) of egress travel . | Facility has removed exit swing glass door at the end of exit access corridors. | Jan 1 2024 | On 19-Feb-25: Corrected. The corridor including glass door has been removed. | Within 3 months | Corrected
Initial Inspection |  | 9 | Means of Egress: Each exit stairs serve more than 5 stories and do not have required re-entry provisions. Location: Building-2 | Every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets ACCORD standard 6.8.3.1. | Facility has provided Re-Entry mark on any of the floor. | Jan 1 2024 | On 19-Feb-25: Re-entry was neither provided nor marked on any of the floors. RPO Comments: On 30-Apr-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Initial Inspection |  | 10 | Means of Egress: The egress path along means of egress has interrupted by obstruction/storage. Location: Building-2 (5th Floor) | Means of egress shall be maintained continuously free and clear of all obstructions/storage. Or Keep egress paths and stairs clear of storage. | Facility has maintained continuously free and clear of all obstructions/storage. | Oct 7 2023 | On 19-Feb-25: Corrected. All the aisles and egress paths were found free of obstructions. | Immediately | Corrected
Initial Inspection |  | 11 | Fire Rated construction: BUILDING-3 The exit stairs are not separated from store areas on each floor by fire-rated construction. | Provide minimum 2-hr fire rated construction for buildings 4 storied or more and 1-hr for up to 3 storied. Seal all unprotected openings to separate the exit stairs from work areas and other spaces on all floor levels by 90 minutes for 2 hr. construction and 60 minutes for 1-hr construction. Ensure that the fire rated doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors and provide vestibules to avoid direct discharge from storage to exit stair enclosure. If fire rated doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. Once fire doors are installed, every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets The RSC Technical Guidelines (Standard) 6.8.3.1 | Facility has removed unapproved means from all doors. | Jan 1 2024 | On 19-Feb-25: The factory has installed fire rated doors on 1st and 2nd floors of both stairs, but doors were open by unapproved means (all doors). RPO Comments: On 30-Apr-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 Months | Pending Verification
Initial Inspection |  | 12 | Means of Egress: The egress court for westside were less than 10 ft. wide but not separated from the building interior. Location: Building-3 (West side) | Provide a 1.5 hr. fire rated door on the store side and Seal all penetrations and openings to the interior of the building along the discharge path up to a height of 10 ft. to provide a minimum 2-hr fire separation. | Facility has Re allocated egress court from west side to Eastside of building -03. | Jan 1 2024 | On 19-Feb-25: Progress observed. The factory has sealed most of the openings within a 10 ft. height, except for one exhaust fan, cable penetration, and pipe penetration on the ground floor, as well as some exhaust outlets on the 1st floor to the egress court from the Mega Washing and Dyeing building. RPO Comments: On 30-Apr-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 Months | Pending Verification
Initial Inspection |  | 13 | Means of Egress: Parapets or guards are not provide in occupiable roof. Location: Building-3 | All occupiable roofs shall be provided with parapets or guards with a minimum height of 1067 mm (42 in.) | Facility has provided parapets or guards diameter 8 In a minimum height. | Jan 1 2024 | On 19-Feb-25: Progress has been observed. The factory has provided parapets/guards, but the intermediate rails or patterns at the rooftop of both Buildings 2 and 3 have a sphere diameter of more than 200 mm (8 in.). Additionally, the parapets/guards of the exit stairs (with rails or patterns having a sphere diameter of more than 200 mm) for both Buildings 2 and 3 need to be rechecked. RPO Comments: On 30-Apr-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 Months | Pending Verification
Initial Inspection |  | 14 | Means of Egress: A single means of exit has been provided. Location: Building-3 | Ground or basement story is allowed a maximum of 50 occupants and 23 m (75ft) travel distance. The second story is allowed a maximum of 30 occupants and 23 m (75ft) travel distance. All other stories require a minimum of 2 egress exits Provide additional means of egress in every floor. | Facility has provided 2nd exit in Building-3 | Jan 1 2024 | On 19-Feb-25: Corrected. The factory has provided an additional exit stair (presently 2 nos. exit stair) for building-3. | Within 3 Months | Corrected
Initial Inspection |  | 15 | Means of Egress: Handrails are not provided throughout the exit stair. Additionally at many location intermediate rails are not provided. Location:Building-3 | Provide handrails on both sides of the exit stair. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in.). New handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. Handrails shall have intermediate rails or pattern such that a sphere 200 mm (8 in.) in diameter cannot pass through any opening up to a height of 865 mm (34 in.). | Facility has provided intermediate rails or patterns of the parapets/guards in both Buildings 2 and 3 within 8 In. | Nov 1 2023 | On 19-Feb-25: Progress has been observed. The factory has provided handrails for all stairs in both Buildings 2 and 3. However, the intermediate rails or patterns of the parapets/guards in both Buildings 2 and 3 have a sphere diameter of more than 200 mm (8 in.). RPO Comments: On 30-Apr-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Initial Inspection |  | 16 | Means of Egress: Sliding type doors have provided along means of egress [Storage, building exits, exit discharge].Location: Building-3 (Ground floor, Wastage Godown) | Replace all collapsible/sliding/shutter type doors & gates by the side‐hinged swinging type doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Facility has replaced all collapsible/sliding/shutter type doors & gates by the side‐hinged swinging type doors. | Nov 1 2023 | On 19-Feb-25: Corrected. The factory has removed the sliding door. | Within 1 Month | Corrected
Initial Inspection |  | 17 | Means of Egress: Doors along means of egress are provided with non compliant locking system. Location: Exit doors of Building-3 | 1. Remove all non compliant locking features from egress doors. 2. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. 3. Doors may be locked where the latch and lock are disengaged with one motion where the occupant load does not exceed 49 persons. 4. Doors may be provided with locking hardware from the ingress side provided that a panic bar is installed on any door with an occupant load exceeding 49 persons. | Facility has removed all non compliant locking features from egress doors. | Oct 7 2023 | On 19-Feb-25: Corrected. Non-compliant locking features were not found with the exit egress doors during inspection | Immediately | Corrected
Initial Inspection |  | 18 | Means of Egress: Fire evacuation maps is not posted at the entrance of all exit stair. Location: Building-3 | Fire evacuation maps shall be posted at the entrance to each exit stair. | Facility has posted the evacuation with separation wall, exit doors, and stairs shown correctly | Nov 1 2023 | On 19-Feb-25: The factory has installed evacuation plans for both buildings-2 & 3, but evacuation plans are not matched with the actual floor plans of both buildings (such as separation wall, exit doors, and stairs were not shown correctly). RPO Comments: On 30-Apr-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Initial Inspection |  | 19 | Means of Egress: Building did not have stair designation signs and occupant load signs at required locations. Location: Building-3 | Provide stair designation signs and occupant load signs at required locations. | Facility has provided stair designation sign & occupant load sign at required locations. | Nov 1 2023 | On 19-Feb-25: Stair designation signs and occupant load signs were provided for stair-1, not for stair-2 of building-3. RPO Comments: On 30-Apr-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 Month | Pending Verification
Initial Inspection |  | 20 | Egress Lighting: Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. Location: Building-3 | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Facility has provided /Replanced emergency light in every required area. | Nov 1 2023 | On 19-Feb-25: The factory has installed emergency lights, but it was observed to be inadequate for a fire pump room on basement, 1st and 2nd floor of building-3 and on all floors of building-2. Many broken & non-functional emergency lights were found on the 4th floor building-2. RPO Comments: On 30-Apr-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 Month | Pending Verification
Initial Inspection |  | 21 | Egress Lighting: Exit sign not provided at exit. Location: Building-2&3 | Lighted exit signs shall be placed at entrance to an exit. Additional exit signs shall be placed throughout the facility anywhere the continuation of the egress is not obvious. Lighted exit signs shall be provided with either battery backup or uninterruptable power supply systems and shall be continuously illuminated. | Facility has placed exit sign at the exit door of all office rooms & floors in Building-2 & 3 | Nov 1 2023 | On 19-Feb-25: Building-2: Exit signs were found missing at the exit door of all office rooms. Building-3: Exit signs were found missing for all exits of all rooms/floors on all floors. RPO Comments: On 30-Apr-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 Month | Pending Verification
Initial Inspection |  | 22 | Means of Egress: Fire evacuation maps is not posted at the entrance of all exit stair. Location: Building-2&3 | Fire evacuation maps shall be posted at the entrance to each exit stair. | Facility has posted the evacuation plan with separation wall, exit doors, and stairs has shown correctly. | Nov 1 2023 | On 19-Feb-25: The factory has installed evacuation plans for both buildings-2 & 3, but evacuation plans are not matched with the actual floor plans of both buildings (such as separation wall, exit doors, and stairs were not shown correctly). RPO Comments: On 22-Jul-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Initial Inspection |  | 23 | Fire Alarm & Detection System (FADS): The fire detection system installation requires detail review to confirm compliance with NFPA-72 and other applicable standard. Location: For all buildings | Submit as-built drawings, testing records, equipment certification and other relevant documentation to the RSC for review and then approval/acceptance test. | Installed all missing devices & after commissoing FACP now in normal moode. Facility has Re-Applied for Pre T & CVI on 04 Jun 2025. Waiting for RSC review comments. | Jun 1 2024 | On 19-Feb-25: The installation of the fire alarm and detection system has not been completed, and the commissioning of the panel has not been done. Many detector heads were found missing (reportedly 58 detectors) on most floors throughout Buildings 2, 3, and the 6-story Mega Denim Ltd. building. Additionally, the FACP was found to be abnormal, with supervisory and fault signals. After completing the installation or modification work and commissioning, the factory needs to re-apply for Pre-T&CVI. RPO Comments: On 15-Dec-2025, the Pre-T&CVI documents are reviewed & accepted on 15 Dec 2025. The factory is now ready for Pre-T&CVI inspection. The systems will be checked in the next inspection. | Drawing review within 2 months and Install/modification within 6 months. | Pending Verification
Initial Inspection |  | 24 | Fire Suppression System (SUPS): Standpipe system and fire pump installation requires to detailed review to confirm compliance with NFPA 14, 20, 22, 24 and RSC standard. Location: For all buildings | Submit the standpipe system drawing to RSC for review. Once reviewed, install or modify the standpipe system throughout the building in accordance with RSC standard, NFPA 14 and 20. The factory management shall contact RSC to conduct the final acceptance testing after the installation, testing & commissioning | Facility has Replaced the new I/O Board & all pump are now functional. Resubmited the SUPS Pre T & C design documents to RSC on 21 July 2025. waiting for RSC Review . | Jun 1 2024 | On 19-Feb-25: The motherboard of the diesel engine-driven fire pump was found burnt out and non-functional. Reportedly, the factory has completed the installation of the standpipe system. After completing the installation, modification work, and commissioning, the factory needs to re-apply for Pre-T&CVI. RPO Comments: On 04-Sep-2025, the Pre-T&CVI documents are reviewed & accepted on 11 Aug 2025. The factory is now ready for Pre-T&CVI inspection. The systems will be checked in the next inspection. | Review within 2 months and Install within 6 months | Pending Verification
Initial Inspection |  | 25 | Fire Alarm & Detection System (FADS): Inspection, testing and maintenance for the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with NFPA 72 and RSC standards. | Facility has maintained Inspect, test the fire alarm system and keep written records on-site, in accordance with NFPA 72 and RSC standards. | Jul 1 2024 | On 19-Feb-25: It is an integrated part of the fire alarm and detection system. RPO Comments: On 15-Dec-2025, the Pre-T&CVI documents are reviewed & accepted on 15 Dec 2025. The factory is now ready for Pre-T&CVI inspection. The systems will be checked in the next inspection. | Within 1 Month After Installation | Pending Verification
Initial Inspection |  | 26 | Fire Suppression System (SUPS): Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records on- site, in accordance with NFPA 10 and RSC standards. | Facility has maintained Inspect, test the portable fire extinguishers and keep written records on- site, in accordance with NFPA 10 and RSC standards. | Nov 1 2023 | On 19-Feb-25: Corrected. The factory was maintaining inspection, testing and maintenance records as per NFPA-10. | Within 1 Month | Corrected
Initial Inspection |  | 27 | Fire Suppression System (SUPS): Inspection, testing and maintenance of the fire pump system is not in accordance with NFPA 20. | Inspect, test and maintain the fire pump system and keep written records on-site, in accordance with NFPA 20 and RSC standards. | Facility has maintained Inspect, test the fire pump system and keep written records on-site, in accordance with NFPA 20 and RSC standards. | Jul 1 2024 | On 19-Feb-25: It is an integrated part of the fire pump system. RPO Comments: On 04-Sep-2025, the Pre-T&CVI documents are reviewed & accepted on 11 Aug 2025. The factory is now ready for Pre-T&CVI inspection. The systems will be checked in the next inspection. | Within 1 Month After Installation | Pending Verification
Initial Inspection |  | 28 | Fire Suppression System (SUPS): Inspection, testing and maintenance of the standpipe system is not in accordance with NFPA 14. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 14 and RSC standards. | Facility has maintained the standpipe system and keep written records on-site, in accordance with NFPA 14 and RSC standards. | Jul 1 2024 | On 19-Feb-25: It is an integrated part of the fire standpipe system. RPO Comments: On 04-Sep-2025, the Pre-T&CVI documents are reviewed & accepted on 11 Aug 2025. The factory is now ready for Pre-T&CVI inspection. The systems will be checked in the next inspection. | Within 1 Month After Installation | Pending Verification
Initial Inspection |  | 29 | Egress Lighting: Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with the RSC standard. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with the RSC standard. Keep written records on-site. | Facility has Replaced all broken and non-functional emergency lights on all floors of building-2. | Nov 1 2023 | On 19-Feb-25: Not corrected. The factory was maintaining inspection, testing and maintenance records, but it was not reflected on the site conditions. Many broken and non-functional emergency lights were found on all floors of building-2. RPO Comments: On 30-Apr-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 Month | Pending Verification
Follow Up Inspection |  | 30 | New Finding (1st FU): The fire pump room is not separated from the wastage store and workshop on ground floor due to unsealed penetrations of building-3. | Ensure that the fire pump room is separated with 2 hr. rated fire separation when not sprinklered and 1 hr. rated fire separation when provided with automatic sprinklers in accordance with NFPA 20 from surrounding occupancy. | Facility has sealed all penetration from the wastage store and workshop on ground floor of the pump room Building-3. | Mar 20 2025 | On 19-Feb-2025: New finding RPO Comments: On 22-Jul-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 Month | Pending Verification
Follow Up Inspection |  | 31 | New Finding (1st FU): The directional signs are not provided where there is a change in direction and where the continuation of the egress path is not obvious. Location: On most of the floors of the buildings-2 & 3. | Install illuminated directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious. | Facility has installed illuminated directional signs where there is a change in the direction for the path of travel and the direction to an exit is obvious. | Mar 20 2025 | On 19-Feb-2025: New finding RPO Comments: On 30-Apr-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 Month | Pending Verification

## Electrical
Date
18-Dec-2025 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Mega Couture Ltd. (Previously Mega Denim Ltd. (Extension)), 88/1, B.K Bari, Taltoli, Mirjapur, Gazipur sadar, Gazipur, Gazipur
Date of Inspection |  | 2023-09-10
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. | Facility has ensured the load, CB Rating identified properly & the individual protection as per as built SLD. | Dec 1 2023 | On 30/04/2024: Not corrected. Factory has got their accepted SLD from RSC on 23-Jan-2024. The six storied building not occupied by the factory. Because there was no power connection/electrical installation. They applied for REB connection but got no response yet. Other 3 storied Hydrant Building is used for fire pump, temporary office & store. fire pump power comes from other ID in this premises. SLD implementation remains in progress. RPO Comments On 10-Jul-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 19/05/2025: Not corrected. Progress has been observed in field (approx. 60%). Still some mismatch has been observed including load are not properly identified, CB rating mismatch, individual protection mismatch/missing etc. RPO Comments: On 22-Jul-2025 , The corrective action plan should be completed as per the given recommendation with immediate concern. On 05/10/2025: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not drawn and installed properly (improper calculation, bi-metallic joint missing etc.) | Factory shall redesign Lightning Protection System (LPS) as per standard and install accordingly. | Factory has redesigned lightning protection system as per standard & installed accordingly. | Dec 1 2023 | On 30/04/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 3 | There is no programmed schedule for periodical inspection & testing of electrical equipment. | An electrical maintenance program shall be prepared which will include inspections and testing of the electrical systems (preventive and proactive). | Factory has prepared an electrical preventive maintenance program with included inspection & testing of the electrical system. | Nov 1 2023 | On 30/04/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 4 | Thermography scanning report is not available. | Thermography survey must be done and recorded at least twice in a year. | Facility has performed Thermography survey & recorded accordingly. | Nov 1 2023 | On 30/04/2024: Not corrected. No progress observed. They will prepare thermography test report after completing the electrical installation. RPO Comments On 10-Jul-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 19/05/2025: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 5 | Manually operated machines (may have chance to be touched by operator/user) have no earth connection. | Manually operated each machine (may have chance to be touched by user/operator) must have earth connection. Cable selection shall be made per CB response and circuit's power demand. | Factory has given earthing connection in manually operated machines. | Nov 1 2023 | On 30/04/2024: Corrected. They rectified the issue which was found during initial. No other panels didn't install. This issue will be rechecked when all the electrical installation will be completed. | 1 MONTH | Corrected
Initial Inspection |  | 6 | Distribution Board's top/bottom is left open (typical issue). | Gland shall be used, where required. | Factory has used gland where required. | Dec 1 2023 | On 30/04/2024: Corrected. They rectified the issue which was found during initial. No other panels didn't install. This issue will be rechecked when all the electrical installation will be completed. | 2 MONTHS | Corrected
Initial Inspection |  | 7 | Cable channel/duct terminals are left open for ingression of lint, dust or fluffs. | Cable ducts must be properly sealed to avoid ingression of any foreign particles. | Factory has properly sealed the cable ducts to avoid ingression of any foreign particles. | Nov 1 2023 | On 30/04/2024: Corrected. They rectified the issue which was found during initial. No other panels didn't install. This issue will be rechecked when all the electrical installation will be completed. | 1 MONTH | Corrected
Initial Inspection |  | 8 | Cables are hanging without proper support and protection. | Cable tray/ladder must be used to support cables at anywhere to keep cable out of tension. | Factory has used cable tray to support cables at anywhere to keep cable out of tension. | Dec 1 2023 | On 30/04/2024: Corrected. They rectified the issue which was found during initial. No other panels didn't install. This issue will be rechecked when all the electrical installation will be completed. | 2 MONTHS | Corrected
Initial Inspection |  | 9 | Combustible materials attached with cable duct/channels. | Cable channels/ducts must be kept neat and clean; these must be free from combustible material and water pot. | Factory has removed combustible materials attached with cable duct/channel. | Nov 1 2023 | On 30/04/2024: Corrected. They rectified the issue which was found during initial. No other panels didn't install. This issue will be rechecked when all the electrical installation will be completed. | 1 MONTH | Corrected
Follow Up Inspection |  | 10 | New Finding: Uncovered/Perforated type cable tray/PVC pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Facility has done the wiring installation in storage area by metal | Jun 6 2024 | RPO Comments On 10-Jul-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 19/05/2025: Corrected. | 1 MONTH | Corrected
Follow Up Inspection |  | 11 | New Finding: Earth pit resistance test record doesn't match with field. | Field information must be accurately reflected in the record. All earthing systems must be tested for resistance on a dry day at least once every two years. Records of each earthing test and its results must be available for inspection when required. | Earth pit resistance test record has matched with field. | Jun 19 2025 | RPO Comments: On 22-Jul-2025 , the factory management reported the remediation completion. This item will be verified in the next inspection. On 05/10/2025: Corrected. | 1 MONTH | Corrected