## Structural
Date
10-May-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Needle Drop Ltd, 50, Chamdpara, Basin Road, Joydevpur national university, Joydevpur, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-06-12
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | No analytical confirmation indicating general conformance with any code is available. | Engage a qualified structural engineer to develop the required documents to confirm the structural integrity of the buildings. Documents must comply with Alliance Standard Part 8 Section 8.19 and 8.20. | Completed | Mar 12 2015 | On 15-Feb-2018: Factory had submitted the design report to ALLIANCE. According to ALLIANCE 5th PCVV report, design report is required to be submitted again to ALLIANCE regarding vertical extension. On 12-Sept-2018: This issue is required to cover in DEA. DEA of factory building got acceptance from Alliance on 19th January,2016. As per PCCVV on 7th Feb 2018, factory is required to revise the DEA of factory building conforming BNBC-2006 due to vertical expansion. Factory submitted revised DEA to Alliance and review comments given from Alliance. Till date of inspection, factory didn't submit DEA to Alliance. Factory is required to submit revised DEA to Alliance within 20th Sept, 2018. On 10th September 2019: Revised documents were re-accepted from Alliance on 14th October 2018. During inspection, truss member size of 2 storied canteen building were found smaller than the drawing size. In drawing, the truss member top and bottom chords are shown to be 50mm but on site they were found 38mm. Factory is required to submit revised documents to ACCORD for review. On 04-Feb-2020: During inspection, on 10th September 2019 some discrepancies were found between accepted drawing and as-built condition of 2-storied Canteen building. Submit the revised drawing along with analysis report to Accord. On 02-Feb-2022: On 10th September 2019, some roof truss members of 2-storied canteen building were found smaller than the accepted drawing and factory was required to submit the revised documents for review. Later factory has demolished the upper floor and submit as-built drawing of single storied RCC canteen building which was accepted from RSC on 02-Sep-2021. Onsite condition was found satisfactory with accepted drawing. On 04-Oct-2023: Corrected previously. During inspection, no discrepancy was found the accepted drawing and onsite condition. On 29-Sep-2025: Previously corrected. | Aug 2 2014 | Corrected
Initial Inspection |  | 2 | There are 3 water tanks, out of which two have water storage capacity 2000L and the other has 1000L. There is no analytical information on the provision of these tanks in the design. | Engage a qualified structural engineer to confirm and document that provisions have been made to accommodate concentrated loads. If provisions have not been made, have a qualified structural engineer develop a remediation plan. | Done | Mar 12 2015 | On 15-Feb-2018: Factory had submitted the design report to ALLIANCE. According to ALLIANCE 5th PCVV report, design report is required to be submitted again to ALLIANCE regarding vertical extension. Plastic water tanks were not observed. RCC water tanks were observed in the stair case. On 12-Sept-2018: During inspection, no plastic tank was found at roof level and RCC water was found over stair case. Loading of water tank is required to cover in DEA. DEA of factory building got acceptance from Alliance on 19th January,2016. As per PCCVV on 7th Feb 2018, factory is required to revise the DEA of factory building conforming BNBC-2006 due to vertical expansion. Factory submitted revised DEA to Alliance and review comments given from Alliance. Till date of inspection, factory didn't submit DEA to Alliance. Factory is required to submit revised DEA to Alliance within 20th Sept, 2018. On 10th September 2019: Revised documents were re-accepted from Alliance on 14th October 2018. During inspection, no discrepancy was observed between accepted drawings of Factory Building and as built condition. On 04-Feb-2020: Corrected from previous inspection. On 02-Feb-2022: Corrected from previous inspection. During inspection no plastic water tank was found at roof but two RCC water tanks were found above staircase as per accepted drawing. On 04-Oct-2023: Corrected previously. On 29-Sep-2025: Previously corrected. | Aug 2 2014 | Corrected
Initial Inspection |  | 3 | There is no program that will ensure that the designated load in each floor will not be exceeded. | Develop a program to ensure that all live loads for which a floor or roof has been designed for will not be exceeded. The designated Load Manager shall oversee this program and ensure it is enforced. | Done | Jul 25 2016 | On 15-Feb-2018: Factory had submitted the design report to ALLIANCE. According to ALLIANCE 5th PCVV report, design report is required to be submitted again to ALLIANCE regarding vertical extension. Load plan had been produced as part of design report. Load plan was found posted during inspection. Load manager was observed. On 12-Sept-2018: Load plan was produced as part of DEA. DEA of factory building got acceptance from Alliance on 19th January,2016. As per PCCVV on 7th Feb 2018, factory is required to revise the DEA of factory building conforming BNBC-2006 due to vertical expansion. Factory submitted revised DEA to Alliance and review comments given from Alliance. Till date of inspection, factory didn't submit DEA to Alliance. Factory is required to submit revised DEA to Alliance within 20th Sept, 2018. During inspection, load plan was found posted in each floor and loading was found within allowable limit (as per previously accepted load plan). Final load plan is required to be posted as per accepted DEA documents. On 10th September 2019: Revised documents were re-accepted from Alliance on 14th October 2018. During inspection, no discrepancy was observed between accepted drawings of Factory Building and as built condition. On 04-Feb-2020: Corrected from previous inspection. Load management program has been developed and maintained accordingly by designated load manager. On 02-Feb-2022: Corrected from previous inspection. During inspection load plan was found posted at each floor and overall loading was found below accepted load limit (63 psf). Designated load manager was found to maintain load register. On 04-Oct-2023: Corrected previously. During inspection, appointed load manager was present and loading was found below the accepted load limit (63 psf) on typical floor area. On 29-Sep-2025: Previously corrected. | Jul 19 2014 | Corrected
Initial Inspection |  | 4 | A set of structural and architectural document is available on site for review but the drawing does not fully comply with the as built condition of the building. However, the design report is not available which is required as per BNBC 2006 clause 1.9.1.1. | Have a qualified structural engineer prepare credible as-built documents based on the requirements of Part 8 Section 8.19 of the Alliance Standard. | Completed | Jan 14 2016 | On 15-Feb-2018: Factory had submitted the design report to ALLIANCE. According to ALLIANCE 5th PCVV report, design report is required to re-submit again to ALLIANCE regarding vertical extension. As-built documents had been prepared as part of design report. On 12-Sept-2018: As built drawing was produced as part of DEA. DEA of factory building got acceptance from Alliance on 19th January,2016. As per PCCVV on 7th Feb 2018, factory is required to revise the DEA of factory building conforming BNBC-2006 due to vertical expansion. Factory submitted revised DEA to Alliance and review comments given from Alliance. Till date of inspection, factory didn't submit DEA to Alliance. Submit revised DEA to Alliance within 20th Sept, 2018. On 10th September 2019: Revised documents were re-accepted from Alliance on 14th October 2018. Truss member size of 2 storied canteen building were found smaller than the drawing size. In drawing, the truss member top and bottom chords are shown to be 50mm but on site they were found 38mm. Factory is required to submit revised documents to ACCORD for review. On 04-Feb-2020: During inspection, on 10th September 2019 some discrepancies were found between accepted drawing and as-built condition of 2-storied Canteen building. Submit the revised drawing along with analysis report to Accord. On 02-Feb-2022: On 10th September 2019, some roof truss members of 2-storied canteen building were found smaller than the accepted drawing and factory was required to submit the revised documents for review. Later factory has demolished the upper floor and submit as-built drawing of single storied RCC canteen building which was accepted from RSC on 02-Sep-2021. Onsite condition was found satisfactory with accepted drawing. On 04-Oct-2023: Corrected previously. On 29-Sep-2025: Previously corrected. | Aug 2 2014 | Corrected
Initial Inspection |  | 5 | There is dampness at the ceiling of 2nd floor and efflorescence at ancillary dining room. There is no maintenance program for all areas including areas with efflorescence, dampness, standing water on rooftops, and corrosion. | Under guidance from a qualified structural engineer, address all areas of needed maintenance by correcting the identified issues. | Done by the first review by the Alliance | Mar 12 2015 | On 15-Feb-2018: No sign of efflorescence and dampness was not observed. Factory is required to monitor efflorescence and dampness for any further occurrence. On 12-Sept-2018: This issue was corrected from previous inspection. During inspection, dampness was not found. On 10th September 2019: Corrected previously. Dampness was not observed. On 04-Feb-2020: Corrected from previous inspection. Dampness, standing water on rooftop and corrosion was not found during inspection. On 02-Feb-2022: Corrected from previous inspection. During inspection no dampness or standing water was found. On 04-Oct-2023: Corrected previously. During inspection, no dampness was found at the ceiling or brick walls. On 29-Sep-2025: Previously corrected. | Aug 2 2014 | Corrected
Initial Inspection |  | 6 | No analytical confirmation regarding the consideration of the requirement of seismic and wind loading in the design of the building is available. | Have a qualified structural engineer document compliance with the seismic and wind requirements stated in the 2006 BNBC. | Completed | Mar 12 2015 | On 15-Feb-2018: Factory had submitted the design report to ALLIANCE. According to ALLIANCE 5th PCVV report, design report is required to be submitted again to ALLIANCE regarding vertical extension. On 12-Sept-2018: This issue required to cover in DEA. DEA of factory building got acceptance from Alliance on 19th January,2016. As per PCCVV on 7th Feb 2018, factory is required to revise the DEA of factory building conforming BNBC-2006 due to vertical expansion. Factory submitted revised DEA to Alliance and review comments given from Alliance. Till date of inspection, factory didn't submit DEA to Alliance. Submit revised DEA to Alliance within 20th Sept, 2018. On 10th September 2019: Revised documents were re-accepted from Alliance on 14th October 2018. During inspection, truss member size of 2 storied canteen building were found smaller than the drawing size. In drawing, the truss member top and bottom chords are shown to be 50mm but on site they were found 38mm. Submit revised documents to ACCORD for review. On 04-Feb-2020: During inspection, on 10th September 2019 some discrepancies were found between accepted drawing and as-built condition of 2-storied Canteen building. Submit the revised drawing along with analysis to Accord. On 02-Feb-2022: During inspection on 10th September 2019, some roof truss members of 2-storied canteen building were found smaller than the accepted drawing and factory was required to submit the revised documents for review. Later factory has demolished the upper floor and submit as-built drawing of single storied RCC canteen building which was accepted from RSC on 02-Sep-2021. During inspection onsite condition was found satisfactory with accepted drawing. On 04-Oct-2023: Corrected previously. On 29-Sep-2025: Previously corrected. | Aug 2 2014 | Corrected
Initial Inspection |  | 7 | There is no clear information available on the design document to understand the consideration of storm surge and wind loading in the design of the building. | Engage a qualified structural engineer to confirm satisfactory structural performance of the buildings under wind loading and storm surge. | Completed | Mar 12 2015 | On 15-Feb-2018: Factory had submitted the design report to ALLIANCE. According to ALLIANCE 5th PCVV report, design report is required to be submitted again to ALLIANCE regarding vertical extension. On 12-Sept-2018: This issue required to cover in DEA. DEA of factory building got acceptance from Alliance on 19th January,2016. As per PCCVV on 7th Feb 2018, factory is required to revise the DEA of factory building conforming BNBC-2006 due to vertical expansion. Factory submitted revised DEA to Alliance and review comments given from Alliance. Till date of inspection, factory didn't submit DEA to Alliance. Submit revised DEA to Alliance within 20th Sept, 2018. On 10th September 2019: Revised documents were re-accepted from Alliance on 14th October 2018. Truss member size of 2 storied canteen building were found smaller than the drawing size. In drawing, the truss member top and bottom chords are shown to be 50mm but on site they were found 38mm. Submit revised documents to ACCORD for review. On 04-Feb-2020: During inspection, on 10th September 2019 some discrepancies were found between accepted drawing and as-built condition of 2-storied Canteen building. Submit the revised drawing along with analysis report to Accord. On 02-Feb-2022: During inspection on 10th September 2019, some roof truss members of 2-storied canteen building were found smaller than the accepted drawing and factory was required to submit the revised documents for review. Later factory has demolished the upper floor and submit as-built drawing of single storied RCC canteen building which was accepted from RSC on 02-Sep-2021. During inspection onsite condition was found satisfactory with accepted drawing. On 04-Oct-2023: Corrected previously. On 29-Sep-2025: Previously corrected. | Aug 2 2014 | Corrected
Initial Inspection |  | 8 | There are signs of corrosion in the steel members of the ancillary structure. | Complete further testing on areas of deterioration and have a qualified structural engineer develop a remediation plan. | Done by the 3rd review by the Alliance | Jul 18 2016 | On 15-Feb-2018: No sign of corrosion was observed during inspection. On 12-Sept-2018: This issue was corrected from previous inspection. During inspection, corrosion was not found at structural members. On 10th September 2019: Corrected previously. On 04-Feb-2020: Corrected from previous inspection. On 02-Feb-2022: Corrected from previous inspection. During inspection no corrosion was found. On 04-Oct-2023: Corrected previously. During inspection, no corrosion was found in the steel members of steel stair. On 29-Sep-2025: Previously corrected. | Aug 2 2014 | Corrected
Initial Inspection |  | 9 | In the storage room on the ground floor, there are racks which are not braced against earthquake forces. Also, there are three plastic water tanks which are not braced or anchored adequately to resist earthquake force. | Adequately anchor and brace all non-structural elements to resist earthquake forces to comply with the BNBC and Alliance Standard. | Done by the 2nd review by the Alliance | Jan 14 2016 | On 15-Feb-2018: Racks were found braced during inspection. On 12-Sept-2018: This issue was corrected from previous inspection. During inspection, racks were found anchored. On 10th September 2019: Corrected previously. On 04-Feb-2020: Corrected from previous inspection. During inspection storage racks were found anchored with floor. On 02-Feb-2022: Corrected from previous inspection. During inspection no rack or plastic water tank was found. On 04-Oct-2023: Corrected previously. During inspection, no racking system was observed in the storage area. On 29-Sep-2025: Previously corrected. | Sep 13 2014 | Corrected
Initial Inspection |  | 10 | Load plans have been prepared on existing loading condition, but there is no evidence regarding consideration of design loads for which the slab is capable of. | Have a qualified structural engineer develop Floor Loading Plans per the requirements of Part 8 Section 8.20.5.3. | Done | Feb 14 2016 | On 15-Feb-2018: Factory had submitted the design report to ALLIANCE. According to ALLIANCE 5th PCVV report, design report is required to be submitted again to ALLIANCE regarding vertical extension. Load plan had been produced as part of design report. Load was found below 42 psf in most f the floors. On 12-Sept-2018: Load plan was produced as part of DEA. DEA of factory building got acceptance from Alliance on 19th January,2016. As per PCCVV on 7th Feb 2018, factory is required to revise the DEA of factory building conforming BNBC-2006 due to vertical expansion. Factory submitted revised DEA to Alliance and review comments given from Alliance. Till date of inspection, factory didn't submit DEA to Alliance. Submit revised DEA to Alliance within 20th Sept, 2018. During inspection, load plan was found posted in each floor and loading was found within allowable limit (as per previously accepted load plan). Final load plan required to be posted as per accepted DEA documents. On 10-Sept-2019: Revised documents were re-accepted from Alliance on 14th October 2018. No discrepancy was observed between accepted drawings of Factory Building and as built condition. On 04-Feb-2020: Corrected from previous inspection. Load plan was found posted & loading was found within allowable limit (63 psf On 02-Feb-2022: Corrected from previous inspection. Load plan was found posted at each floor and overall loading was found below accepted load limit (63 psf). On 04-Oct-2023: Corrected previously. Load plan was found posted on each floor and loading was found below the accepted load limit (63 psf) on typical floor area. On 29-Sep-2025: Previously corrected. | Aug 2 2014 | Corrected
Initial Inspection |  | 11 | No standard Floor load plan are posted as per Alliance standard Part 8 Section 8.20.5.3. | Have a qualified structural engineer prepare load plans including the information required in Section 8.20 of the Alliance Standard.Floor load plans should be visibly posted on all levels of all buildings. | Done | Jan 14 2016 | On 15-Feb-2018: Factory had submitted the design report to ALLIANCE. According to ALLIANCE 5th PCVV report, design report is required to submit again to ALLIANCE regarding vertical extension. Load plan had been produced as part of design report. Load was found below 42 psf in most f the floors. On 12-Sept-2018: Load plan was produced as part of DEA. DEA of factory building got acceptance from Alliance on 19th January,2016. As per PCCVV on 7th Feb 2018, factory is required to revise the DEA of factory building conforming BNBC-2006 due to vertical expansion. Factory submitted revised DEA to Alliance and review comments given from Alliance. Till date of inspection, factory didn't submit DEA to Alliance. Factory is required to submit revised DEA to Alliance within 20th Sept, 2018. During inspection, load plan was found posted in each floor and loading was found within allowable limit (as per previously accepted load plan). Final load plan required to be posted as per accepted DEA documents. On 10-Sept-2019: Revised documents were re-accepted from Alliance on 14th October 2018. No discrepancy was observed between accepted drawings of Factory Building and as built condition. Load plans were posted during inspection. On 04-Feb-2020: Corrected from previous inspection. Load plan was found posted and loading was found within allowable limit (63 psf). On 02-Feb-2022: Corrected from previous inspection. Load plan was found posted at each floor and overall loading was found below accepted load limit (63 psf). On 04-Oct-2023: Corrected previously. During inspection, appointed load manager was present and loading was found below the accepted load limit (63 psf) on typical floor area. On 29-Sep-2025: Previously corrected. | Aug 2 2014 | Corrected
Initial Inspection |  | 12 | There is no standard load plan. Also, there is no marking on the floor to designate spaces and height for storage of work materials. | Have a qualified structural engineer prepare the Load Plan for each floor and provide signage or the appropriate markings at all areas used for storage to indicate the acceptable loading limits detailed in the Load Plan. | Done | Jul 18 2016 | On 15-Feb-2018: Factory had submitted the design report to ALLIANCE. According to ALLIANCE 5th PCVV report, design report is required to submit again to ALLIANCE regarding vertical extension. Load plan had been produced as part of design report. Load was found below 42 psf in most f the floors. Load restriction height marking was observed. On 12-Sept-2018: During inspection, load limit marking was found at storage area. Final load limit required to be marked as per accepted load plan. On 10-Sept-2019: Load plans and load height markings were posted during inspection. On 04-Feb-2020: Corrected from previous inspection. During inspection load plan and load height mark were found posted. On 02-Feb-2022: Corrected from previous inspection. During inspection load plan was found posted at each floor and overall loading was found below accepted load limit (63 psf). Load restriction height mark was also found at storage area. On 04-Oct-2023: Corrected previously. Loading was found below the accepted load limit (63 psf) on typical floor area. On 29-Sep-2025: Previously corrected. | Aug 2 2014 | Corrected
Initial Inspection |  | 13 | There is no designated representative (Factory Load Manager), who is onsite full time, trained regarding the structural floor capacity, and serves as an ongoing vendor resource and monitor of operational factory floor loadings. | Designate a representative as the Factory Load Manager. The Factory Owner shall ensure that at least one individual, the Factory Load Manager who is located onsite full time at the factory, is trained in calculating operational load characteristics of the specific factory. The Factory Load Manager shall serve as an ongoing resource to RMG vendors and be responsible to ensure that the factory operational loads do not at any time exceed the factory floor loading limits as described on the Floor Loading Plans. | Done by the 2nd review by the Alliance | Jan 14 2016 | On 15-Feb-2018: Factory had assigned Mr. Md. Asaduzzaman as load manager. Load log book was observed during inspection. On 12-Sept-2018: This issue was corrected from previous inspection. During inspection, designated load manager was found to maintain load register. On 10-Sept-2019: Corrected previously. On 04-Feb-2020: Corrected from previous inspection. During inspection, designated load manager was found to maintain load register. On 02-Feb-2022: Corrected from previous inspection. During inspection, designated load manager was found to maintain load register. On 04-Oct-2023: Corrected previously. During inspection, designated load manager was present. On 29-Sep-2025: Previously corrected. | Jul 19 2014 | Corrected
Initial Inspection |  | 14 | The factory has not obtained the Certificate of Occupancy from the authority. | Provide Certificates of Occupancy for review. | N/A | Mar 12 2015 | On 15-Feb-2018: Not applicable. On 12-Sept-2018: This issue was corrected from previous inspection. On 10-Sept-2019: N/A On 04-Feb-2020: N/A. On 02-Feb-2022: N/A. On 04-Oct-2023: Corrected previously (N/A). On 29-Sep-2025: Previously corrected. | Aug 2 2014 | Corrected
Initial Inspection |  | 15 | Cracks have been identified at front side of the second level and at north side of ground level. | Have a qualified structural engineer provide further analysis of the identified cracks to determine the appropriate course of corrective action. | Done | Mar 12 2015 | On 15-Feb-2018: No crack was observed during inspection. However, the analysis should be covered in the DEA. The design report is required to be submitted again to ALLIANCE for review. On 12-Sept-2018: During inspection, no crack was found. But no analysis and repair methodology was found for the cracks. Crack analysis report and repair methodology is required to be include in DEA report. On 10-Sept-2019: No crack was observed. Also no crack investigation report was found on site. Submit crack investigation report and repair methodology with DEA. On 04-Feb-2020: No crack was found during inspection. Crack investigation report was found prepared during inspection. According to report cracks were found in plaster which propagate on surface of brick wall. Factory management had repaired the crack accordingly. On 02-Feb-2022: Corrected from previous inspection. During inspection no further crack was found. On 04-Oct-2023: Corrected previously. No cracks were found during the inspection. On 29-Sep-2025: Previously corrected. | Aug 2 2014 | Corrected
Initial Inspection |  | 16 | Dampness has been observed almost every side of the main building, especially on the main entrance side of the 2nd and 3rd level. | Repair the exterior façade system to prevent water intrusion. | Done by the first review by the Alliance | Mar 12 2015 | On 15-Feb-2018: Dampness was not found during inspection. Factory is required to monitor for any water intrusion issue. On 12-Sept-2018: This issue was corrected from previous inspection. During inspection, dampness was not found. On 10-Sept-2019: Corrected previously. On 04-Feb-2020: Corrected from previous inspection. Dampness was not found during inspection. On 02-Feb-2022: Corrected from previous inspection. Dampness was not found during inspection. On 04-Oct-2023: Corrected previously. No dampness was found during the inspection. On 29-Sep-2025: Previously corrected. | Sep 13 2014 | Corrected

## Fire
Date
10-May-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Needle Drop Ltd, 50, Chamdpara, Basin Road, Joydevpur national university, Joydevpur, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-06-02
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | A centralized automatic fire alarm and smoke detection system with a control panel is not available. Only standalone smoke detectors are available. | Install an automatic fire alarm and detection system for the facility. System shall comply with the Alliance Standard and NFPA 72. Consult a qualified fire protection engineer and/or authorized fire alarm company to design and install the system. | Fire Alarm Control Panel system is normal | Dec 22 2017 | On 03/01/2019: Fire alarm system drawing has been reviewed by Alliance. Installation was almost completed. Fire doors, HVAC system, fire pump controls should be interfaced with FACP if applicable. Factory have to prove whether the installed fire alarm control panel with required accessories & cable has been certified by recognized third party or not. (Commissioning of the system in-front of contractor/ 3rd party will be done by Accord). On 20/10/2019: Installation complete for old building but a building was found under construction phase which will be interconnected each other. Management is planning to install the system considering new building in the same system. So that, they are working on the redesign of the system. On 27-Sep-2021: Factory has provided documents to facilitate pre T&C inspection. However modification work needed. On 18/12/2022: Factory is not ready for T&C according to documents assessment (Pre T&C). See the detailed Pre T&C report. On 16/08/2023: The addressable fire alarm and detection system is ready for final T&C based on pre-T&C documents. For details see Pre-T&CVI report. On 04/10/2023: The T&CVI found that the FADS system is not Approved. See the detailed T&CVI report. On 21/11/2023 (Special Inspection): Not verified. On 28-Oct-2024: The T&CVI found that the FADS System is not approved, required another full T&CVI. For details see the T&CVI report. On 25-Sep-25: Reportedly the factory has finished all modification tasks and will provide the design and documents to RSC for T&CVI within a week. During the inspection fire alarm control panel found active and free of abnormal system conditions. On 18-Feb-26: The T&CVI found that the FADS System is not approved, required final verification inspection. For details see the T&CVI report. RPO Comments: On 10-May-2026 the T&CVI documents are reviewed & accepted. The factory is now ready for FVV inspection. The systems will be checked in the next inspection. | Dec 12 2014 | Pending Verification
Initial Inspection |  | 2 | All of the stairs are provided with steel, rolling shutter doors and one stairwell has one open door but the exit openings are more than 0.8 meters. No fire door is installed along the path of egress. | Replace non-compliant doors and frames in the means of egress with side-swinging doors. Replacement doors shall be a minimum width of 0.8 m (32 in), and are listed, approved, self-closing, fire rated door assemblies (door and frame) with latching panic hardware. | Corrected | Sep 15 2017 | On 03/01/2019: During follow up inspection smoke seal was found damaged on several installed doors on several floors as well as factory shall ensure that doors are interfacing properly with compliant Fire Alarm System by electro-magnetic door holder device as doors are keeping open. On 20/10/2019: Corrected. No non-compliant exit door was found in any of the exit. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected On 21/11/2023 (Special Inspection): Corrected. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Nov 28 2014 | Corrected
Initial Inspection |  | 3 | One door in the means of egress is collapsible and some are sliding steel type and some are open (no door provided). | Replace non-compliant doors and frames in the means of egress with side-swinging doors. Replacement doors shall be a minimum width of 0.8 m (32 in), and are listed, approved, self-closing, fire rated door assemblies (door and frame) with latching panic hardware. | Corrected | Jul 20 2015 | On 03/01/2019: Corrected. Factory has removed non-compliant doors/gates from egress routes. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected as per previous follow-up On 21/11/2023 (Special Inspection): Corrected. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Nov 28 2014 | Corrected
Initial Inspection |  | 4 | There are locking arrangements like hasps, locks, slide bolts at the exit doors but doors are not locked. | Remove all locking devices from all egress doors and means of egress components in accordance with Alliance Standard Section 6.8. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Jul 15 2015 | On 03/01/2019: Corrected. Factory has removed non-compliant locking features from egress routes exit doors/gates. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected On 21/11/2023 (Special Inspection): Corrected. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Nov 21 2014 | Corrected
Initial Inspection |  | 5 | There are 3 exit enclosures in the Main Building. Each floor entrance of the Main Building is not properly fire protected since no fire door is installed at the entrance. | Provide fire-resistive rated construction barriers and associated opening protection for exit enclosures in accordance with Alliance Standard Sections 4.5 and 4.6. Consult a qualified fire protection engineer to design the required rated construction barrier. | Corrected | Sep 20 2017 | On 03/01/2019: During follow up inspection smoke seal was found damaged on several installed doors on several floors as well as factory shall ensure that doors are interfacing properly with compliant Fire Alarm System by electro-magnetic door holder device as doors are keeping open. On 20/10/2019: Partially Corrected. Fire doors not found functional during inspection. Smoke seal not found in the door. Small portion was not properly locked or with the facility of coordination. Interfacing didn't work during inspection. On 27-Sep-2021: Doors were found damaged and with excessive clearance. In some cases field modification has been conducted that shall be permitted by manufacturer and listing authority. Inactive leaf of fire doors were found to be kept open with magnetic door holders which is not permitted because of the presence of manual flash bolts. Additionally exit stair is not separated from building interior. On 18/12/2022: Some fire doors were found damaged and field modification has been conducted that shall be permitted by manufacturer and listing authority. Exit stair-1 is not separated from building interior. On 16/08/2023: In Progress. Exit stair-1 is separated from building interior. Some fire door accessories were not found functional during inspection. On 21/11/2023 (Special Inspection): Corrected. Exit stair enclosures were found separated by fire rated construction and openings were protected by fire rated door. Fire doors were found functional and interfacing with FACP was checked and found active and functional. On 25-Sep-25: Corrected. Fire rated doors were found functional and interfaced with FADS. On 18-Feb-26: Corrected. Fire rated doors were found functional. | Dec 12 2014 | Corrected
Initial Inspection |  | 6 | Standalone detectors are available. There is no fire alarm control panel. Manual switch or pull stations for occupant notification are installed at egress point of production floors. | Install initiating devices and notification appliances as required by the Alliance Standard and NFPA 72. Connect devices to an automatic fire alarm and detection system for the facility. All fire alarm installations shall be submitted for review by the Alliance prior to commencement of installation. | Facility Management has complete FADS System. | Dec 22 2017 | On 03/01/2019: It is an integrated part of fire alarm system. On 20/10/2019: It is an integrated part of fire alarm system. On 27-Sep-2021: Integrated part of FA system. On 18/12/2022: It is an integrated part of fire alarm system. On 16/08/2023: The addressable fire alarm and detection system is ready for final T&C based on pre-T&C documents. For details see Pre-T&CVI report. On 04/10/2023: The T&CVI found that the FADS system is not Approved. See the detailed T&CVI report. On 21/11/2023 (Special Inspection): Not verified. On 28-Oct-2024: The T&CVI found that the FADS System is not approved, required another full T&CVI. For details see the T&CVI report. On 25-Sep-25: Corrected. No standalone detectors have been found installed. The issue is part of the integrated fire alarm system and has already been addressed under CAP-1. As the system is currently in the T&C verification stage, the issue is considered resolved. On 18-Feb-26: Corrected | Dec 12 2014 | Corrected
Initial Inspection |  | 7 | Only 30 people are trained and certified by BGMEA out of 890 people in fire fighting, first aid and rescue by the appropriate authority. | Train and certify at least 25 percent of workers in fire fighting, first aid, and rescue by the proper authority as per Alliance Standard. | Corrected | Jun 30 2016 | On 03/01/2019: Corrected as per previous follow up. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Dec 17 2014 | Corrected
Initial Inspection |  | 8 | All the openings, penetrations, and ducts through rated walls in the assessed buildings were found to be non-rated. Some major locations are: A non-rated aluminum glass window opening exists in between the Main Building (northeast side of ground floor and 1st floor) and generator shed. Non-rated opening of finished goods storage exists with Generator Shed. A non-rated opening in the electrical accessories storage exists beside the doctor's room. | Provide fire-resistive rated opening and penetration protection for rated walls and assemblies in accordance with Alliance Standard Sections 4.6 and 4.7. Consult a qualified fire protection engineer to design the required opening protectives and penetration systems. | Corrected | Sep 30 2016 | On 03/01/2019: Corrected. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Dec 12 2014 | Corrected
Initial Inspection |  | 9 | Occupancy separations are not fire rated and the opening protections are not fire rated as well. Some major locations are: spot removing room on the ground floor with glass and aluminum partitions. The spot lifter uses compressed air guns beside the production area, and the separation is not fire rated. Proper separation is not provided on ground floor of Main Building between bonded warehouse and accessories storage. Proper separation is not provided between warehouse and production floor on 2nd floor of Main Building. The generator room is not provided with proper separation at north-east corner of Main Building. | Provide fire-resistive rated construction barriers between hazard types in accordance with Alliance Standard Sections 3.4 and 4.5. Consult a qualified fire protection engineer to design the required rated construction barrier. | Corrected | Sep 20 2017 | On 03/01/2019: Corrected. Factory has separated store room from production floor by fire rated construction. During follow up inspection it was observed that factory only using surf excel (liquid) in spot removing room. Generator room is located in separate building. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Dec 18 2014 | Corrected
Initial Inspection |  | 10 | An automatic fire alarm and detection system is not available in the factory. Currently there is no monitoring company in Bangladesh. Fire service and Civil Defence is not capable of monitoring fire alarm and detection systems of the factories. | Install a new automatic fire alarm and detection system. Once installed, arrange for direct connection of the fire alarm and detection system to a central station monitoring service or the Fire Service and Civil Defence as per Alliance Standard Section 5.7.5. Until that time, a person trained to contact the Fire Service and Civil Defence in the event of fire alarm activation shall be provided. An annunciator shall be located in a constantly attended location (such as a fire control room) to alert this person. | Corrected | Mar 31 2016 | On 03/01/2019: Corrected. Factory has assigned a dedicated fire officer to monitor Fire Alarm System. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Dec 12 2014 | Corrected
Initial Inspection |  | 11 | Fabrics are stored underneath the cutting tables at the cutting section on the ground floor of the Main Building. | Remove all combustibles stored underneath the cutting tables at the noted locations. | Corrected | Mar 24 2016 | On 03/01/2019: Corrected. Removed. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Nov 14 2014 | Corrected
Initial Inspection |  | 12 | On the ground floor of the main building, there is a maintenance room with sewing machines. This is not permitted as per the Alliance Standard. | Remove all types of occupancy from stair enclosure to clear stair enclosure. | Corrected | Apr 20 2016 | On 03/01/2019: Corrected. Removed. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Aug 15 2014 | Corrected
Initial Inspection |  | 13 | None of the stairwells have handrails on both sides in any building of the factory premises. | Provide handrails on both sides of each stairway. Provide intermediate handrails when the stair width exceeds 2.2 m (87 in). Provide handrail of height between the range 865 mm (34 in) and 965 mm (38 in) as per Alliance Standard. | Corrected | Jan 31 2016 | On 03/01/2019: Corrected. Provided. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Dec 18 2014 | Corrected
Initial Inspection |  | 14 | A record of verifying emergency power for means of egress illumination is not found as required in accordance with Alliance Standards. | Develop a testing and maintenance program that ensures the operation of all egress lighting is verified at least once per year. If battery-operated lights are used, they shall be tested on a monthly basis. Functional testing of battery powered lights shall be provided for a minimum of 90 min once per year. | Corrected | Jan 28 2015 | On 03/01/2019: Corrected. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Nov 14 2014 | Corrected
Initial Inspection |  | 15 | Occupant loads are not posted in a conspicuous space near the main exits or exit access doorways as per the Alliance Standard. | Post the occupant load for every assembly or production floor in a conspicuous space near the main exit or exit access doorway for the space as per the Alliance Standard. | Corrected | Jan 15 2016 | On 03/01/2019: Corrected. Posted. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected On 21/11/2023 (Special Inspection): . Corrected. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Nov 21 2014 | Corrected
Initial Inspection |  | 16 | Illuminated exit signs are placed at entrances to exits, but not along the path of egress where there is a change in direction and where the continuation of egress is not obvious. | Provide continuously illuminated exit signs per Alliance Standard Section 6.11. Signs shall be placed at all required exits and along egress paths, especially where there is a change in direction for the path of travel. | Corrected | Jan 31 2016 | On 03/01/2019: Corrected. Provided. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Dec 17 2014 | Corrected
Initial Inspection |  | 17 | No plan or record of conducting periodic tests of the emergency battery backup for illumination of exit signs was found as required. | Develop a testing and maintenance program that ensures the emergency power for exit signs is tested at least once per year. If battery operated signs are used, these signs are tested on a monthly basis. Functional testing of battery powered signs is provided for a minimum 90 min once per year. | Corrected | Jan 28 2015 | On 03/01/2019: Corrected. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected. On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Nov 14 2014 | Corrected
Initial Inspection |  | 18 | Workers are aware of the evacuation procedure upon commencement of the alarm. However, no procedure defining evacuation process was available. | Develop an emergency evacuation plan which includes all components required by the Alliance Standards and communicate the plan to all employees. | Corrected | Mar 28 2015 | On 03/01/2019: Corrected. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected. On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Nov 21 2014 | Corrected
Initial Inspection |  | 19 | No document of any training program in accordance with the Alliance Safety Training Curriculum is found. Factory authority arranged for some training, but it is not in accordance with the Alliance Safety Training Curriculum. | Implement training programs and document in accordance with the Alliance Safety Training Curriculum. | Corrected | Jan 28 2015 | On 03/01/2019: Corrected. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected. On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Nov 28 2014 | Corrected
Initial Inspection |  | 20 | Building approval is for a commercial building as of 28/02/2007. A BERC waiver certificate for 250KW capacity generators is available. Factory applied for electrician license on 24/12/2013. There are two boilers; one boiler license is available and the other boiler license is currently being renewed. Boiler operator license is available. Factory license, fire licenses, and trade license are up-to-date. | Apply to Biddyut Paridaptor for electrician license. Apply to Gazipur City Corporation for approval of the unapproved prefab shed and also to approve the Main Building as an industrial building. Apply to boiler inspection department for the boiler license. | Corrected | Jul 28 2015 | On 03/01/2019: Corrected. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected. On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Nov 14 2014 | Corrected
Initial Inspection |  | 21 | A hot-work permit program is not established. However, hot-work is not taking place in the factory right now. | Develop a hot work permit program. The program must comply with the requirements of NFPA 51B. | Corrected | Jan 28 2015 | On 03/01/2019: Corrected. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected. On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Dec 18 2014 | Corrected
Initial Inspection |  | 22 | No occupancy certificates are available for any building on the factory premises. | Apply to Gazipur City Corporation in an expeditious manner for issuance of the Certificates of Occupancy for each building and ancillary structure according to building use. | Corrected | Jun 30 2006 | On 03/01/2019: Corrected. Not Applicable. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected. On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Nov 21 2014 | Corrected
Initial Inspection |  | 23 | Fire department pre-planning has not been completed. | Complete fire department pre-planning activities with the local Fire Service and Civil Defence in accordance with the Alliance Standard. | Corrected | Mar 31 2016 | On 03/01/2019: Corrected. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected. On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Nov 14 2014 | Corrected
Initial Inspection |  | 24 | Floor level is posted but stair name or designation are not mentioned. | Install signage adjacent to each stair door indicating the stair name and the floor level in English and Bengali at the noted locations in accordance with the Alliance Standard. | Corrected | Jan 1 2016 | On 03/01/2019: Corrected. Provided. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected. On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Nov 21 2014 | Corrected
Follow Up Inspection |  | 25 | New Finding (2nd Follow-up): The existing factory building with an occupiable floor greater than 10 m (33 ft) above the finished grade is protected with an standpipe system. Design was reviewed from Alliance. | System commissioning is pending. Fire pump controls shall have to be interfaced with Fire Alarm system properly. Factory needs to prove whether the system equipments are third party certified or not. | Standpipe system all deficiencies are addressed properly done. | Dec 11 2017 | On 03/01/2019: Standpipe system drawing has been reviewed Alliance. During follow up inspection it was observed that factory has installed centrifugal fire pump in negative suction. Factory shall install listed fire pump in positive suction as per NFPA 20. On 20/10/2019: Pump modification not done. UGWR constructed in new building, management is planning to install the system considering new building in the same system. So that, they are working on the redesign of the system. On 27-Sep-2021: Factory has provided documents to facilitate pre T&C inspection. However modification work needed. On 18/12/2022: Factory is not ready for T&C according to documents assessment (Pre T&C). See the detailed Pre T&C report. On 16/08/2023: Follow-up inspection was conducted with Pre-T&CVI inspection. Pre-T&CVI recommended an on-desk review after modification some non-conformities identified during inspection. For details see Pre-T&CVI report. On 21/11/2023 (Special Inspection): Not verified. On 14-Jul-2024: The T&CVI found that the SUPS (Standpipe) System is required final verification inspection. For details see the T&CVI report. On 25-Sep-25: Final verification inspection (FVI) has been conducted, and the system is approved. For details see FVI report. On 18-Feb-26: Corrected. System found functional. | Within 2 months | Corrected
Follow Up Inspection |  | 26 | New Finding in 3rd Follow-up: Unsealed penetrations and openings are located in the fire rated floor/ceiling assemblies. Location: Electrical riser at North-west side of the building. | Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor level. Seal all penetrations and openings in floors/ceiling assemblies to maintain the fire separation. | Corrected | Aug 20 2017 | On 03/01/2019: Corrected. Sealed. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Within 1 month | Corrected
Follow Up Inspection |  | 27 | New Finding in 3rd Follow-up: The boiler room is not separated by fire rated construction (openings, non-rated doors, penetrations). | Separate the boiler room by a minimum 2-hr fire rated construction (for high rise building)/ 1-hr fire rated construction (for low rise building). Seal and/or protected all openings to maintain fire separations | Corrected | Aug 20 2017 | On 03/01/2019: Corrected. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected. On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Within 1 month | Corrected
Follow Up Inspection |  | 28 | New Finding in 3rd Follow-up: Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected | Aug 20 2017 | On 03/01/2019: Corrected. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected. On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Within 1 month | Corrected
Follow Up Inspection |  | 29 | New Finding in 3rd Follow-up: Manual on-off switch is provided for [emergency lighting / exit signage] units. | Remove manual on/off switches from [emergency lighting /exit signage] units to prevent them from being switched off | Corrected | Apr 14 2017 | On 03/01/2019: Corrected. Removed. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected. On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Within 1 month | Corrected
Follow Up Inspection |  | 30 | New Finding in 3rd Follow-up: Storages (combustibles, IPS etc.) were located in exit stair. | Remove storage from the exit stairs and egress path | Corrected | Mar 17 2017 | On 03/01/2019: Corrected. Removed. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected. On 21/11/2023 (Special Inspection): Corrected. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Immediate | Corrected
Follow Up Inspection |  | 31 | New Finding in 3rd Follow-up: Areas used for combustible storage are not separated by fire-rated construction | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m | Facility Management has been shift of condustible materials from cutting to dedicated fabric store. | Apr 14 2017 | On 03/01/2019: Corrected. Not observed during inspection. On 20/10/2019: Corrected. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected on previous follow-up. Note: Vestibule shall be provided in stair 4 & 5 of the extension part on 1st & ground floor where the storage rooms discharge directly into the exit stair enclosure. On 16/08/2023: Corrected. Note: Vestibule shall be provided in stair 4 & 5 of the extension part on 1st & ground floor where the storage rooms discharge directly into the exit stair enclosure. On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Issue re-opened. In-process storages were observed not maintaining as per standard on the ground floor in the main building. RPO Comments: On 10-May-2026 the factory management reported the remediation completion. This item will be verified in the next inspection | Within 1 month | Pending Verification
Follow Up Inspection |  | 32 | New Finding (4th Follow-up): Liquefied or compressed gas cylinders were located besides dining. | Separate the hazardous materials / flammable liquid storage room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations or Remove from egress path. | Corrected | Aug 20 2017 | On 03/01/2019: It was found same as it was before. On 20/10/2019: Corrected. Removed. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected. On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected. Not found. On 18-Feb-26: Corrected | Within 1 month | Corrected
Follow Up Inspection |  | 33 | New Finding (4th Follow-up): Doors along means of egress are provided with non compliant locking system at all exit discharges on ground floor, three stair on roof top and dinning | 1. Remove all non compliant locking features from egress doors. 2. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. 3. Doors may be locked where the latch and lock are disengaged with one motion where the occupant load does not exceed 49 persons. 4. Doors may be provided with locking hardware from the ingress side provided that a panic bar is installed on any door with an occupant load exceeding 49 persons. | Corrected | Aug 20 2017 | New Finding (4th Follow-up) On 26/04/2018: Corrected. On 03/01/2019: Corrected. Removed. On 27-Sep-2021: Corrected on previous follow-us. On 18/12/2022: Corrected. On 16/08/2023: Corrected. On 21/11/2023 (Special Inspection): Corrected. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Immediate | Corrected
Follow Up Inspection |  | 34 | New Finding (8th FU/RSC): Penetrations through floor/ceiling assemblies are found unsealed. Location(s): Construction joint between the buildings. | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. If Proprietary materials are used for seal, then it shall be classified for the purpose it is classified for. | Corrected | Oct 28 2021 | On 27-Sep-2021: New Finding. Comments from CH- On 07.07.2022 : No timeline extension has been accepted. Corrective action plan should be completed as per the given recommendation with immediate concern. On 18/12/2022: Penetrations through floor/ceiling assemblies were found due to expansion joint and electric cable riser. Factory is in planning phase to remediate this issue. On 16/08/2023: Corrected. Factory has sealed the expansion joint and electric cable riser by fire stop materials. On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Within 1 month | Corrected
Follow Up Inspection |  | 35 | New Finding (9th Follow-up): Dining area has been found with production section at 2nd floor without proper fire rated seapration. | Dining shall be separated from other occupancies according to RSC Technical Guidelines (Standard) Part 3 Secton 3.4.1. | Corrected | Mar 18 2022 | On 18/12/2022: New Finding On 16/08/2023: Corrected. Factory has shifted the dining area from 2nd floor to roof floor. Roof floor dining area is separated from others occupancies. On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected On 18-Feb-26: Corrected | Within 3 months | Corrected
Follow Up Inspection |  | 36 | New Finding in 10th Follow-up: Egress aisle has not been marked properly and the width of egress aisles are less than 36-inch on ground floor. | Aisles shall be marked and provided with a minimum unobstructed clear-width of 0.9 m (36 in.) accordance with RSC technical guidelines (Standard) 6.5.1. | Facility Management already done Aisles Mark clear width morethen 36 in at Ground & 2nd Floor | Sep 16 2023 | On 16/08/2023: New Finding On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected. The factory provided aisles on the ground floor. On 18-Feb-26: Corrected | 1 month | Corrected
Follow Up Inspection |  | 37 | New Finding in 10th Follow-up: Exit stair door/egress door serving 50 or more occupants does not swing in the direction of egress travel. Location: Roof floor, | Modify the egress door to swing in the direction of egress travel. | Facility Management already Modified the exit door to swing in the direction of exit travel. | Sep 16 2023 | On 16/08/2023: New Finding On 21/11/2023 (Special Inspection): Not verified. On 25-Sep-25: Corrected. The factory has altered the swing direction of the roof doors to facilitate egress. Additionally, the dining area on the roof floor has been removed, found an idle machine storage area, which accommodates an occupant load of four individuals. On 18-Feb-26: Corrected | 1 month | Corrected
Follow Up Inspection |  | 38 | New Finding (12FU): Directional signs are not provided at some required locations at all the storage areas in the main building. | Illuminated directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.11.3. | Facility Management has provided directional signs at all the storage areas in the main building. | Mar 18 2026 | On 18-Feb-26: New Finding. RPO Comments: On 10-May-2026 the factory management reported the remediation completion. This item will be verified in the next inspection | Within 1 months | Pending Verification
Follow Up Inspection |  | 39 | New Finding (12FU): Evacuation map is not proper as aisles layout does not match in maximum floors in the main building. | Update the fire evacuation map and shall be posted at the entrance to each exit stair in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 13.3. | Facility Management has corrected evacuation map with aisles layout in all floors in the main building | Mar 18 2026 | On 18-Feb-26: New Finding. RPO Comments: On 10-May-2026 the factory management reported the remediation completion. This item will be verified in the next inspection | Within 1 months | Pending Verification
Follow Up Inspection |  | 40 | New Finding (12FU): Water tap and wash basin were observed in the Stair-2 enclosure, and water tap piping arrangements were observed in the Stair-1 enclosure of the main building, which may create slip hazards due to water spillage and adversely affect safe egress during an emergency. | Remove the water taps arrangements & basin from exit stair enclosures. | Facility Management will be Removed the water taps & basin from exit stair area. | Apr 18 2026 | On 18-Feb-26: New Finding. RPO Comments: On 10-May-2026, the provided final timeline has been expired. Threfore, the corrective action plan should be completed as per the given recommendation with immediate concern. | Within 2 months | In Progress

## Electrical
Date
10-May-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Needle Drop Ltd, 50, Chamdpara, Basin Road, Joydevpur national university, Joydevpur, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-06-02
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Workers that operate and maintain the electrical system have not received electrical safety training. | Develop and implement an electrical safety program. Include key topics such as lock out tag out procedures, personal protective equipment requirements, etc. Keep records of completed training available on site. |  | Jan 31 2015 | On 27/12/2015: Factory should continue this training program periodically. On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 30 2014 | Corrected
Initial Inspection |  | 2 | Not all metal in the building is connected to the building grounding system such as metal rebar in concrete, metal frame of building or metal water pipe. | Connect all metal in the building to the building grounding system such as metal rebar in concrete, metal frame of building or metal water pipe. |  | May 26 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 30 2014 | Corrected
Initial Inspection |  | 3 | Underground service cables are not laid in conformity with the requirements of concealed wiring. | Ensure underground cables for electrical distribution in the premises of the building are encased in GI or PVC pipes and laid in earth trenches of sufficient depth as per BNBC 2.5.7.2. | Corrected | Sep 15 2016 | On 27/12/2015: This issue is not corrected yet . New committed timeline is till 29/02/16. On 24/03/2016: This has not been resolved yet. The time extension is given till 31/05/2016. On 14/03/2017: Not Corrected. Work in progress. On 20/06/2017: Not Corrected On 25/10/2017: Corrected. | Jul 30 2014 | Corrected
Initial Inspection |  | 4 | The substation room does not have the required fire rating/protection and is not physically separated from the remainder of the building. | Provide adequate fire rating/protection for substation room and make it separate from rest of the building. | Corrected | Sep 20 2016 | On 27/12/2015: This issue is not corrected yet . New committed timeline is till 29/02/16. On 24/03/2016: This has not been resolved yet. The time extension is given till 31/05/2016 On 14/03/2017: Corrected. | Jul 30 2014 | Corrected
Initial Inspection |  | 5 | Generator room is not properly rated but it is physically separated from the remainder of the building. | Ensure the generator room properly rated and physically separated from the remainder of the building. | Corrected | Sep 20 2016 | On 27/12/2015: This issue is not corrected yet . New committed timeline is till 29/02/16. On 24/03/2016: This has not been resolved yet. The time extension is given till 31/05/2016 On 14/03/2017: Corrected. | Jul 16 2014 | Corrected
Initial Inspection |  | 6 | Emergency power switchboards, distribution boards and circuits are not properly identified. | Ensure proper identification of emergency power switchboards, distribution boards and circuits. |  | Apr 22 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 2 2014 | Corrected
Initial Inspection |  | 7 | Electrical drawings indicating information such as panel and circuit locations throughout the building(s) were available but not “As-Built”. | Have a qualified electrical engineer develop an as-built single line diagram detailing key components and capacity of the electrical system. | The facility has completed an as-built single line diagram detailing key components and capacity of the electrical system . | Feb 15 2016 | On 27/12/2015: Some mismatch found. New timeline is till 15/02/16. | Jul 30 2014 | Corrected
Initial Inspection |  | 8 | Distribution board are metal enclosed but don't have dead front construction. | Ensure distribution boards are metal enclosed with a dead front construction. | It has been done, distribution boards are metal enclosed with a dead front construction. | Apr 22 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 2 2014 | Corrected
Initial Inspection |  | 9 | Electrical cables are not sized according to capacity of circuit breakers. | Consult with a qualified Electrical Engineer and ensure electrical cables are sized according to capacity of circuit breakers. | It has been done & appointed a qualified electrical engineer to ensured all electrical cables are sized according to capacity of circuit breakers. | Jun 4 2015 | On 24/03/2015: This issue had been found corrected in the 1st follow-up visit. | Jul 30 2014 | Corrected
Initial Inspection |  | 10 | Generator room is not properly ventilated. Generator is placed in the substation room and there is no forced ventilation provided. | Ensure proper ventilation for generator room. | Corrected | Sep 30 2016 | On 27/12/2015: This issue is not corrected yet . New committed timeline is till 29/02/16. On 24/03/2016: This has not been resolved yet. The time extension is given till 31/05/2016. On 14/03/2017: Corrected. | Jul 16 2014 | Corrected
Initial Inspection |  | 11 | No additional insulation is provided for wiring exposed to external heat sources. | Provide Shielding for wiring exposed to external heat sources. | It has been done periodically wiring insulation test for adequate insulation. | Jun 3 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 16 2014 | Corrected
Initial Inspection |  | 12 | The lightning protection ground terminals are not bonded to the building or structure grounding. | Take necessary action so to make the lightning protection ground terminals are bonded to the building or structure grounding. | Corrected | Apr 30 2016 | On 27/12/2015: This issue had been found corrected in the 1st follow-up visit. On 24/03/2016: The LPS has been uninstalled due to new construction purpose. Now re-installation work is going on. The time extension is given till 30/04/2016. On 14/03/2017: Not Corrected. On 20/06/2017: Not Corrected On 25/10/2017: Not corrected. Installation has not been done properly. On 26/04/2018: Corrected. | Jul 16 2015 | Corrected
Initial Inspection |  | 13 | The size of generator room is not appropriate. Inadequate clearance between wall and generator. | Ensure appropriate size for generator room in order to properly access the generator to perform routine maintenance activities. | increased size for generator room in order to properly access the generator to perform routine maintenance activities, further management make decided to change the generator room another constructed shed. | Feb 29 2016 | On 27/12/2015: This issue is not corrected yet. New committed timeline is till 29/02/16. | Aug 27 2014 | Corrected
Initial Inspection |  | 14 | No evidence found to review that, transformer does not contain harmful substances such as PCBs. | Collect proper evidence (certificates) from the transformer manufacturing company to confirm transformer does not have any harmful substances such as PCBs. | It has been done & received certificates from the transformer manufacturing company. | Apr 20 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 30 2014 | Corrected
Initial Inspection |  | 15 | No periodic safety inspections of the electrical system components are completed. | Establish a periodic inspection program to ensure the electrical systems are free from damage, debris, dirt, lint, etc. Maintain records concerning inspections and follow up actions. | It has been done & Establish a periodic inspection program to ensure the electrical systems are free from damage, debris, dirt, lint, etc. Maintain records concerning inspections and follow up actions. | Mar 28 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 30 2014 | Corrected
Initial Inspection |  | 16 | Records concerning the testing and inspection of the electrical systems are not maintained on site and up to date. | Develop an electrical maintenance program that includes inspections and testing of the electrical systems. Reference NFPA 70 for example program requirements. | It has been done & Testing and inspection records of the electrical systems are available as per NFPA 70 Standard | Jun 3 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 30 2014 | Corrected
Initial Inspection |  | 17 | The electrical switchgear and panel boards are not inspected on an annual basis to ensure that the equipment is installed in accordance with the listed ratings. | Inspect electrical switchgear and panel boards on an annual basis to ensure that the equipment is in good working condition. | It has been done & have prepare an annual basis inspection record for electrical switchgear and panel boards. | Jun 3 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 30 2014 | Corrected
Initial Inspection |  | 18 | Thermo graphic scans of electrical equipment are not completed. | Complete thermo graphic scans at least on a three year cycle. | It has been done & electrical equipment are completed thermo graphic scans . | Apr 22 2015 | On 27/12/2015: Implementation required as soon as possible. On 24/03/2016: This issue had been found corrected in 1st follow-up visit. | Jul 30 2014 | Corrected
Initial Inspection |  | 19 | Periodical Insulation Resistance Measurement Program established but no record found of insulation resistance. | Develop an Insulation Resistance Measurement Program that ensures deterioration of insulation resistance will be identified quickly. Testing should be in compliance with International Electrical Testing Association (NETA). | It has been done & Periodical Insulation Resistance Measurement program established and insulation resistance record are available | Mar 22 2015 | On 27/12/2015: Plan for next with proper format. On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 30 2014 | Corrected
Initial Inspection |  | 20 | Electrical cables are not properly identified. | Ensure the means of identification is obtained by separate color coding, marking tape, tagging or other approved means. | It has been done & present electrical cables are properly identified. | Mar 22 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 30 2014 | Corrected
Initial Inspection |  | 21 | Distribution boards have no clear identification markings. The markings found on temporary basis, printed on plastic. | Ensure clear and permanent identification marks are painted in all distribution boards, switchboards, sub main boards and switches. | It has been done & distribution boards have clear identification markings. | Dec 3 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 2 2014 | Corrected
Initial Inspection |  | 22 | Distribution boards do not have proper capacity information labels. There are improper postings that contain some information. | Provide capacity information labels (Maximum current rating, no of circuit breakers etc.) for distribution boards. | It has been done & distribution board have proper capacity information labels. Provided maximum current rating. | Apr 25 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 16 2014 | Corrected
Initial Inspection |  | 23 | Inadequate mechanical guards are provided for electrical equipment. The exhaust fans are installed at an inaccessible height and closely attached to the walking path of working floors. | Provide mechanical guards for electrical equipment where necessary. | It is done & Adequate mechanical guards for electrical equipment are available | Feb 29 2016 | On 27/12/2015: This issue is not corrected yet . New committed timeline is given till 29/02/16. | Jul 2 2014 | Corrected
Initial Inspection |  | 24 | The appropriate numbers of down conductors are not installed based on the building size. 24 lightning arresters and 4 down conductors are installed on the building. | Consult with an Expert electrical engineer to make sure your system have appropriate numbers of down conductors are installed based on the building size. | Corrected | Apr 20 2016 | On 27/12/2015: The appropriate numbers of down conductors are not installed. On 24/03/2016: The LPS has been uninstalled due to new construction purpose. Now re-installation work is going on. The time extension is given till 30/04/2016. On 14/03/2016: Not Corrected. On 20/06/2017: Not Corrected On 25/10/2017: Not corrected. Base plates for air terminals are missing in several points. On 26/04/2018: Corrected. | Jul 27 2014 | Corrected
Initial Inspection |  | 25 | Cable sockets are not provided for stranded conductors. | Provide cable sockets for stranded conductors having a nominal cross-sectional area 6mm2 or greater. Conductors below 6 mm2 without cable sockets, all strands at the exposed ends are soldered together or are crimped using suitable sleeve or ferrules. | It has been done & all cable sockets are provided for stranded conductors. | Apr 20 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 16 2014 | Corrected
Initial Inspection |  | 26 | Electrical wiring and conduit is not properly supported. 11KV cable hanged without mechanical guard in substation room. | Provide adequate supports for electrical wiring and conduit. | Corrected | Sep 30 2016 | On 27/12/2015: This issue is not corrected yet . New committed timeline is till 29/02/16. On 24/03/2016: This has not been resolved yet. The time extension is given till 31/05/2016 On 14/03/2017: Corrected. | Jul 16 2014 | Corrected
Initial Inspection |  | 27 | The substation room does not have adequate ventilation. Though there are lots of openings in substation room but no exhaust fan for forced ventilation for a diesel generator in the room. | Provide means of ventilation for the substation room. Consult a qualified electrical engineer to determine the required ventilation rates based on the installed equipment. | Corrected | Sep 30 2016 | On 27/12/2015: This issue is not corrected yet . New committed timeline is till 29/02/16. On 24/03/2016: This has not been resolved yet. The time extension is given till 31/05/2016 On 14/03/2017: Corrected. | Jul 16 2014 | Corrected
Initial Inspection |  | 28 | Generator room is not properly illuminated. There is lighting provided in the substation room which is adequate but inadequate lighting provided in the generator side. | Ensure generator room is properly illuminated. | Our Management agree to build another generator shed to transfer generator to make ensure the generator room properly rated | Sep 30 2016 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 16 2014 | Corrected
Initial Inspection |  | 29 | Distribution boards are not provided with physical means to prevent the installation of more over current devices than that number for which the panel board was designed, rated and listed. | Ensure distribution boards provided with physical means to prevent the installation of more over current devices than that number for which the panel board was designed, rated and listed following NFPA 70 section 408.54. | It has been done & Provided with physical means to prevent the installation of more over current devices. | Feb 15 2016 | On 27/12/2015: This issue is not corrected yet . New committed timeline is till 15/02/16. | Jul 30 2014 | Corrected
Initial Inspection |  | 30 | Internal components of distribution boards are not properly concealed. There is a opening at the bottom of the panel. | Provide covers or blanks to conceal all live internal components of distribution boards. | It has been done & Internal components of distribution boards are properly concealed at now. | Mar 26 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 2 2014 | Corrected
Initial Inspection |  | 31 | Electrical wires are not properly terminated. | Ensure all electrical wiring properly terminated at its point of termination. | It has been done & Ensured all electrical wiring are properly terminate at its point of termination. | Mar 20 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 30 2014 | Corrected
Initial Inspection |  | 32 | Transformer oil analysis is not routinely completed on main service transformer. | Complete an oil analysis on applicable transformers at appropriate intervals based on voltage and power. | It has been done & Transformer oil analysis is routinely completed document is available on side at now. | Mar 22 2015 | On 27/12/2015: There is a document of transformer oil analysis dated at 24/05/2015 and factory should continue this testing periodically. On 24/03/2016: This issue has been found corrected during 1st follow-up visit. | Jul 30 2014 | Corrected
Initial Inspection |  | 33 | Inspection, maintenance and testing procedures of the IPS are not completed. | Ensure inspection, maintenance and testing procedures of the UPS and IPS are completed and documented. | It has been done & Procedures of UPS and IPS testing and maintenance document is available on side at now. | Feb 20 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 30 2014 | Corrected
Initial Inspection |  | 34 | No signage indicating the prohibition of light fixtures without protective covers is installed at required locations. | Ensure Signage indicating the prohibition of light fixtures without protective covers is installed at required locations. | It has been done & Provided adequate signage indicating all the prohibition of installation of naked light fixtures. | Mar 28 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jun 30 2014 | Corrected
Initial Inspection |  | 35 | Inspection, maintenance and testing procedures of the emergency generator are not being completed. There is a checklist for emergency generator but no maintenance & testing records. | Ensure inspection, maintenance and testing procedures of the emergency generator being completed and documented. | It has been done & Inspection, maintenance and testing procedures of the emergency generator was completed and documented. | Mar 28 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 30 2014 | Corrected
Initial Inspection |  | 36 | Inadequate required equipment and safety signage is posted within the substation room. | Ensure required equipment and safety signage is posted within the substation room. | It has been done & Provided adequate required equipment and safety signage is posted within the substation room | Feb 28 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 2 2014 | Corrected
Initial Inspection |  | 37 | Inadequate electrical insulation mats are provided in front of substation and distribution boards. | Provide electrical insulation mats in front of distribution boards of adequate size. | It has been done & Provided electrical insulation mats in front of all distribution boards of adequate size. | Feb 28 2015 | On 24/03/2016: This issue had been found corrected in the 1st follow-up visit. | Jul 2 2014 | Corrected
Follow Up Inspection |  | 38 | New Finding: Field information has no/less reflection in existing SLD. | Electrical SLD shall be updated properly; all the required information shall be mentioned there; and it shall be updated when you do substantial amount of changes of your electrical system. | Corrected | Jul 30 2017 | On 20/06/2017: Not Corrected. New committed time line is given till 30/07/2017 to close this issue. On 25/10/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 39 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) shall kept at least 0.9 meter apart from any electrical installation. In unavoidable case heat source shall be covered by proper and adequate insulator. | Corrected | Jul 30 2017 | On 25/10/2017: Corrected. | 1Month | Corrected
Follow Up Inspection |  | 40 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, shall be made following proper guidance. | Completed | Dec 10 2019 | On 26/09/2021: Corrected. | 1Month | Corrected
Follow Up Inspection |  | 41 | New Finding: At the cutting section, power sockets are hanging or kept on the floor. | Power socket has to be installed with proper locking arrangement for cables. Need to provide rigid support/base and at minimum 200mm above floor level. It cannot be hanged. | Completed | Dec 10 2019 | On 26/09/2021: work's been started, but not finished yet. Not Corrected. On 18/12/2022: Corrected. | 1Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Field information has no/less reflection in existing SLD. | Factory is required to resubmit SLD to RSC for another Review with CAD file, load table & earthing layout. |  | Nov 10 2021 | On 18/12/2022: SLD has been submitted to RSC for review. On 16/08/2023: Not corrected. Phase identification, all Load identification, all TOB identification needs to be done as per accepted SLD. On 24/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Thermography survey record is not prepared properly(Panel partially covered). Hot spots have been observed at some points. | Thermography survey shall be done and recorded at least twice in a year. Hot spots shall be removed. | Work is completed | Nov 10 2021 | On 18/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Insulation resistance test of electrical power cables is manipulated(Data randomly copied & report has no pictorial evidence). | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) shall be performed once every 2 years cycle and recorded (this shall require a complete power shut off). Pictorial evidence is required. | Work is completed | Nov 10 2021 | On 18/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Both LPS drawing and installation need modification. Air terminal missing at some places. Air terminals ate not installed at a proper height. Metal bonding missing. | Modification work shall be done according to acknowledged standard. | Completed | Nov 10 2021 | On 18/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Distribution boards have no clear identification markings. Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at a visible location. Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manually operated machinery) shall be ensured. | Completed | Nov 10 2021 | On 18/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Lighting circuits and sockets are not separated in the electrical system. | Lighting circuits and sockets shall be installed separately (shall have no interconnections). | Completed | Nov 10 2021 | On 18/12/2022: Those sockets has been removed. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Tap-off box has openings & BBT end cover is missing. Cable channel/duct terminals are left open for ingression of lint, dust or fluffs. Wooden support used for electrical installation/element. | Unwanted openings shall be sealed & BBT end cover needs to be installed. cable ducts shall be properly sealed to avoid the ingress of any foreign particles. Replace wooden support and it is preferable to fix each electrical devices with noncombustible support. | Completed | Nov 10 2021 | On 18/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Electrical power cables(including neutral & earthing) are not identified properly. | Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables used in the system according to SLD. | Work is completed (Re-submit revised SLD as per review 06.03.2023) | Nov 10 2021 | On 18/12/2022: The work is in progress. Factory will complete it after getting the reviewed SLD. On 16/08/2023: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Uninsulated electrical tools are used by maintenance personnel in the factory. | For maintenance purposes, all the electrical tools shall be properly insulated and these insulations shall be checked periodically. | Completed | Nov 10 2021 | On 18/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) shall be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Completed | Nov 10 2021 | On 18/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Inadequate illumination in front of panel. | Ensure adequate illumination in front of panel, thus any maintenance can be done comfortably (150 lux shall be maintained). | Completed | Nov 10 2021 | On 18/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: No PPE are used by maintenance personnel in the factory. Electric safety training program document is not enriched enough. | For maintenance purposes, all the electrical tools shall be properly insulated and these insulations shall be checked periodically & proper PPE shall be arranged. It is a periodic task that which factory has to continue to improve the overall electrical safety situation for the staff.(Factory may follow NFPA 70E). | Completed | Nov 10 2021 | On 18/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: Materials used to enclose MCCB is improper. | Each MCCB/MCB shall be enclosed with the proper type of material. the material shall not be more than 18 SWG graded. | Completed | Nov 10 2021 | On 18/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding: Power cables are bent excessively. Phase barrier/separators are missing in MCCBs. | Power cables shall be installed as straight as possible; in unavoidable cases, not less than 135-degree bending can be allowed. Phases shall be separated by an insulator (a rubber type no-flammable materials shall be used for it). | Work is completed (Re-submit revised SLD as per review 06.03.2023) | Nov 10 2021 | On 18/12/2022: Cable bending is found for a few panels. Phase separator is provided at the circuit breaker terminals. On 16/08/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 56 | New Finding: Inadequate working space around the transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) shall be maintained. | Work is ongoing factory will be completed within 31.07.2022 | Nov 10 2021 | Comments from CH- On 07.07.2022 : No timeline extension has been accepted. Corrective action plan should be completed as per the given recommendation with immediate concern. On 18/12/2022: No progress is observed. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: Panel has unwanted openings. | Openings shall be sealed properly. | Completed | Nov 10 2021 | On 18/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: Wiring using flexible/rigid PVC pipe- this arrangement does not have any support for cables. | A cable ladder shall be used; if it is routed through outside wall, either the cable ladder shall be covered or a cable duct shall be used. | Completed | Nov 10 2021 | On 18/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: Panel/Distribution boxes are inaccessible or cannot be opened to perform any maintenance work. | Each electrical distribution board/panel shall be easily accessible. In case of height, its top shall not be higher than 2m from the base; and the door opening shall be at least 90 degrees. | Completed | Nov 10 2021 | On 18/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: Cumulative breaker size is greater than cable ampacity. MCCBs are not adjusted per load demand. | All the MCCBs shall be adjusted per cable current ampacity/load current; if adjustment is not possible, replacement will be the only way. For connecting multiple MCB use separate jumper bus bar within cable ampacity. For connecting multiple MCB use separate jumper bus bar within cable ampacity. | Completed | Nov 10 2021 | On 18/12/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Manually operated machines (may have chance to be touched by operator/user) have no earth connection. | Manually operated each machine (may have chance to be touched by user/operator) must have earth connection. Cable selection shall be made per CB response and circuit's power demand. |  | Oct 1 2023 | On 24/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Panel / Distribution boxes are inaccessible or cannot be opened to perform any maintenance work. | Each electrical distribution board/panel must be easily accessible. |  | Nov 1 2023 | On 24/01/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 63 | New Finding: Generator room has inadequate ventilation. | Adequate ventilation must be maintained in generator room. Cross/forced ventilation must be ensured. |  | Nov 1 2023 | On 24/01/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 64 | New Finding: Lightning Protection System (LPS) is not maintained properly. (Air terminal missing/Roof conductor missing/Class I used instead of Class II etc). | Factory shall redesign Lightning Protection System (LPS) as per standard and install accordingly (if required). Also periodic maintenance shall be done to maintain LPS. |  | Mar 6 2024 | RPO Comments: On 28-Feb-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. On 30/04/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 65 | New Finding: Uncovered/Perforated type cable tray/PVC pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. |  | Mar 6 2024 | RPO Comments: On 28-Feb-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. On 30/04/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 66 | New Finding: Equipments/ Load are not identified properly. | Identify every equipments as per accepted SLD to distinguish from others (Add point reference, L1-4, PS-1, PS-2, SM 1-10...etc). |  | Mar 6 2024 | RPO Comments: On 28-Feb-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. On 30/04/2025: Corrected. | 1 Month | Corrected

## Boiler
Date
10-May-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Needle Drop Ltd, 50, Chamdpara, Basin Road, Joydevpur national university, Joydevpur, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2022-02-28
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 12048 | Necessary technical documents (Except Maintenance manual, Water treatment report and maintenance logbook) are not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Factory Premises has available nesessary technical documents to verify the boiler design and operation parameters. | Nov 30 2025 | Comments on 13-Jan-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 2 | BB 8047 | Necessary technical documents (Except Water treatment report, maintenance logbook and construction drawing) are not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Boiler Registration No-8047 has been idle and facility management applied to Deputy Chief boiler inspector to shut down the said boiler, after that, Deputy Chief Boiler Inspector declared all official activities have been temporarily shut down. | Nov 30 2025 | Comments on 13-Jan-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 3 | BB 8047 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | Boiler Registration No-8047 has been idle and facility management applied to Deputy Chief boiler inspector to shut down the said boiler, after that, Deputy Chief Boiler Inspector declared all official activities have been temporarily shut down. | Nov 30 2025 | Comments on 13-Jan-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 4 | BB 12048 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | Facility Management has installed emergency stop push switch near the entrance outside of the boiler room and on the boiler control panel. | Nov 30 2025 | Comments on 13-Jan-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 12048 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Facility Management has been marked Low Low water level on water level gauge glass system. | Nov 30 2025 | Comments on 13-Jan-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 8047 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Boiler Registration No-8047 has been idle and facility management applied to Deputy Chief boiler inspector to shut down the said boiler, after that, Deputy Chief Boiler Inspector declared all official activities have been temporarily shut down. | Nov 30 2025 | Comments on 13-Jan-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 7 | BB 12048 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | Facility management has been directed the Boiler Safety Valve outlet line to outside of the boiler room. | Nov 30 2025 | Comments on 13-Jan-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 14578 | Boiler (Horizontal Vessel) Safety Valve outlet line was not directed outside of the boiler room. | Boiler (Horizontal Vessel) Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | Facility management has been directed the Boiler (Horizontal Vessel) Safety Valve outlet line to outside of the boiler room. | Nov 30 2025 | Comments on 13-Jan-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 14578 | Necessary technical documents (Except Maintenance manual, Water treatment report and maintenance logbook) are not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Factory Premises has available nesessary technical documents to verify the boiler design and operation parameters. | Nov 30 2025 | Comments on 13-Jan-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 10 | BB 14578 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Facility Management has been marked Low Low water level on water level gauge glass system. | Nov 30 2025 | Comments on 13-Jan-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 14578 | Boiler body was found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | Facility management has been insulation properly the boiler body. | Nov 30 2025 | Comments on 13-Jan-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 12 | BB 12048 | Boiler body was found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | Facility management has been insulation properly the boiler body. | Nov 30 2025 | Comments on 13-Jan-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 13 | BB 12048 | The inside of the boiler was found corroded due to inadequate water treatment. | Feed water must be externally or internally treated. The boiler operator should blow down regularly as per the manufacturer’s recommendation. Rapid boiling should be avoided. Shell and end plate thicknesses must be within the allowable limit specified by the manufacturer. | As per Manufacturers instruction/advice we are doing softener wash inside the boiler and have taken preventive measure for corrosion by using the Dugurd 24 chemical. | Nov 30 2025 | Comments on 13-Jan-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification