## Structural
Date
08-Apr-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Next Export Zone Ltd. , 105/4, Adaboi, Peara Bagan, Joydebpur, Gazipur, Bangladesh, Gazipur, Dhaka
Date of Inspection |  | 2020-02-24
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Undocumented water tanks and non-engineered supporting structure on the roof. (Main Building) | Building Engineer is required to relocate the existing water tanks as per accepted load plan. Also, survey the upporting structure and take necessary remedial actions. | Non-engineered structure is already demolished. Picture evidence for your easy reference. | May 17 2020 | On 29-Nov-2021:This issue is required to be covered under Detailed Engineering Assessment(DEA). Factory submitted DEA to RSC which was accepted by RSC on 21 October 2021. Retrofitting work was required for grade beams considering vertical extension. During inspection, no vertical extension was observed. Currently the building is 5 storied. During verification, discrepancy was found in beam layout. Stair landing beams were shown in drawing(two stairs), but were not found on site. Floor beam was missing in grid A(between grid 1&2). Some undocumented steel beams were found connecting grid 1-2(between grid A-C). Five nos.500 L and one 5000L plastic water tanks was found on roof floor which was not shown in drawing. Factory is required to update as-built drawings and FEM and submit revised DEA within 2 weeks after receiving this report. On 13-Nov-2022: Factory submitted the revised DEA and the DEA was re-accepted by RSC on 31-Jul-2022. During inspection accepted drawings matched with as-built condition. Roof water tanks were placed as per accepted load plan. On 11-Oct-2023: Corrected previously. water tank location matched with accepted drawing. On 15-Oct-2025: Previously corrected. | Within 6 week | Corrected
Initial Inspection |  | 2 | Mismatches in the design report and software analysis file (Main Building) | The building engineer to update the engineering assessment (structural design) report including the software analysis file and submit to Accord for further review. | Already submitted the drawing to RSC. | May 17 2020 | On 29-Nov-2021: This issue is required to be covered under Detailed Engineering Assessment(DEA). Factory submitted DEA to RSC which was accepted by RSC on 21 October 2021. During verification, some discrepancy was found. Factory is required to update as-built drawings and FEM and submit revised DEA within 2 weeks after receiving this report. On 13-Nov-2022: Factory submitted the revised DEA and the DEA was re-accepted by RSC on 31-Jul-2022. During inspection accepted drawings matched with as-built condition. On 11-Oct-2023: Corrected previously. On 15-Oct-2025: Previously corrected. | Within 6 week | Corrected
Initial Inspection |  | 3 | Mismatches in the design report and software analysis file (Main Building) | Update and active manage the floor loading plans based on the column and floor capacity of the building. | Already submitted the drawing to RSC. | May 17 2020 | On 29-Nov-2021: No load plan was posted. Loading was found within 63 psf. This issue is required to be covered under Detailed Engineering Assessment(DEA). Factory submitted DEA to RSC which was accepted by RSC on 21 October 2021. During verification, some discrepancy was found. Factory is required to update as-built drawings and FEM and submit revised DEA within 2 weeks after receiving this report. On 13-Nov-2022: Accepted load plan(63 psf) was posted. Loading was found below allowable limit. Retrofitting work was completed as per re-accepted DEA. On 11-Oct-2023: Corrected previously. Loading was found within accepted load plan (63 psf). On 15-Oct-2025: Previously corrected. | Within 6 week | Corrected
Initial Inspection |  | 4 | Mismatches in the design report and software analysis file (Main Building) | Complete remedial works arising from engineering assessment | Already submitted the drawing to RSC. | Oct 5 2020 | On 29-Nov-2021: This issue is required to be covered under Detailed Engineering Assessment(DEA). Factory submitted DEA to RSC which was accepted by RSC on 21 October 2021. As per accepted DEA, factory is required to carry out retrofitting work for grade beams. Retrofitting work was not started till inspection date. During verification, some discrepancy was found. Factory is required to update as-built drawings and FEM and submit revised DEA within 2 weeks after receiving this report. Factory will carry out remedial works as per accepted DEA. On 13-Nov-2022: Factory submitted the revised DEA and the DEA was re-accepted by RSC on 31-Jul-2022. As per re-accepted DEA, retrofitting work was completed. Retrofitting completion certificate and material test report were available. On 11-Oct-2023: Corrected previously. On 15-Oct-2025: Previously corrected. | within 6-months | Corrected
Initial Inspection |  | 5 | Mismatches in the design report and software analysis file (Main Building) | Continue to implement load plan. | Already submitted the drawing to RSC. | Oct 5 2020 | On 29-Nov-2021: No load plan was posted. Loading was found within 63 psf. This issue is required to be covered under Detailed Engineering Assessment(DEA). Factory submitted DEA to RSC which was accepted by RSC on 21 October 2021. During verification, some discrepancy was found. Factory is required to update as-built drawings and FEM and submit revised DEA within 2 weeks after receiving this report. On 13-Nov-2022: Accepted load plan(63 psf) was posted. Loading was found below allowable limit. Retrofitting work was completed as per re-accepted DEA. Retrofitting completion certificate and material test report were available. On 11-Oct-2023: Corrected previously. Loading was found within accepted load plan (63 psf). On 15-Oct-2025: Previously corrected. | within 6-months | Corrected
Initial Inspection |  | 6 | Non-engineered shed at roof (Main Building) | Remove or demolish the temporary shed. Otherwise, replace the existing shed with an engineered structure. | Non-engineered structure is already demolished.Picture evidence for your easy reference. | May 17 2020 | On 29-Nov-2021: Factory demolished the rooftop steel shed. On 13-Nov-2022: Corrected in previous follow-up inspection. Rooftop steel shed was demolished. On 11-Oct-2023: Corrected previously. Rooftop steel shed was found demolished. On 15-Oct-2025: Previously corrected. | Within 6 week | Corrected
Initial Inspection |  | 7 | Lack of as-built documents (Ancillary Structures) | The building engineer to survey the structure and produce asbuilt drawings with complete structural information. | Already submitted the drawing to RSC. | May 17 2020 | On 29-Nov-2021: Factory did not submit as-built drawings of the ancillary structures. Factory is required to submit the as-built drawings within 2 weeks after receiving this report. On 13-Nov-2022: As-built drawing for boiler& substation was re-accepted by RSC on 31-Jul-2022. During inspection as-built drawing matched with as-built condition. On 11-Oct-2023: Corrected previously. As-built drawing matched with as-built condition. On 15-Oct-2025: Previously corrected. | Within 6 week | Corrected
Initial Inspection |  | 8 | Non-engineered connection in the Medical & Childcare shed | Building engineer to check the connections and capacity of the lightweight roof structure against lateral loading. | Non-engieered structure is already demolished.Picture evidence for your easy reference. | May 17 2020 | On 29-Nov-2021: Factory demolished the Medical & Childcare shed. On 13-Nov-2022: Corrected in previous follow-up inspection. Medical & Childcare shed were demolished. On 11-Oct-2023: Corrected previously. On 15-Oct-2025: Previously corrected. | Within 6 week | Corrected
Initial Inspection |  | 9 | Non-engineered connection in the Medical & Childcare shed | Carry out remedial works resulting from engineering | Non-engieered Medical & Child care is already demolished.Picture evidence for your easy reference. | Oct 5 2020 | On 29-Nov-2021: Factory demolished the Medical & Childcare shed. On 13-Nov-2022: Corrected in previous follow-up inspection. Medical & Childcare shed were demolished. On 11-Oct-2023: Corrected previously. On 15-Oct-2025: Previously corrected. | within 6-months | Corrected
Follow Up Inspection |  | 10 | New Findings-1: Undocumented Masonry structure (Security room). | Produce As-built drawings and submit to RSC for review. | Done | Nov 28 2023 | On 11-Oct-2023: An undocumented masonry structure was found during inspection. Factory is required to produce as-built drawings and submit to RSC for review. On 15-Oct-2025: As-built drawing was accepted by RSC on 14 Nov 2024. During inspection as-built drawing was found satisfactory with onsite condition. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 11 | New Findings-2: Undocumented separate RCC stair with steel shed besides main building | Produce as-built drawings for RCC stair and check the lateral stability of the steel shed as a part of EA and submit to the RSC for review. | Done | Nov 28 2023 | On 11-Oct-2023: During inspection, a separate RCC stair was found constructed up to the half of ground floor of main building with a steel shed (not connected to the stair) as a roof to the stair. Factory engineer is required to produce as-built drawings for RCC stair and check the lateral stability of the steel shed as a part of EA and submit to the RSC for review. On 15-Oct-2025: The as-built drawing of the RCC stair and the declaration letter for demolition of the steel shed over the RCC stair were accepted by RSC on 14 November 2024. The as-built drawing of the RCC stair was found satisfactory with onsite conditions. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 12 | New Findings-3: Undocumented separate RCC stair with steel shed besides main building | complete remedial works after getting acceptance from RSC | Done | Apr 17 2024 | On 11-Oct-2023: Factory is required to do the remedial works after getting acceptance from RSC. On 15-Oct-2025: As per demolishing plan, the factory was required to remove the steel shed by 02 December 2024. During the inspection, the shed was found demolished. | (within 6 months) | Corrected
Follow Up Inspection |  | 13 | New Findings-4: Lack of design documents, material test report, load plan and discrepancies in as-built drawing Building 2 (2-storied (G+1), total area 13000 sft) | The Building Engineer is required to update as-built drawings, carry out Detailed Engineering Assessment (DEA) following BNBC 2020, and s to RSC for review | In Progress | Dec 4 2025 | RPO Comments: On 08/04/2026 - The design documents (Structural EA) are pending to be submitted to RSC. On 15-Oct-2025: During the inspection, a new structure named Building 2, located adjacent to the Main Building, was identified. Construction of this building commenced in September 2022. Building 2 and the Main Building are not structurally connected but are architecturally connected, sharing common floor areas. Currently, the factory occupies only the ground floor, while finishing work on the 1st floor is in progress. Construction drawings were not available; only as-built drawings were provided during the inspection. Several discrepancies were noted, including mismatches in grid dimensions and beam sizes, as well as missing details such as cantilever slab and beam dimensions and shear wall thickness. The Building Engineer is required to update and submit the revised as-built drawings, and Detailed Engineering Assessment (DEA) to RSC for review. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 14 | New Findings-5: Lack of design documents, material test report, load plan and discrepancies in as-built drawing Building 2 (2-storied (G+1), total area 13000 sft) | Verify in situ concrete strength by taking 100 mm diameter concrete cores from lower tier of the structural members (4 nos from Column, 4 nos from Beam-Slab) | In Progress | Dec 4 2025 | RPO Comments: On 08/04/2026 - The design documents (Structural EA) are pending to be submitted to RSC. On 15-Oct-2025: During inspection, no test report was available. The factory is required to verify in situ concrete strength by taking 100 mm diameter concrete cores from lower tier of the structural members (4 nos from Column, 4 nos from Beam-Slab). | (within 6 weeks) | In Progress
Follow Up Inspection |  | 15 | New Findings-6: Lack of design documents, material test report, load plan and discrepancies in as-built drawing Building 2 (2-storied (G+1), total area 13000 sft) | Prepare load plan as per structural capacity and BNBC requirement and implement load management plan | In Progress | Dec 4 2025 | RPO Comments: On 08/04/2026 - The design documents (Structural EA) are pending to be submitted to RSC. On 15-Oct-2025: During the inspection, load plan was not found. The Building Engineer is required to prepare a load plan considering the structural capacity and BNBC requirements, post the load plan on each floor, and clearly indicate the storage height and designated storage areas (if any). | (within 6 weeks) | In Progress
Follow Up Inspection |  | 16 | New Findings-7: Lack of design documents, material test report, load plan and discrepancies in as-built drawing Building 2 (2-storied (G+1), total area 13000 sft) | Carry out the required remedial work where required. | In Progress | Apr 26 2026 | RPO Comments: On 08/04/2026 - The design documents (Structural EA) are pending to be submitted to RSC. On 15-Oct-2025: After getting acceptance of DEA from RSC, the building engineer is required to carry out remedial works where required. | (within 6 months) | In Progress
Follow Up Inspection |  | 17 | New Findings-8: Column stress exceeds normal design limit considering possible vertical extension (7 storied) Building 2 | Prior to any vertical extension, the Building Engineer is required to complete a Detailed Engineering Assessment (DEA) for the proposed building and implement any remedial works, if required. | In Progress | Dec 4 2025 | RPO Comments: On 08/04/2026 - The design documents (Structural EA) are pending to be submitted to RSC. On 15-Oct-2025: As stated by the factory representative, the building was designed for seven stories. However, considering the minimum concrete design strength, some columns were found to be overstressed. Prior to any vertical extension, the Building Engineer is required to carry out a Detailed Engineering Assessment (DEA) for the proposed building and implement remedial works, if required. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 18 | New Findings-9: Building 2 is rigidly attached to the adjacent Main Building | A clear gap is required to be provided with an expansion joint, and the gap is to be filled with appropriate compressible materials as per the engineer’s recommendation. | In Progress | Dec 4 2025 | RPO Comments: On 08/04/2026 - The design documents (Structural EA) are pending to be submitted to RSC. On 15-Oct-2025: Building 2 is architecturally connected to the adjacent Main Building, sharing the same floor area, with no visible expansion gap observed between the two structures. A clear expansion gap shall be provided in accordance with BNBC requirements and filled with appropriate compressible material as recommended by the Building Engineer. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 19 | New Findings-10: Lack of design documents Boiler Room 2 (single storied, total area 2450 sft) | The Building Engineer is required to prepare a design report following BNBC 2020 | In Progress | Dec 4 2025 | RPO Comments: On 08/04/2026 - The design documents (Structural EA) are pending to be submitted to RSC. On 15-Oct-2025: During the inspection, a new structure named Boiler Room 2 was identified. It was constructed between September and November 2023. Credible as-built drawings were available during the inspection but design report was not available. The Building Engineer is required to submit design report to RSC for review, and implement any remedial works as recommended in the design report. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 20 | New Findings-11: Lack of permit drawing from the local authority (Building 2, Boiler Room 2) | Obtain building permit from the local authority | In Progress | Apr 26 2026 | RPO Comments: On 08/04/2026 - The design documents (Structural EA) are pending to be submitted to RSC. On 15-Oct-2025: Building permits were not available for this structure during the inspection. The building engineer is required to obtain building permit from the local authority. | (within 6 months) | In Progress

## Fire
Date
08-Apr-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Next Export Zone Ltd. , 105/4, Adaboi, Peara Bagan, Joydebpur, Gazipur, Bangladesh, Gazipur, Dhaka
Date of Inspection |  | 2020-02-24
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The exit stairs are not separated from work areas and other spaces on each floor by fire rated construction. Fire rated door was installed but were nonfunctional. | The exit stair enclosure shall be provided with a minimum 2-hr. fire resistant construction with minimum 1.5 hr. fire rated door and seal all penetrations and openings by 2 hr.fire rated fire rated barrier construction. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | Corrected | Jul 5 2020 | RPO Comments: On 08/04/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 11/10/2023: Most of the fire door was found functional during inspection. Fire door for ground floor stair-1 has been removed. Exit stair modification work is on going. | 3 month | Pending Verification
Initial Inspection |  | 2 | Unsealed penetrations and openings are located in the fire-rated floor/ceiling assemblies. Location: Electric Riser on every floor. | Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation at least by 2-hr. The used sealer shall be 3rd party certified and installation shall be as per manufacturer's datasheet. | Corrected | May 5 2020 | RPO Comments: On 08/04/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 11/10/2023: Factory has sealed the penetration with metal sheet which is not accepatable. Moreover, penetration through pvc toilet pipe was found. Factory shall seal the penetrations with fire rated sealer materials. | 1 month | Pending Verification
Initial Inspection |  | 3 | Areas used for combustible storage open to the factory are not separated by fire rated construction. Location: Ground floor of the building. | Separate the dedicated storage rooms by minimum 1-hr fire-rated construction. Provide 0.75 hr. fire rated door and seal all penetrations and openings by 1 hr. fire rated fire rated barrier construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.45m (8ft.) and maximum area of 23m2 (250 ft2) - If sprinkler protected: maximum height of 3.66m (12ft.) and maximum area of 93m2 (305ft2). Separate areas of unenclosed combustible storage by a minimum clear distance of 3m (10ft.). | Work completed. | Jul 5 2020 | On 11/10/2023: Corrected. In process storage was found within limit during inspection. | 3 month | Corrected
Initial Inspection |  | 4 | North-East stair discharge inside of building. | Ensure direct discharge from stair or provide 2-hr fire rated passageway for safe evacuation. | Corrected | Jul 5 2020 | RPO Comments: On 08/04/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 11/10/2023: Factory has started the modification work but not completed yet for stair-1 & 2. | 3 month | Pending Verification
Initial Inspection |  | 5 | Parapet height measured 28 '' in some portions. | Extend the parapet to maintain minimum 42 inch in height. | Work completed as per standard. | Jul 5 2020 | On 11/10/2023: Corrected. | 3 month | Corrected
Initial Inspection |  | 6 | Inspection, testing and maintenance for the emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | Corrected. Picture evidence for your further reference. | May 5 2020 | On 11/10/2023: Corrected. | 1 month. | Corrected
Initial Inspection |  | 7 | Headroom in the passageway of NorthEast stair measured less than 6 ft 8 ich. | Ensure minimum headroom 6ft 8 inch or re-route the egress way to avoid the critical path. | Corrected | May 5 2020 | RPO Comments: On 08/04/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 11/10/2023: Stair modification work is on going. | 1 month | Pending Verification
Initial Inspection |  | 8 | Handrails are not provided on both sides for any of the exit stair on all floors. | Provide handrails on both sides of the exit stair. New handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in.) | Corrected. Picture evidence for your further reference. | May 5 2020 | On 11/10/2023: Corrected. | 3 month | Corrected
Initial Inspection |  | 9 | Fire rated door obstructed the landing of stairs. | Re-arrange the door installation to avoid obstruction. | Completed | Oct 5 2020 | Corrective action plan should be completed as per Report’s action plan within the agreed timeline. Comments from RCH: On11-Jan-2023: Factory asking the final time line 5th Feb -2023. Time extension is not accepted. The corrective action plan should be completed as per RSC's required remediation or safety findings with immediate concern. On 11/10/2023: Corrected. | 1 month | Corrected
Initial Inspection |  | 10 | The addressable fire detection and alarm system is installed for the building but the system was not functional during inspection. However, the compliance level of the system shall be verified as per relevant Standard. | Submit the Fire Detection and Alarm system design to ACCORD for review and modify the system as per the recommendation. The equipment shall be listed and 3rd party certified. The installation shall be as per NFPA -72. | Fire detection system is already installed. Drawing is reviewed on month of March,2026. We will submit as built drawing asap. Final completion date 30th June, 2026 | Nov 30 2020 | Comments from RPO: On 08/04/2026 - The submitted Proposed FADS system drawings (hard copy) have been reviewed and accepted. The factory is responsible to ensure the installation of the system as per the design reviewed by the RSC and in accordance with relevant NFPA sections by 9 May 2026. Corrective action plan should be completed as per Report’s action plan within the agreed timeline. On 11/10/2023: Fire Alarm & Detection System drawing has been reviewed from RSC. Reportedly, installation has been completed. Factory shall apply for T&C. | Design submission within 1 month and installation modification within 4 months | In Progress
Initial Inspection |  | 11 | Inspection, testing and maintenance (ITM) for the fire detection and alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire detection and alarm system and keep written records on-site, in accordance with NFPA 72. | Fire detection system is already installed. Drawing is reviewed on month of March,2026. We will submit as built drawing asap. Final completion date 30th July, 2026 | Dec 30 2020 | Comments from RPO: On 08/04/2026 - The submitted Proposed FADS system drawings (hard copy) have been reviewed and accepted. The factory is responsible to ensure the installation of the system as per the design reviewed by the RSC and in accordance with relevant NFPA sections by 9 May 2026. Corrective action plan should be completed as per Report’s action plan within the agreed timeline. On 11/10/2023: It is an integrated part of fire alarm & detection system. | Within 01 month (After complete installation) | In Progress
Initial Inspection |  | 12 | The highest occupied floor of existing building is more than 10 m (33 ft.) above/ below grade but standpipe system is not installed in the building. | Provide class-III standpipe system (both a 40 mm connection with attached hose and a 65 mm connection) throughout the building in accordance with NFPA 14, 20, 22 and 24. | Fire Protection system is already installed. Drawing will be submitted 22nd april, 2026. For factory's expansion- the drawing is reviewed several times. We will submit as built drawing asap. Final completion date 5th July, 2026 | May 5 2021 | Comments from RPO: On 08/04/2026 - The revised soft copy SUPS have been submitted. They are requested to submit the printed/hard copies of the initial designs according to the electronic/soft copies to the RSC on 22 Apr 2026. Corrective action plan should be completed as per Report’s action plan within the agreed timeline. On 11/10/2023: Fire Protection System (Standpipe & Pump)drawing has been reviewed from RSC. Reportedly, L/C has been opened for fire pump. | Design within 4 months and installation within 9 months | In Progress
Initial Inspection |  | 13 | Inspection, testing and maintenance (ITM) of the fire pump is not in accordance with NFPA 25. | Inspect, test and maintain the fire pump and keep written records on-side, in accordance with NFPA 25. | Fire Protection system is already installed. Drawing will be submitted 22nd april, 2026. For factory's expansion- the drawing is reviewed several times. We will submit as built drawing asap. Final completion date 5th August 2026 | Jun 5 2021 | Comments from RPO: On 08/04/2026 - The revised soft copy SUPS have been submitted. They are requested to submit the printed/hard copies of the initial designs according to the electronic/soft copies to the RSC on 22 Apr 2026. Corrective action plan should be completed as per Report’s action plan within the agreed timeline. On 11/10/2023: It is an integrated part of fire protection system (Pump). | 01 month (After complete installation) | In Progress
Initial Inspection |  | 14 | Inspection, testing and maintenance (ITM) of the standpipe system is not in accordance with NFPA 25. | Inspect, test and maintain the standpipe system and keep written records on-side, in accordance with NFPA 25. | Fire Protection system is already installed. Drawing will be submitted 22nd april, 2026. For factory's expansion- the drawing is reviewed several times. We will submit as built drawing asap. Final completion date 5th October 2026. | Aug 5 2021 | Comments from RPO: On 08/04/2026 - The revised soft copy SUPS have been submitted. They are requested to submit the printed/hard copies of the initial designs according to the electronic/soft copies to the RSC on 22 Apr 2026. On 11/10/2023: It is an integrated part of fire protection system (Standpipe). | 03 months (After complete installation) | In Progress
Initial Inspection |  | 15 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10. | Corrected. Picture evidence for your further reference. | May 5 2020 | On 11/10/2023: Corrected. | 1 month | Corrected

## Electrical
Date
08-Apr-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Next Export Zone Ltd. , 105/4, Adaboi, Peara Bagan, Joydebpur, Gazipur, Bangladesh, Gazipur, Dhaka
Date of Inspection |  | 2020-02-24
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Electrical Single Line Diagram (SLD) is unavailable in the factory. | As built Electrical SLD must be prepared; it must have factory's whole electrical installation information. | Work Completed as Per Standard. | Jun 5 2020 | RPO Comments: On 21/04/2025 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 11/10/2023: Not Corrected. Factory got acceptance from RSC on 10 Nov 2022. Significant changes of the electrical system is observed from accepted SLD. Factory needs to re-submit the SLD to RSC for review. On 14/02/2024: Not corrected. Factory resubmitted SLD to RSC. SLD is now under review. On 26/05/2025: Corrected. The factory received acceptance on SLD on 25 Feb 2024 and implemented it onsite. | 2 MONTHS | Corrected
Initial Inspection |  | 2 | Lightning Protection System (LPS) and drawing is available but it is not covered for the whole factory. | Factory has to design Lightning Protection System (LPS) for the whole factory (where the Risk index is more than 40). Once a LPS is designed properly, installation must be done accordingly asap. | Work Completed as Per Standard. | Jul 5 2020 | On 11/10/2023: Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 3 | Electric safety training program has initiated but has no influence in the factory. | Electrical safety training and awareness program for the electrical personnel must be initiated. It is a periodic task which factory has to continue to improve the overall electrical safety situation for the staffs. | Work Completed as Per Standard. | May 5 2020 | On 11/10/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 4 | No working separation between LT ( Low Tension) panel/s and HT (High Tension) unit/s (Transformer, HT switchgear). | A working separation between LT and HT must be ensured. A brick wall will do it; and adequate working clearance (1.07m) and ventilation must be ensured. | Work Completed as Per Standard. | Jun 5 2020 | On 11/10/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 5 | Inadequate working space around the generator for performing maintenance work. | Minimum working space (1.07m) around the generators (and related electrical installations) must be maintained. | Work Completed as Per Standard. | Jul 5 2020 | On 11/10/2023: Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 6 | Cables are laid on floor haphazardly. | Power cables have to be guided and routed properly through cable trench. A cable tray shall be installed in the trench to ensure proper support and dressing for cables. | Work Completed as Per Standard. | Jun 5 2020 | On 11/10/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 7 | Lead acid battery terminals must be covered /capped and rust must be checked and cleaned. | Lead acid battery terminals must be covered/capped and rust must be checked and cleaned. | Work Completed as Per Standard. | May 5 2020 | On 11/10/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 8 | Distribution Board's bottom is left open (typical issue). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. | Work Completed as Per Standard. | May 5 2020 | On 11/10/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 9 | Earth pits are not identifiable. | Each earth pit shall be properly identifiable and marked for periodic maintenance. | Work Completed as Per Standard. | May 5 2020 | On 11/10/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 10 | Distribution boards have no clear identification markings. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. | Work Completed as Per Standard. | May 5 2020 | On 11/10/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 11 | Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ Busbar. | Each electrical circuit must be terminated at single MCB/MCCB/Busbar terminals. | Work Completed as Per Standard. | Jun 5 2020 | On 11/10/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 12 | Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. | Work Completed as Per Standard. | May 5 2020 | On 11/10/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 13 | No LOTO (Lock-Out-Tag-Out) policy is introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. | Work Completed as Per Standard. | May 5 2020 | On 11/10/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 14 | Unprotected cables terminated at sockets and plugs. | Proper protection must be ensured for unprotected cables termination with socket and plug and ensure proper cable support. | Work Completed as Per Standard. | May 5 2020 | On 11/10/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 15 | Manually operated machines/tools (may have chance to be touched by operator/user) have no earth connection. | Manually operated each machine (may have chance to be touched by user/operator) must have earth connection. Cable selection shall be made per CB response and circuit's power demand. | Work Completed as Per Standard. | May 5 2020 | On 11/10/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 16 | Excess cables coiled and kept unsupported at the back of panel. | Unsupported/unprotected power cables must be supported/protected by cable tray/ladders (If it is HT cable, rearrangement shall be made rather than trimming). | Work Completed as Per Standard. | May 5 2020 | On 11/10/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 17 | Electrical rotatory device/s has(ve) been installed unsafely. | Adequate and proper safety measures must be taken for all the rotary type installation. | Work Completed as Per Standard. | May 5 2020 | On 11/10/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 18 | Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Work Completed as Per Standard. | May 5 2020 | On 11/10/2023: Corrected. | 1 MONTH | Corrected
Follow Up Inspection |  | 19 | New Finding: Transformer Oil Test (dielectric strength test) report is unavailable. | Transformer oil test (dielectric strength test for oil) shall be done once in a year. | Work Completed as Per Standard. | Nov 26 2023 | RPO Comments: On 21/04/2025 - The factory management reported the remediation completion. This item will be verified in the next inspection.. On 14/02/2024: Not corrected. Oil test report found but dielectric breakdown test result is not satisfactory. Factory shall centrifuge or change the oil. On 26/05/2025: Corrected. The factory has replaced the transformer oil, and the latest test results indicate that the oil quality is satisfactory. | 1 MONTH | Corrected
Follow Up Inspection |  | 20 | New Finding: Hot spots have been observed at one points. (above 40ºC of ambient). | Hot spots must be eliminated from entire electrical system. | Work Completed as Per Standard. | Feb 29 2024 | RPO Comments: On 21/04/2025 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 26/05/2025: Corrected. | 1 Week | Corrected

## Boiler
Date
08-Apr-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Next Export Zone Ltd. , 105/4, Adaboi, Peara Bagan, Joydebpur, Gazipur, Bangladesh, Gazipur, Dhaka
Date of Inspection |  | 2022-08-31
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 12455 | Necessary technical documents (Except manufacturing drawing and maintenance logbook) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Documentation work is 50 % complete and remaining work is in progress, approximate finished time 15th Oct'24 | Oct 15 2024 | Comments On 9-Sep-2024: The remediation work shall be done following provided guideline and applicable standards within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 2 | BB 12455 | No emergency stop push switch was available near the entrance outside of the boiler room. | An emergency stop push switch must be installed outside of the boiler room near the entrance door. | Completed | Oct 15 2024 | Comments On 9-Sep-2024: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 12455 | Boiler's initial registration certificate was not available on-site during the inspection. | Boiler registration certificate from the government authority which was provided after the installation shall be available on-site during the inspection. | Completed | Oct 15 2024 | Comments On 9-Sep-2024: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 12455 | Boiler Safety Valve outlet line is not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support & drainage system. | Completed | Sep 15 2024 | Comments On 9-Sep-2024: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 12455 | The boiler registration number plate was not found mounted on the boiler. | Boiler registration number plate shall be made available on the boiler according to the Bangladesh Boiler Act 2022. | Completed | Oct 15 2024 | Comments On 9-Sep-2024: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 12455 | Boiler body was found with improper insulation. | Proper insulation to expose parts of the boiler body and steam distribution pipelines should be provided. | Insulation work is 70 % complete and remaining work is in progress. Apprx Finishing timeline 15/09/24 | Sep 15 2024 | Comments On 9-Sep-2024: The remediation work shall be done following provided guideline and applicable standards within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 7 | BB 12455 | Induced draught fan rotor shaft and driving system was found open/unprotected in boiler room. | Mechanical guard shall be provided to feed pump rotating shaft/any rotating object. | Motor cover work is 50 % complete and remaining work is in progress. Apprx Finishing timeline 15/10/24 | Oct 15 2024 | Comments On 9-Sep-2024: The remediation work shall be done following provided guideline and applicable standards within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 8 | BB 12455 | The boiler manufacturer's nameplate was not available on the boiler. | The boiler manufacturer's nameplate shall be available on the boiler with accurate technical information and the boiler manufacturer's name in standard language. | Nameplates are ordered to be manufactured. Apprx Finishing timeline 15/09/24 | Sep 15 2024 | Comments On 9-Sep-2024: The remediation work shall be done following provided guideline and applicable standards within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 9 | BB 12455 | Direct groundwater was used as feed water for the boiler. | Boiler feed water shall be treated and shall meet the standard parameters. Boiler feed water quality shall be monitored and recorded regularly. | Completed | Oct 15 2024 | Comments On 9-Sep-2024: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 10496 | Necessary technical documents (Except manufacturing drawing and maintenance logbook) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | This boiler is closed | Oct 15 2024 | Comments On 9-Sep-2024: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 10496 | No emergency stop push switch was available near the entrance outside of the boiler room. | An emergency stop push switch must be installed outside of the boiler room near the entrance door. | This boiler is closed | Oct 15 2024 | Comments On 9-Sep-2024: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 12 | BB 10496 | Boiler's initial registration certificate was not available on-site during the inspection. | Boiler registration certificate from the government authority which was provided after the installation shall be available on-site during the inspection. | This boiler is closed | Oct 15 2024 | Comments On 9-Sep-2024: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 13 | BB 10496 | Boiler Safety Valve outlet line is not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support & drainage system. | This boiler is closed | Sep 15 2024 | Comments On 9-Sep-2024: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 14 | BB 10496 | Boiler body was found with improper insulation. | Proper insulation to expose parts of the boiler body and steam distribution pipelines should be provided. | This boiler is closed | Sep 15 2024 | Comments On 9-Sep-2024: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 15 | BB 10496 | The boiler manufacturer's nameplate was not available on the boiler. | The boiler manufacturer's nameplate shall be available on the boiler with accurate technical information and the boiler manufacturer's name in standard language. | This boiler is closed | Sep 15 2024 | Comments On 9-Sep-2024: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 16 | BB 10496 | Direct groundwater was used as feed water for the boiler. | Boiler feed water shall be treated and shall meet the standard parameters. Boiler feed water quality shall be monitored and recorded regularly. | This boiler is closed | Oct 15 2024 | Comments On 9-Sep-2024: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 17 | BB 12455 | The economizer was not equipped with a safety valve. | Economizers that can be isolated from a boiler allowing the economizer to become a fired pressure vessel, shall have a minimum of one pressure safety valve in a location recommended by the manufacturer or as close as practical to the economizer outlet. | The materials required to carry out this work have been purchased and Work is ongoing . Apprx Finishing timeline 15/09/24 | Sep 15 2024 | Comments On 9-Sep-2024: The remediation work shall be done following provided guideline and applicable standards within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 18 | BB 12455 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | The materials required to carry out this work have been purchased and Work is ongoing . Apprx Finishing timeline 15/09/24 | Sep 15 2024 | Comments On 9-Sep-2024: The remediation work shall be done following provided guideline and applicable standards within the committed timeline. | 1 MONTH | In Progress