## Structural
Date
15-Jun-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Renown Apparels Ltd., Bhatiary Link Road ( South Side ) Barodighir Par, Hathazary, Chattogram, Chattogram, Chittagong
Date of Inspection |  | 2014-08-20
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | High stresses to internal colums, factor of safety between 1.50 & 1.86 based on current loading. | Ensure that the slabs are not loaded above 2.0kPa(40psf). | We ensured slabs are not loaded above 2.0Kpa(40psf),moreove we engaged BV for Detailed Engineering Assessmentt ,Lod management Etc.They started work from 17th Nov.Attached their timeline. | Jan 11 2014 | On 7-Jun-2015: Loads were found satisfactory, But A load plan giving attributes to load type, loading area & height to be stacked to be developed, implemented & managed which was found missing. On 20/04/2016: Load was observed under 42 psf. On 18/10/2016: No overloading was seen. Corrected in previous. On 21/05/2017: Corrected in previous follow up. On 12/07/2018: Load plan has been prepared along with DEA report which was accepted by ACCORD. During inspection, loading was observed within the allowable load limit (42 psf) as per accepted load plan. Load plan was found posted in each floor. On 21-Sep-2021: This issue was corrected from previous inspection. Load plan has been prepared as part of DEA report which was accepted from ACCORD on 7-June-2016. During inspection, floor loading was found below accepted allowable load limit (42 psf). Load plan was found posted to each floor. On 15-Jun-2022: Corrected from previous follow up inspection. During inspection loading was found within the allowable load limit (42 psf). Load plan was found posted on each floor. On 07-Sep-2023: This issue has been corrected from previous inspection. Loading was found within the allowable load limit (42 psf) and load plan was found posted. On 10-Mar-2024: Corrected previously. During inspection, load plan was found posted on every floor and loading was found within the allowable limit of 42 psf for the typical floor area. On 27-Jul-2025: Corrected previously. During inspection, loading was found within the allowable limit of 42 psf for the typical floor area and load plan was found posted on every floor. On 06-Apr-2026: Previously corrected. | Immediately | Corrected
Initial Inspection |  | 2 | High stresses to internal colums, factor of safety between 1.50 & 1.86 based on current loading. | Carry out a Detailed Engineering Assessment on the columns, taking 100mm core samples where necessary to establish the strength. | Facility has already corrected in Accord Time line. | Jan 30 2015 | On 7-Jun-2015: DEA done, submitted to ACCORD, not yet presented. Some evidences of core cutting/rebar exposing were observed. Damege/Notches to be properly repaired. Also column core strength results(4 nos-in DEA f'c=2360 psi acc to ACI 562 but not showed any calculation, but while checked f'ceq was found 2007 psi) needs clarifications. On 20/04/2016: DEA was accepted by Accord on and cores were taken. On 18/10/2016: Factory got DEA acceptance from Accord. Corrected in previous. On 21/05/2017: Corrected in previous follow up. On 12/07/2018: This issue has been corrected from previous inspection. Cores were taken and covered in DEA. On 21-Sep-2021: This issue was corrected from previous inspection. Detailed Engineering Assessment (DEA) was accepted from ACCORD on 7-June-2016. On 15-Jun-2022: Corrected from previous follow up inspection. On 07-Sep-2023: This issue has been corrected from previous inspection. On 10-Mar-2024: Corrected previously. On 27-Jul-2025: Corrected previously. On 06-Apr-2026: Previously corrected. | 6 - weeks | Corrected
Initial Inspection |  | 3 | High stresses to internal colums, factor of safety between 1.50 & 1.86 based on current loading. | Carry out any recommendations highlighted in the Detailed Engineering Assessment. | Our DEA was approved on 06.07.2016 and we started retrofitting works from 15.08.2016. Accord Time was 31.12.2016.In this Time We have completed Most of columns and now doing beam retrofitting. But beam retrofitting takes more time than we expected. One beam takes 12to 15 days to complete. We now finished 11 beams out of 28 beams. So need more times to fully complete the retrofitting works. We will be grateful to you if you allow us time until end April to fully complete the retrofitting works. | Dec 31 2016 | On 7-Jun-2015: After reviewing DEA, ACCORD will advise whether to go with it or correct it & finally implement its recommendations after approving DEA. Till then it is advised to follow what is told in the preliminary report. On 20/04/2016: DEA was accepted by Accord on 28 December, 2015 and recommended retrofitting has not been started yet. On 18/10/2016: Retrofitting work was seen ongoing. Factory is required to complete the retrofitting work within 31 December 2016. On 21/05/2017: The remediation work was found ongoing. On 12/07/2018: This issue is covered in DEA. Factory has carried out DEA and got approval from ACCORD on 07-06-2016. As per the approved DEA, factory management has completed the retrofitting works. On 21-Sep-2021: This issue was corrected from previous inspection. On 15-Jun-2022: Corrected from previous follow up inspection. Factory got DEA acceptance on 7-Jun-2016 from ACCORD. Factory completed all the remediation works previously. On 07-Sep-2023: This issue has been corrected from previous inspection. On 10-Mar-2024: Corrected previously. Factory completed the remedial works as per accepted DEA. On 27-Jul-2025: Corrected previously. On 06-Apr-2026: Previously corrected. | 6 - months | Corrected
Initial Inspection |  | 4 | Shear cracking observed at beam - beam connections. | Carry out a Detailed Engineering Assessment on the beams, removing, plaster, to establish what load they can safely support. | DEA Approved by ACCORD dated-07.06.2016.We are inprocess to start retrofitting. | Jun 30 2016 | On 7-Jun-2015: Crackings were found to be the same state. Moreover some repairing recommendations were made in DEA recommendations and beam retrofitting was suggested too. On 20/04/2016: DEA was accepted by Accord on 28 December, 2015 and verified on 20-April-2016. According to DEA recommendation retrofitting is needed which have not been started yet. On 18/10/2016: Corrected in previous. On 21/05/2017: Corrected in previous follow up. On 12/07/2018: This issue has been corrected from previous inspection. Factory has carried out DEA and got approval from ACCORD on 07-06-2016. As per the approved DEA, factory management has completed the retrofitting works. On 21-Sep-2021: This issue was corrected from previous inspection. Detailed Engineering Assessment (DEA) was accepted from ACCORD on 7-June-2016. On 15-Jun-2022: Corrected from previous follow up inspection. On 07-Sep-2023: This issue has been corrected from previous inspection. On 10-Mar-2024: Corrected previously. On 27-Jul-2025: Corrected previously. On 06-Apr-2026: Previously corrected. | 6- weeks | Corrected
Initial Inspection |  | 5 | Shear cracking observed at beam - beam connections. | Carry out actions from the Detailed Engineering Assessment. | Our DEA was approved on 06.07.2016 and we started retrofitting works from 15.08.2016. Accord Time was 31.12.2016.In this Time We have completed Most of columns and now doing beam retrofitting. But beam retrofitting takes more time than we expected. One beam takes 12to 15 days to complete. We now finished 11 beams out of 28 beams. So need more times to fully complete the retrofitting works. We will be grateful to you if you allow us time until end April to fully complete the retrofitting works. | Dec 31 2016 | On 7-Jun-2015: Crackings were found to be the same state(unrepaired). Moreover some repairing recommendations were made in DEA recommendations and beam retrofitting was suggested too. On 20/04/2016: DEA was accepted by Accord on 28 December, 2015 and recommended retrofitting has not been started yet. On 18/10/2016: Retrofitting work was seen ongoing. Factory is required to complete the retrofitting work within 31 December 2016. On 21/05/2017: The remediation was found ongoing . The remediation is required to be completed immediately as soon as possible as deadline is crossed. On 12/07/2018: This issue is covered in DEA. Factory has carried out DEA and got approval from ACCORD on 07-06-2016. As per the approved DEA, factory management has completed the retrofitting works. On 21-Sep-2021: This issue was corrected from previous inspection. On 15-Jun-2022: Corrected from previous follow up inspection. Factory got DEA acceptance on 7-Jun-2016 from ACCORD. Factory completed all the remediation works previously. On 07-Sep-2023: This issue has been corrected from previous inspection. During the inspection, crack was not found at beam-beam connections. On 10-Mar-2024: Corrected previously. On 27-Jul-2025: Corretced previously. On 06-Apr-2026: Previously corrected. | 6-month | Corrected
Initial Inspection |  | 6 | Plinths have been constructed on the slab around wash room areas & cracks were observed in the beams below. | Carry out a Detailed Engineering Assessment to determine if the slab is adequate to support the higher dead load of the plinth. | DEA Approved by ACCORD dated-07.06.2016.We are inprocess to start retrofitting. | Jun 30 2016 | On 7-Jun-2015: The situation was found the same state and factory has not done any alterations/repair to beams. On 20/04/2016: DEA was accepted by Accord on 28 December, 2015 and verified on 20-April-2016 On 18/10/2016: Corrected in previous. On 21/05/2017: Corrected in previous follow up. On 12/07/2018: This issue is covered in DEA. Factory has carried out DEA and got approval from ACCORD on 07-06-2016. On 21-Sep-2021: This issue was corrected from previous inspection. Detailed Engineering Assessment (DEA) was accepted from ACCORD on 7-June-2016. On 15-Jun-2022: Corrected from previous follow up inspection. On 07-Sep-2023: This issue has been corrected from previous inspection. On 10-Mar-2024: Corrected previously. See item no. 13. On 27-Jul-2025: Corretced previously. On 06-Apr-2026: Previously corrected. | 6- weeks | Corrected
Initial Inspection |  | 7 | Plinths have been constructed on the slab around wash room areas & cracks were observed in the beams below. | Caryy out actions highlighted in the Detailed Engineering Assessment, renoving or lowering the heights of the plinths as required. | DEA Approved by ACCORD dated-07.06.2016.We are inprocess to start retrofitting. | Jun 30 2016 | On 7-Jun-2015: After reviewing DEA, ACCORD will advise whether to go with it or correct it & finally implement its recommendations after approving DEA. Till then it is advised to follow what is told in the preliminary report. On 20/04/2016: DEA was accepted by Accord on 28 December, 2015. On 18/10/2016: corrected in previous. On 21/05/2017: Corrected in previous follow up. On 12/07/2018: This issue is covered in DEA. Factory has carried out DEA and got approval from ACCORD on 07-06-2016. On 21-Sep-2021: This issue was corrected from previous inspection. On 15-Jun-2022: Corrected from previous follow up inspection. Factory got DEA acceptance on 7-Jun-2016 from ACCORD. Factory completed all the remediation works previously. On 07-Sep-2023: This issue has been corrected from previous inspection. During the inspection, crack was not found in the beams. On 10-Mar-2024: Corrected previously. See item no. 13. On 27-Jul-2025: Corrected previously. On 06-Apr-2026: Previously corrected. | 6- months | Corrected
Initial Inspection |  | 8 | There is no obvious stability system for the building. | Carry out Detailed Engineering Assessment on the building to verify that it is stable under lateral loading. | Completed and verified by Accord | Jun 30 2016 | On 7-Jun-2015: DEA was tried to be verified and as built drawings were matched(grid distances/column sizes, rebar nos-quick scan). Also some core cutting locations were verified. On 20/04/2016: DEA was accepted by Accord on 28 December, 2015 and verified on 20-April-2016. According to DEA recommendation retrofitting is needed which have not been started yet. On 18/10/2016: covered in DEA. Factory got DEA acceptance from Accord on 7 June 2016. On 21/05/2017: Corrected in previous follow up. On 12/07/2018: This issue is covered in DEA. Factory has carried out DEA and got approval from ACCORD on 07-06-2016. On 21-Sep-2021: This issue was corrected from previous inspection. Detailed Engineering Assessment (DEA) was accepted from ACCORD on 7-June-2016. On 15-Jun-2022: Corrected from previous follow up inspection. On 07-Sep-2023: This issue has been corrected from previous inspection. On 10-Mar-2024: Corrected previously. On 27-Jul-2025: Corrected previously. On 06-Apr-2026: Previously corrected. | 6- weeks | Corrected
Initial Inspection |  | 9 | There is no obvious stability system for the building. | Carry out all recommendations of the Detailed Engineering Assessment. | Our DEA was approved on 06.07.2016 and we started retrofitting works from 15.08.2016. Accord Time was 31.12.2016.In this Time We have completed Most of columns and now doing beam retrofitting. But beam retrofitting takes more time than we expected. One beam takes 12to 15 days to complete. We now finished 11 beams out of 28 beams. So need more times to fully complete the retrofitting works. We will be grateful to you if you allow us time until end April to fully complete the retrofitting works. | Dec 31 2016 | On 7-Jun-2015: Some recommendations including retrofitting of shear walls and new shear wall insertions were made in the DEA recommendation. After reviewing DEA, ACCORD will advise whether to go with it or correct it & finally implement its recommendations after approving DEA. Till then it is advised to follow what is told in the preliminary report. On 20/04/2016: DEA was accepted by Accord on 28 December, 2015 and recommended retrofitting has not been started yet. On 18/10/2016: Retrofitting work was seen ongoing. Factory is required to complete the retrofitting work within 31 December 2016. On 18/10/2016: Retrofitting work was seen ongoing. Factory is required to complete the retrofitting work within 31 December 2016. On 21/05/2017: The remediation was seen ongoing. It is required factory complete the remediation work within deadline. On 12/07/2018: This issue is covered in DEA. Factory has carried out DEA and got approval from ACCORD on 07-06-2016. As per the approved DEA, factory management has completed the retrofitting works. On 21-Sep-2021: This issue was corrected from previous inspection. On 15-Jun-2022: Corrected from previous follow up inspection. Factory got DEA acceptance on 7-Jun-2016 from ACCORD. Factory completed all the remediation works previously. On 07-Sep-2023: This issue has been corrected from previous inspection. On 10-Mar-2024: Corrected previously. Factory completed all the remedial works as per accepted DEA. On 27-Jul-2025: Corrected previously. On 06-Apr-2026: Previously corrected. | 6- months | Corrected
Initial Inspection |  | 10 | Loading plans exist for the structure, but are not displayed. | Ensure loading plans are displayed and actively managed at each level. | Facility has already corrected | Jul 30 2015 | On 7-Jun-2015: Loads were found satisfactory, But A load plan giving attributes to load type, loading area & height to be stacked to be developed, implemented & managed which was found missing. On 20/04/2016: Before retrofitting Load plan was posted and maintained. Load was under 20 psf.Factory shall maintain proposed load plan after completion of retrofitting works. On 18/10/2016: 20 psf load plan was seen maintained. Factory can implement final load plan after retrofitting is completed. On 21/05/2017: Safe Load plan was seen posted and also maintained. Final load plan can be posted after remediation is completed. On 12/07/2018: Load plan has been prepared along with DEA report which was accepted by ACCORD. During inspection, loading was observed within the allowable load limit (42 psf) as per accepted load plan. Load plan was found posted in each floor. On 21-Sep-2021: This issue was corrected from previous inspection. Load plan has been prepared as part of DEA report which was accepted from ACCORD on 7-June-2016. During inspection, floor loading was found below accepted allowable load limit (42 psf). Load plan was found posted to each floor. On 15-Jun-2022: Corrected from previous follow up inspection. During inspection loading was found within the allowable load limit (42 psf). Load plan was found posted on each floor. On 07-Sep-2023: This issue has been corrected from previous inspection. Loading was found within the allowable load limit (42 psf) and load plan was found posted. On 10-Mar-2024: Corrected previously. During inspection, load plan was found posted on every floor and loading was found within the allowable limit of 42 psf for the typical floor area. On 27-Jul-2025: Corrected previously. During inspection, loading was found within the allowable limit of 42 psf for the typical floor area and load plan was found posted on every floor. On 06-Apr-2026: Previously corrected. | 6 - weeks | Corrected
Initial Inspection |  | 11 | The 30,000 litre water tank on the roof is leaking or overflowing. | If the tank is to remain repair the tank appropriately, draining the tank if necessary to facilitate the repair. | Facility has already corrected | Jun 30 2015 | On 7-Jun-2015: Factory personnel(Mr. Shamsul Azam) informed that they are not using this tank anymore, instead they are using 3 plastic tanks. On 20/04/2016: Water tank has been repaired. On 18/10/2016: corrected in previous. On 21/05/2017: Corrected in previous follow up On 12/07/2018: This issue has been corrected from previous inspection. On 21-Sep-2021: This issue was corrected from previous inspection. During inspection, leakage was not found in the water tank. On 15-Jun-2022: Corrected from previous follow up inspection. Leakage was not found in the water tank. On 07-Sep-2023: This issue has been corrected from previous inspection. During inspection, leakage was not found in the water tank. On 10-Mar-2024: Corrected previously. During inspction, water tanks were found on roof as per accepted DEA. On 27-Jul-2025: Corrected previously. During inspection, leakage was not found in the water tank. On 06-Apr-2026: Previously corrected. | 6- months | Corrected
Initial Inspection |  | 12 | No waterproofing membrane to roof, ponding water on roof & distress due to water ingress | Cover the concrete roof with a suitable waterproofing membrane, e.g. waterproof screed. | Our DEA was approved on 06.07.2016 and we started retrofitting works from 15.08.2016. Accord Time was 31.12.2016.In this Time We have completed Most of columns and now doing beam retrofitting. But beam retrofitting takes more time than we expected. One beam takes 12to 15 days to complete. We now finished 11 beams out of 28 beams. So need more times to fully complete the retrofitting works. We will be grateful to you if you allow us time until end April to fully complete the retrofitting works. | Dec 31 2016 | On 7-Jun-2015: The rooftop was found the same without waterproofing and also poor water drainage was seen (waterclogging) On 20/04/2016: Not done yet. On 18/10/2016: No water proofing was seen done yet. Factory ins required to complete the all remediation work as per a qualified engineer. On 21/05/2017: Factory provided waterproofing agent at the roof top. No water accumulation was observed. On 12/07/2018: This issue has been corrected from previous inspection. During inspection no dampness was found on roof surface. Factory authority provided water proofing membrane on roof. On 21-Sep-2021: This issue was corrected from previous inspection. Factory provided water proofing layer on roof top and improved the drainage system. On 15-Jun-2022: Corrected in previous inspection. Factory authority provided water proofing membrane on rooftop. On 07-Sep-2023: This issue has been corrected from previous inspection. On 10-Mar-2024: Corrected previously. During inspection, water proofing membrane was found on roof and no water ponding was observed. On 27-Jul-2025: Corrected previously. During inspection, water proofing membrane was found on roof and no water ponding was observed. On 06-Apr-2026: Previously corrected. | 6- months | Corrected
Follow Up Inspection |  | 13 | New finding-01: Hairline cracks on beams of Factory Building. | Building engineer is required to survey the whole structure and repair the hairline cracks on beams. | Update 13 May'24,Facility assigned a required engineer and engineer diagnosis whole structure crack and authority is waiting for engineer report. It will complete within 31st May'24 Update 18.09.24 Facility assigned a required engineer and engineer diagnosis whole structure crack and authority is waiting for engineer report. It will complete within 31st Oct'24 Update 29.01.25, Our consultant engineer declared the crack as a non structural crack and On 21st Dec'24 We provided Crack Investigation Report to RSC & RSC authority will verify during next inspetion schedule. Update 20.04.25, Our consultant engineer declared the crack as a non structural crack and On 21st Dec'24 We provided Crack Investigation Report to RSC & RSC authority will verify during next inspetion schedule. Update 17.07.25, Our consultant engineer declared the crack as a non structural crack and On 21st Dec'24 We provided Crack Investigation Report to RSC & RSC authority will verify during next inspetion schedule. | Apr 21 2024 | On 10-Mar-2024: During inspection, hairline cracks were found on beams of Factory Building. Building engineer is required to survey the whole structure and repair the hairline cracks on beams. On 27-Jul-2025: Factory got acceptance of the crack investigation report from RSC on 30-April-2025. Factory has repaired all the hairline cracks on beams as per recommendation of the accepted crack investigation report. During inspection, no further cracks were found on the beams. On 06-Apr-2026: Previously corrected. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 14 | New finding-02: Water seeping through crack of basement floor slab of the Factory Building. | Factory is required to engage a qualified geotechnical engineer to check the reason of crack and water seepage considering buoyancy force due to soil and water pressure. The structural and geotechnical engineer is required to prepare an investigation report with necessary investigation procedure, findings, and suitable remedial actions. | Update 13 May'24,Facility assigned a required engineer and engineer is working to check the reason of water seepage and authority is waiting for engineer report. It will complete within 31st May'24. Update 18.09.24 acility assigned a required engineer and engineer is working to check the reason of water seepage and authority is waiting for engineer report. It will complete within 31st Oct'24 Update 31.01.25 we provided Report on basement slab crack& water leakage on 03rd Nov'24 to RSC & RSC verify report on 06th Jan'25 also facility provided report and drawing according to RSC suggestion on 13th January'25. Now facility waiting for RSC Comments. Update 20.04.25 we provided Report on basement slab crack& water leakage on 03rd Nov'24 to RSC & RSC verify report on 06th Jan'25 also facility provided report and drawing according to RSC suggestion on 13th January'25 and also send revised drawing on 08th April'25. Now facility waiting for RSC Comments. Update 03.06.25 we provided Report on basement slab crack& water leakage RSC authority received and Comments on 20th May'25 according to RSC suggestion facility will complete this work within31st July'25. Update 17.07.25 we provided Report on basement slab crack& water leakage RSC authority received and Comments on 20th May'25 according to RSC suggestion facility will complete this work within31st July'25. | Apr 21 2024 | On 10-Mar-2024: During inspection, water was found seeping through crack of basement floor slab of Factory Building. Factory is required to engage a qualified geotechnical engineer to check the reason of crack and water seepage considering buoyancy force due to soil and water pressure. The structural and geotechnical engineer is required to prepare an investigation report with necessary investigation procedure, findings, and suitable remedial actions. On 27-Jul-2025: Factory got acceptance of both the crack investigation report and the proposed basement slab design from RSC on 30-April-2025. On 06-Apr-2026: Previously corrected. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 15 | New finding-03: Water seeping through crack of basement floor slab of the Factory Building. | Carryout suggested remedial actions. | Already we have submitted proposed basement slab design to RSC. When we will get approval from RSC then we will start work. | Sep 10 2024 | On 10-Mar-2024: Any remediation work raised from the investigation report is required to be implemented after getting acceptance from RSC. On 27-Jul-2025: Factory got acceptance of both the crack investigation report and the proposed basement slab design from RSC on 30-April-2025. Factory is required to complete the proposed basement slab by 31-July-2025. Till the date of inspection. factory hasn't started the remedial works. On 06-Apr-2026: Factory received acceptance of both the crack investigation report and the proposed basement slab design from RSC on 30-April-2025. Factory has constructed the new basement slab on top of the previous basement slab. But during inspection, following discrepancies were found- 1. As per the accepted drawing, a 12-inch slab was propsed, whereas only a 4-inch slab was constructed on-site. 2. Two layers of reinforcement (top and bottom) were specified, but only one layer was provided. Additionally, anchorage/embedment of slab reinforcement into the pile cap could not be verified. Therefore, the building engineer is required to implement the remediation works as per the accepted remediation scheme of basement slab. Progress Status: 20% RPO Comments: On 15-Jun-2026 the propposed basement slab design are currently under RSC’s review. | (within 6 months) | In Progress

## Fire
Date
15-Jun-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Renown Apparels Ltd., Bhatiary Link Road ( South Side ) Barodighir Par, Hathazary, Chattogram, Chattogram, Chittagong
Date of Inspection |  | 2014-07-19
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The generator room is not separated by fire-rated construction that is openings, non-rated doors, penetrations on basement floor. | Separate the generator room by a minimum 2-hr fire-fated construction. Seal and/or protected all openings to maintain the required fire separations | Issue has been completed as per RSC standard and also verified by the Inspection team. | Jun 30 2016 | On 24/04/2016: It was same as it was 1st follow up visit. Final CAP Timeline: Expired. Committed Timeline: Within 30th June, 2016. On 18/10/2016: Civil related work is going on and fire rated door is not installed yet. Fire rated doors are in house. Separation work (civil work and fire door installation) will be completed after retrofitting work. On 21/05/2017: Civil work completed but fire door is not installed yet. On 17/09/2017: Corrected. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 2 | Rooms used for combustible storage are not separated by fire-rated construction on ground, 1st, 2nd and 3rd floors. | Provide dedicated storage rooms separated by minimum1-hr fire-rated construction. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Jun 30 2016 | On 24/04/2016: It was same as it was 1st follow up visit. Final CAP Timeline: Expired. Committed Timeline: Within 30th June, 2016. On 18/10/2016: Civil related work is going on and fire rated door is not installed yet. Fire rated doors are in house. Separation work (civil work and fire door installation) will be completed after retrofitting work. On 21/05/2017: Corrected. If fire doors are required to be held open for functional reasons, provide automatic- closing devices (magnetic door holder) tied to the FACP. On 17/09/2017: Corrected. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 3 | The exit stairs are not separated from work areas and other spaces on each floor by fire-rated construction. | provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Jun 30 2016 | On 24/04/2016: Factory management confirms that this issue will be completed within committed timeline. Final CAP Timeline: Expired. Committed Timeline: Fire rated door L/C open 10th May, 2016 and installation within 30th June, 2016. On 18/10/2016: Civil related work is going on and fire rated door is not installed yet. Fire rated doors are in house. Separation work (civil work and fire door installation) will be completed after retrofitting work. On 21/05/2017: Factory has installed fire rated door in both the exit stairs on all floors. Doors were held open during follow-up inspection. If fire doors are required to be held open for functional reasons, provide automatic- closing devices (magnetic door holder) tied to the FACP. On 17/09/2017: Corrected. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | Unsealed penetrations and openings are located in exit stair enclosures. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Jun 30 2016 | On 18/10/2016: Unsealed opening has found on the south-west exit stair at 1st floor. On 21/05/2017: Corrected. On 17/09/2017: Corrected. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 5 | Areas used for combustible storage are not separated by fire-rated construction on ground, 1st, 2nd and 3rd floors. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows:-Maximum height of 2.4m and maximum area of 23m2-if sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Jan 30 2015 | On 07/06/2015: Corrected. On 24/04/2016: Corrected. Factory management is maintaining arrangement as per recommendation. This issue was corrected in 1st follow up report. On 18/10/2016: Corrected. Non-compliant storage areas are not found during 3rd follow-up inspection. On 21/05/2017: Corrected. On 17/09/2017: Corrected as per site observations. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 6 | Egress doors/gates with locking features are provided at building exits, exit stairs, along egress routes and exit discharge on all floors. All gates/doors were open and unlocked during inspection. | Remove locking features from all egress doors/gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Nov 26 2014 | On 07/06/2015: Corrected. On 24/04/2016: Corrected. Factory has removed non-compliant locking features from egress routes exit doors/gates. This issue was corrected in 1st follow up report. On 18/10/2016: Corrected. Factory has removed non-compliant doors/gates with locking features from egress routes and exits. On 21/05/2017: Corrected. Factory has removed non-compliant doors/gates with locking features from egress routes and exits. On 17/09/2017: Corrected as per site observations. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. No locking features were found with the exit doors along means of egress. | Immediately | Corrected
Initial Inspection |  | 7 | Storage was located in the egress path on 2nd and 3rd floors. | Keep egress paths and stairs clear of storage. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Nov 20 2014 | On 07/06/2015: Corrected. On 24/04/2016: Corrected. This issue was corrected in 1st follow up report. On 18/10/2016: Corrected. On 21/05/2017: Corrected. On 17/09/2017: Corrected as per site observations. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. No storages were found in the egress path during the inspection. | Immediately | Corrected
Initial Inspection |  | 8 | Storage was located in the exit stair on ground floor. | Remove all storage from exit stairs and egress paths. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Nov 24 2014 | On 07/06/2015: Corrected. On 24/04/2016: Corrected. This issue was corrected in 1st follow up report. On 18/10/2016: Corrected. On 21/05/2017: Corrected. On 17/09/2017: Corrected as per site observations. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. No storages were found in the exit stair during the inspection. | Immediately | Corrected
Initial Inspection |  | 9 | Collapsible gates/sliding doors are provided at building exits, exit stairs, along egress routes and exit discharge on all floors. | Replace all gates/sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are rewuired for security reasons, utilize special door locking features complying with NFPA 101. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Dec 25 2014 | On 07/06/2015: Corrected. On 24/04/2016: Corrected. Factory has removed non-compliant doors/gates from egress routes. This issue was corrected in 1st follow up report. On 18/10/2016: Corrected. Factory has removed non-compliant doors/gates with locking features from egress routes and exits. On 21/05/2017: Corrected. Factory has removed non-compliant doors/gates with locking features from egress routes and exits. On 17/09/2017: Corrected as per site observations. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 10 | The width of egress aisles is less than 36-in on first floor. | Provide minimum aisle widths of 36-in. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Jan 30 2015 | On 24/04/2016: Corrected. On 18/10/2016: Corrected. On 21/05/2017: Corrected. On 17/09/2017: Corrected. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 11 | Egress door does not swing in the direction of egress travel on ground and first floors. | Modify the egress door to swing in the direction of egress travel. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Nov 25 2014 | On 07/06/2015: Corrected. On 24/04/2016: Corrected. This issue was corrected in 1st follow up report. On 18/10/2016: Corrected. On 21/05/2017: Corrected. On 17/09/2017: Corrected. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 12 | Handrails are not provided in the exit stair on basement and 6th floors. | Provide bandrails on at least one side of exit stair. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Dec 26 2014 | On 07/06/2015: Corrected. On 24/04/2016: Corrected. This issue was corrected in 1st follow up report. On 18/10/2016: Corrected. On 21/05/2017: Corrected. On 17/09/2017: Corrected. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 13 | A single means of egress is provided on basement floor in the north exit. | Provide additional means of egress. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Jan 25 2015 | On 07/06/2015: Corrected. Factory has created new exit stair. On 24/04/2016: Corrected. This issue was corrected in 1st follow up report. On 18/10/2016: Corrected. On 21/05/2017: Corrected. On 17/09/2017: Corrected. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 14 | The fire alarm system is antiquated, not a listed system, and does not provied alarm and fotification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Jun 30 2016 | On 07/06/2015: Factory has submitted drawings for Accord review. Final CAP Timeline: Design submission date has expired. Committed Timeline: Fire alarm system installation September 30, 2015. On 24/04/2016: Fire alarm system drawing has been reviewed by Accord on 13th October, 2015 and installation is in progress. Final CAP Timeline: Expired. Committed Timeline: Within 30th June, 2016. On 18/10/2016: The reviewed drawing of fire alarm system has been found during the 3rd follow-up inspection. Installation work of fire alarm system is going on. On 21/05/2017: Installation of automatic fire alarm system is going on. Note that third party certification mark or permanent label shall be present on each and every fire detection and alarm system equipment. On 17/09/2017: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected as per previous follow up. On 10-March-2024: See Issue# 25. On 27-Aug-25: See Issue# 25. | Design within 4 months, install within 9 month | Corrected
Initial Inspection |  | 15 | Inspection, testing, and maintenance of the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records no-site, in accordance with NFPA 72. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Jun 30 2016 | On 07/06/2015: No action has been taken yet. Final CAP Timeline: Expired. Committed Timeline: Factory management confirms that they will inspect, test and maintain when the new system will be installed. On 24/04/2016: It was same as it was 1st follow up visit. Final CAP Timeline: Expired. Committed Timeline: Within 30th June, 2016. On 18/10/2016: It is an integrated part of fire alarm system. On 21/05/2017: It is an integrated part of fire alarm system. ITM record for new system will be maintained after complete the installation. On 17/09/2017: Corrected. On 29/01/2018: Corrected. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 16 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Remove single-station smoke alarms. Provide automatic smoke detection throughout the building, tied into the fire alarm system, in accordance with NFPA 72. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Jun 30 2016 | On 07/06/2015: Factory has submitted drawings for Accord review. Final CAP Timeline: Design submission date has expired. Committed Timeline: Fire alarm system installation September 30, 2015. On 24/04/2016: It is an integrated part of fire alarm system. Final CAP Timeline: Expired. Committed Timeline: Within 30th June, 2016. On 18/10/2016: It is an integrated part of fire alarm system. On 21/05/2017: It is an integrated part of fire alarm system. On 17/09/2017: Corrected. On 29/01/2018: Corrected. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected as per previous follow-up. On 10-March-2024: See Issue# 25. On 27-Aug-25: See Issue# 25. | Within 6 months | Corrected
Initial Inspection |  | 17 | Exit sign with directional arrows are not provided at exit access to the exit doors. | Provide exit signs with directional arrows above all exits access leading to the exterior and all doors to the exit stairs. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Nov 20 2014 | On 07/06/2015: Corrected. On 24/04/2016: Corrected. This issue was corrected in 1st follow up report. On 18/10/2016: Corrected. On 21/05/2017: Corrected. On 17/09/2017: Corrected. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 18 | Exit signage not illuminated burned out or broken on 1st, 2nd and 3rd floors. | Regularly inspect all exit signge and replace/install lights as needed to illuminate signs | Issue has been completed as per RSC standard and also verified by the Inspection team. | Jan 11 2014 | On 07/06/2015: Corrected. On 24/04/2016: Corrected. This issue was corrected in 1st follow up report. On 18/10/2016: Corrected. On 21/05/2017: Corrected. On 17/09/2017: Corrected. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 19 | Emergency lighting did not function in test mode burned out or broken on 1st, 2nd and 3rd floors. | Reguarly test the emergency lighting system on each floor and replace/repai lights as reeded. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Jan 11 2014 | On 07/06/2015: Corrected. On 24/04/2016: Corrected. This issue was corrected in 1st follow up report. On 18/10/2016: Corrected. On 21/05/2017: Corrected. On 17/09/2017: Corrected. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 20 | Inspection, testing, and maintenance for the emergency lighting system was not in accordance with The ACCORD standard. | inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Jun 30 2015 | On 07/06/2015: Not corrected. Factory management is inspecting, testing and maintaining but which is not as per Accord standard. Final CAP Timeline: Expired. Committed Timeline: June 30, 2015. On 24/04/2016: Corrected. Factory management is maintaining emergency & exit light maintenance checklist as per Accord standard. On 18/10/2016: Corrected. On 21/05/2017: Corrected. On 17/09/2017: Corrected. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 21 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes no 1st, 2nd and 3rd floors. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Issue has been completed as per RSC standard and also verified by the Inspection team. | May 20 2016 | On 24/04/2016: Factory management is increasing emergency light on aisles as per standard and confirms that this issue will be completed within committed timeline. Final CAP Timeline: Expired. Committed Timeline: Within 20th May, 2016. On 18/10/2016: Corrected. On 21/05/2017: Corrected. On 17/09/2017: Corrected. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 22 | New Findings: The required standpipe system is antiquated not in accordance with the ACCORD standard. | Install a new standpipe system in accordance with ACCORD standard 5.4 and NFPA 14. A class III system shall be installed in buildings with the highest occupied floor 10 m (33 ft.) above grade or more. A class I system shall be permitted in buildings protected throughout by an approved automatic sprinkler system. | Based on the technical meeting with RSC team on 20-May-26: The factory will work on existing reservoir. After completion of work the Factory concern will inform RSC. | Aug 30 2016 | For previous comments, see the previous reports. On 31/01/2023: Pre T&C found that the system is not corrected. See detailed Pre T&C report. On 10-March-2024: During the inspection, no significant progressive action was observed. In addition, the fire pump room was not directly accessible from the outside or not provided with an enclosed passageway. The factory person has reported that they are addressing the issues outlined in the previous pre-T&CVI report. They have been in communication with various contractors and have indicated that they require additional time to complete the remaining tasks. Furthermore, they have requested financial support from RSC to facilitate the completion of this work. On 27-Aug-25: The factory submitted the SUPS documents on 30-Apr-2025 for pre-T&CVI and received review feedback with observations on 08-Jul-2025. After addressing the observations, the factory resubmitted the revised documents on 24-Aug-2025 and is currently awaiting review feedback. Several modification works, as noted in the last pre-T&CVI report, were found ongoing, such as fire protection of the feed main and 65 mm connection pipe for the landing valve, replacement of non-listed air vent valve and pressure gauges, and improvement of pump room ventilation and water drainage system etc. RPO Comments: On 15-Jun-2026 the T&CVI documents are pending to be submitted to RSC. | Within 6 months | In Progress
Follow Up Inspection |  | 23 | New Finding (3rd Follow-up): Penetrations through floor/ceiling assemblies (expansion joints) are found unsealed. Location(s): Basement to 5th floor. | Seal all the (expansion joints) penetrations by a minimum 2-hr fire rated materials to maintain the fire separation. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Jan 20 2016 | On 21/05/2017: Corrected. On 17/09/2017: Corrected. On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 24 | New Finding (5th Follow-up): Fire door is held open for entry and exit purpose. Location generator room on basement. | If fire door is required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system & door co-ordinator for double leaf door. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Oct 17 2017 | On 29/01/2018: Corrected based on site observations. On 18/09/2018: Corrected. On 12/09/2021: Corrected. On 31/01/2023: Corrected. On 10-March-2024: Corrected. On 27-Aug-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 25 | New Finding (5th Follow-up): The fire detection system (a few detector) did not install proper position. Location: 2nd floor finishing & several position nearest fan, detector is missed for 1st floor on landing-stair-1, . | Re-arrange the detector such that the fire detection system is throughout the building in accordance with NFPA 72. | Based on the technical meeting with RSC team on 20-May-26: FADS: The factory will collect a declaration from manufacturer about SLC loop current limit & calculation process. After collecting the declaration, the Factory concern will share it with RSC. | Sep 17 2017 | For previous comments, see the previous reports. On 31/01/2023: Pre T&C found that the system is not corrected. See detailed Pre T&C report. On 10-March-2024: During the inspection, no significant progressive action was observed. The factory person has reported that they are addressing the issues outlined in the previous pre-T&CVI report. They have been in communication with various contractors and have indicated that they require additional time to complete the remaining tasks. Furthermore, they have requested financial support from RSC to facilitate the completion of this work. On 27-Aug-25: The factory submitted the FADS documents on 30-Apr-2025 for pre-T&CVI and received review feedback with observations on 08-Jul-2025. After addressing the observations, the factory resubmitted the revised documents on 24-Aug-2025 and is currently awaiting review feedback. The FACP was found with lots of trouble during the inspection. RPO Comments: On 15-Jun-2026 the T&CVI documents are pending to be submitted to RSC.. | Within 1 month | In Progress
Follow Up Inspection |  | 26 | New Finding (10th FU): Dining (E4 occupancy) area is not separated from production (G2 occupancy) with fire rated assemblies. | Separate the dining area from other occupancies with 3-hr fire rated construction, provide minimum 3-hr. rated doors for the openings and seal the unprotected penetrations. Provide minimum two exits that lead directly to the street or exit stairwell or leading to a corridor or open space. | Already facility has been completed. | May 12 2024 | New Finding On 27-Aug-25: The factory submitted the gypsum board documents on 09-Mar-2025 for separation of the dining area from the production area and received review feedback with observations on 03-Jun-2025. After addressing the observations, the factory resubmitted the revised documents and is currently awaiting review feedback. Based on remediation methodology approval, the factory will separate the dining area from the the production area by fire rated gypsum boards. RPO Comments: On 15-Jun-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 Months | Pending Verification
Follow Up Inspection |  | 27 | New Finding (10th FU): Compressor is not properly separated by fire rated construction with store. | Compressor shall be separated from other occupancies by a minimum 1-hr fire rated construction (wall, floor, slab etc). Seal all penetrations and openings (door, window etc.) should be protected by 0.75-hr (45 min) fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. Or Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. | Issue has been completed as per RSC standard and also verified by the Inspection team. | Apr 18 2024 | On 27-Aug-25: Corrected. The factory has separated the compressor room from the store by fire rated wall and fire rated door from the store in basement. | Within 1 Month | Corrected

## Electrical
Date
15-Jun-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Renown Apparels Ltd., Bhatiary Link Road ( South Side ) Barodighir Par, Hathazary, Chattogram, Chattogram, Chittagong
Date of Inspection |  | 2014-07-19
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Fuse tube of DO fuse is missing. | Install fuse tube, if not possible replace DO fuse by a new set. | Facility has already completed the task as per standerd and it was verified by RSC team | Jun 30 2016 | On 06/07/2015: This issue has not corrected yet. New committed timeline is 30/08/2015. On 24/04/2016: Not corrected yet. New committed timeline is given till 30/06/2016. On 18/10/2016: Still in corrected. On 21/05/2017: Corrected. | 25 Weeks | Corrected
Initial Inspection |  | 2 | Overhead service cables are not supported. | Overhead service cable must be firmly fixed at both ends and supported on catenary wire. | Facility has already completed the task as per standerd and it was verified by RSC team | Aug 30 2015 | On 06/07/2015: Factory engineer is suggested to avoid support the cable with the tree. New committed timeline is 30/08/2015. On 24/04/2016: Corrected. | 25 Weeks | Corrected
Initial Inspection |  | 3 | Cables are not supported (typical). | Cables must be supported in trays or ladders or PVC pipe. | Facility has already completed the task as per standerd and it was verified by RSC team | Nov 25 2014 | This issue is verified at 1st follow up. | 4 Weeks | Corrected
Initial Inspection |  | 4 | Multiple cables are connected to the MCCB terminal. | Connect single cable in single port. | Facility has already completed the task as per standerd and it was verified by RSC team | Aug 30 2015 | On 06/07/2015: This issue has not corrected yet. New committed timeline is 30/08/2015. On 24/04/2016: Corrected. | 3 Weeks | Corrected
Initial Inspection |  | 5 | Cable trench without cover. | The cable trench must be tightly covered to avoid physical damage to the cables from falling objects. The cover must prevent the trench from falling debris, dust and lint. | Facility has already completed the task as per standerd and it was verified by RSC team | Nov 30 2014 | This issue is verified at 1st follow up. | 12 Weeks | Corrected
Initial Inspection |  | 6 | Cable terminated from panel (top and base) is not supported. | Steel or PVC conduit or cable tray must be installed for the cable support to prevent damages and stress to the cables. | Facility has already completed the task as per standerd and it was verified by RSC team | Nov 25 2014 | This issue is verified at 1st follow up. | 4 Weeks | Corrected
Initial Inspection |  | 7 | Panel doors not connected with earth bond (typical). | Provide earth connection for body and doors of metallic distribution boards using green cables preferably braid so that the metallic door remains at zero potential all the time. | Facility has already completed the task as per standerd and it was verified by RSC team | Jul 30 2015 | On 06/07/2015: This issue has not corrected yet. New committed timeline is 30/07/2015. On 24/04/2016: Corrected. | 3 Weeks | Corrected
Initial Inspection |  | 8 | Barrier/ separators between different phases are not installed. | Install separators between different phases of MCCB. Standard separators provided by the MCCB manufacturer must be used. | Facility has already completed the task as per standerd and it was verified by RSC team | Nov 15 2014 | This issue is verified at 1st follow up. | 3 Weeks | Corrected
Initial Inspection |  | 9 | Cables connected to MCCBs without lug. | Cables terminating at MCCBs must be installed with cable lugs/ terminals of required size and rating. | Facility has already completed the task as per standerd and it was verified by RSC team | Nov 15 2014 | This issue is verified at 1st follow up. | 3 Weeks | Corrected
Initial Inspection |  | 10 | Flexible cables are laid on concrete floor without mechanical guard. | Steel or PVC conduit or cable tray must be installed for the cable to prevent damages and stress to the cables. | Facility has already completed the task as per standerd and it was verified by RSC team | Nov 30 2014 | This issue is verified at 1st follow up. | 12 Weeks | Corrected
Initial Inspection |  | 11 | Wires connected to bus bar without using cable lug. | Cables shall be connected to terminals only by soldered/ welded lugs according to the size of the respective cables. Proper crimping tools must be used to punch the socket. | Facility has already completed the task as per standerd and it was verified by RSC team | Nov 15 2014 | This issue is verified at 1st follow up. | 3 Weeks | Corrected
Initial Inspection |  | 12 | The factory does not have electrical single line diagram. | Factory must have as-built electrical single line diagram for proper maintenance of their electrical system. | Facility has already completed the task as per standerd and it was verified by RSC team | Jun 30 2016 | On 06/07/2015: This issue has not corrected yet. New committed timeline is 30/08/2015. On 24/04/2016: Factory has a drawing but not amended and not as built. Send as built SLD to ACCORD for review. New timeline is given till 30/06/2016. On 18/10/2016: SLD is submitted to ACCORD for 3rd review. Still in corrected. On 21/05/2017: Not corrected. On 17/09/2017: Corrected. | 12 Weeks | Corrected
Initial Inspection |  | 13 | No circuit directory on the panel. | Correct circuit directory should be put/attach inside each panel with one line diagram. | Facility has already completed the task as per standerd and it was verified by RSC team | Dec 30 2014 | This issue is verified at 1st follow up. | 12 Weeks | Corrected
Initial Inspection |  | 14 | No test report submitted during inspection. | 1. Thermographic scanning inspection should be done three times per year. 2. Insulation resistance test of electrical equipment should be done in five years cycle. 3. Earth resistance test should be done in five years cycle. | Facility has already completed the task as per standerd and it was verified by RSC team | Feb 12 2015 | This issue is verified at 1st follow up. | 25 Weeks | Corrected
Follow Up Inspection |  | 15 | New Finding: Transformer arcing horns are not aligned. | Transformer arcing horn should be aligned. | Facility has already completed the task as per standerd and it was verified by RSC team | Oct 26 2015 | On 18/10/2016: Verified at 2nd follow up inspection. | 3 Months | Corrected
Follow Up Inspection |  | 16 | New Finding: Transformer silica gel is discolored. | Replace silica gel by a new one; or dry it under sun and reuse it, if colour regains. | Facility has already completed the task as per standerd and it was verified by RSC team | Oct 26 2015 | On 18/10/2016: Verified at 2nd follow up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 17 | New Finding: Generator body has no earth connection. | Ensure minimum two earthing connection for generator body (consult with your generator supplier). | Facility has already completed the task as per standerd and it was verified by RSC team | Sep 26 2015 | On 18/10/2016: Verified at 2nd follow up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 18 | New Finding: Inadequate rubber (insulation) mat on the working area of distribution board/panel. | Put electrical insulation (rubber mat) on the working area of each electrical installation (transformer/ LT panel/MDB/ DB/SDB/ other manual operated machineries). | Facility has already completed the task as per standerd and it was verified by RSC team | Aug 26 2015 | On 18/10/2016: Verified at 2nd follow up inspection. | 1 Month | Corrected
Follow Up Inspection |  | 19 | New Finding: Cables passing through wall/ floor slab are not protected at the entry/exit point(s). | Cables passing through permanent wall/floor slab must be protected. Seal the opening by fire rated material protecting power cables thus no smoke can pass through this. | Facility has already completed the task as per standerd and it was verified by RSC team | Sep 26 2015 | On 18/10/2016: Verified at 2nd follow up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 20 | New Finding: Battery terminals are left open. | Use insulated rubber cap to cover all the battery terminals. | Facility has already completed the task as per standerd and it was verified by RSC team | Aug 26 2015 | On 18/10/2016: Verified at 2nd follow up inspection. | 1 Month | Corrected
Follow Up Inspection |  | 21 | New Finding: Inadequate working space around panels and access to the panel is inconvenient. | Ensure at least 1 meter (or equal to the width of board, whichever is higher) working clearance in front of each panel. | Facility has already completed the task as per standerd and it was verified by RSC team | Oct 26 2015 | On 18/10/2016: Verified at 2nd follow up inspection. | 3 Months | Corrected
Follow Up Inspection |  | 22 | New Finding: Unterminated wire is kept inside the electrical panel. | All unterminated wires shall be removed. | Facility has already completed the task as per standerd and it was verified by RSC team | Sep 26 2015 | On 18/10/2016: Verified at 2nd follow up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 23 | New Finding: Lightning Protection System (LPS) drawing is unavailable. | Design LPS as built and share with Accord to get information any necessary modification. | Facility has already completed the task as per standerd and it was verified by RSC team | Jun 30 2016 | On 24/04/2016: LPS drawing is found but not installed yet. New timeline is given till 30/06/2016. On 16/06/2016: The proposed time extension on 31/07/2016 is not acceptable. This issue is now behind the schedule. On 18/10/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 24 | New Finding: Safety program is not initiated. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. After the training, there should be exam to evaluate the influence of the training program. | Facility has already completed the task as per standerd and it was verified by RSC team | Oct 26 2015 | After the training, there should be exam to evaluate the influence of the training program. | 3 Months | Corrected
Follow Up Inspection |  | 25 | New Finding: Generator room has inadequate ventilation. | Ensure/arrange cross ventilation for generator room; You may use fire damper if you have to keep any opening on the corridor/ egress path/exit. | Facility has already completed the task as per standerd and it was verified by RSC team | Jun 30 2016 | On 18/10/2016: Additional ventilation is provided for generator room. During inspection generator is found temporarily shifted to ground floor from basement for retrofitting work. | 2 Months | Corrected
Follow Up Inspection |  | 26 | New Finding: Safety program is initiated but has no influence in the factory. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. | Facility has already completed the task as per standerd and it was verified by RSC team | Jun 30 2017 | On 17/09/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding: Oil spillage/ leakage has been observed in generator room. | Any kind of oil spillage/ leakage must be stopped; and generator must be kept always dry. | Facility has already completed the task as per standerd and it was verified by RSC team | Oct 31 2017 | On 29/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding: Power cables are hanging without proper support. Cable duct/channels are filled with fluffs (lint/ dust). | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Facility has already completed the task as per standerd and it was verified by RSC team | Mar 3 2018 | On 18/09/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/ undersize. | Earth lead cable/ Earth Continuity Conductor (ECC) must be resized by half of the phase cable. Cable size shall be selected depending on the CB's response time and phase cable's size. | Facility has already completed the task as per standerd and it was verified by RSC team | Apr 3 2018 | On 18/09/2018: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 30 | New Finding: LPS air terminal are disconnected & loose bonding found at several points. | Missing down conductors shall be reinstalled & tightening all the bonding's shall be done as per standard. | Facility has already completed the task as per standerd and it was verified by RSC team | Apr 3 2018 | On 18/09/2018: Not corrected. LPS not maintained regularly. Connectors are rusted, conductors are painted etc. On 21-Sep-2021: Factory has replaced a few baseplates. But few other baseplates still need to be modified. On 28-Dec-2022: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 31 | New Finding: Calibration certificates of testing equipment's are not proper. | Calibration certificates of all testing equipment's shall have proper information of testing equipment's. | Facility has already completed the task as per standerd and it was verified by RSC team | Nov 5 2021 | On 28-Dec-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 32 | New Finding: Hazardous lights in store room/ storage areas are uncovered. | Hazardous lights in store room/ storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. | Facility has already completed the task as per standerd and it was verified by RSC team | Nov 5 2021 | On 28-Dec-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: Field information has less reflection in existing SLD. | Electrical SLD must be updated properly; all the required information must be mentioned there; and it shall be updated when you do substantial amount of changes of your electrical system. | The factory is currenly working to re-submit SLD for RSC review within 12-Days. | Feb 20 2023 | On 12/12/2023: Not corrected. Update as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. On 10/03/2024: Not corrected. As-built SLD found but not submitted to RSC yet for approval. On 05/02/2025: Not corrected. The review status of SLD is "Accepted" from RSC on 21-Apr-2024. Remediation work is going on; almost 40% of the work has been completed. On 29/04/2026: Not corrected. Significant changes of the electrical system have been observed from the accepted SLD. So, SLD needs to resubmit by 10-Jun-2026 to RSC for further review. RPO Comments: On 15-Jun-2026 the design documents SLD are pending to be submitted to RSC.The timeline has be expired on 10-Jun-2026. | 1 Month | In Progress
Follow Up Inspection |  | 34 | New Finding: Multiple cables (came from different electrical consumers) terminated at busbar. | Each electrical circuit must be terminated at single busbar/ MCB/MCCB terminals. | Update 27.07.2024 These work is completed. | May 20 2024 | On 05/02/2025: Corrected as per satisfactory pictorial evidence provided by factory. | 2 Months | Corrected
Follow Up Inspection |  | 35 | New Finding: Hot spots have been observed at some points. | Hot spots must be eliminated from entire electrical system. | Update 18.09.2024 These work is completed. | Apr 21 2024 | On 05/02/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 36 | New Finding: Outdoor cables are not covered to protect from weather effect. | Outdoor cable tray/ladders shall be covered properly to avoid seasonal effect on cables and its longevity. | Update 18.09.24 These work is completed. | May 20 2024 | On 05/02/2025: Corrected as per satisfactory pictorial evidence provided by factory. | 2 Months | Corrected
Follow Up Inspection |  | 37 | New Finding: Lightning Protection System (LPS) is not installed properly including improper air terminal spacing & mismatch between drawing and physical installation. | Factory required to be redesign the Lightning Protection System (LPS) as per standard for the entire facility. Once the LPS is properly designed, it must be installed according to the design specifications to ensure effective protection against lightning strikes. | Update 02.11.2025 Work completed. | May 5 2025 | On 29/04/2026: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 38 | New Finding: Electric safety training program is not initiated by qualified electrical personnel. | Electrical safety training and awareness programs for electrical personnel must be conducted regularly by qualified personnel and documented. This periodic task is crucial for continuously improving overall electrical safety for factory staff. | Facility has been completed and waiting for verification. | May 29 2026 | RPO Comments: On 15-Jun-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 39 | New Finding: Uncovered cables are used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Facility has been completed and waiting for verification. | Jul 29 2026 | RPO Comments: On 15-Jun-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 3 Months | Pending Verification
Follow Up Inspection |  | 40 | New Finding: Earth Continuity Conductor size is inadequate/ not available. | Earth lead cable/ Earth Continuity Conductor (ECC) shall be determined according to BNBC or Adiabatic method (considering CB's response time, fault current & type of earth conductor other factors). | Facility has been completed and waiting for verification. | Jun 29 2026 | RPO Comments: On 15-Jun-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 Months | Pending Verification
Follow Up Inspection |  | 41 | New Finding: Ceiling fan installed within reach of average human height. | Install the ceiling fan above average human height. | Facility has been completed and waiting for verification. | Jun 29 2026 | RPO Comments: On 15-Jun-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 Months | Pending Verification