## Structural
Date
12-Apr-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Ripon Knitwear Ltd, Jarun, Konabari, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-04-23
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Highly stressed column for irregular structural arrangement | No further construction at roof level to be carried out until a full Detail Engineering Assessment (DEA, see attached scope) of the building is completed. | Corrected | Mar 1 2016 | On 25/08/2015: The factory already completed construction and it will cover in DEA report. On 17/02/2016: Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st-March-2016.Previous timeline was 08-Aug-2014. On 20/12/2016: DEA has been submitted to Accord and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. No discrepancy were found in as built drawings. On 21/10/2018: Corrected in previous follow up inspection. DEA had been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was found completed. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. No further construction was observed. On 21-Sep-2023: This issue was corrected from previous inspection. DEA of Building 1 had been re-accepted on 16 October 2022 by RSC. As per accepted DEA recommendation, strengthening work was found completed. No further construction was observed. On 28-Sep-2025: Previously corrected. | Immediately | Corrected
Initial Inspection |  | 2 | Highly stressed column for irregular structural arrangement | Factory Engineer to review design, loads and columns stresses for all columns. | Corrected | Mar 1 2016 | On 25/08/2015: DEA is under review On 17/02/2016: This issue will be covered in DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014. On 20/12/2016: DEA has been submitted to Accord and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. No discrepancy were found in as built drawings. On 21/10/2018: Corrected in previous follow up inspection. DEA had been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was found completed. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. (See Item-44). On 21-Sep-2023: This issue was corrected from previous inspection. DEA of Building 1 was re-accepted on 16 October 2022 by RSC. (See Item no 44) On 28-Sep-2025: Previously corrected. | Immediately | Corrected
Initial Inspection |  | 3 | Highly stressed column for irregular structural arrangement | Verify in situ concrete stresses either by cores or existing cylinder strength data for all the columns or 100mm dia. cores from minimum 4 non-critical columns. | Corrected | Aug 8 2014 | On 25/08/2015: The factory already completed test work. On 17/02/2016: Concrete Cores have taken from structural elements. On 20/12/2016: Corrected from previous follow up inspection. On 08/05/2017: Concrete strength test was done by factory. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. This issue was corrected by previous inspection. On 21/10/2018: Corrected in previous follow up inspection. Core test had been done. DEA had been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was found completed. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. On 21-Sep-2023: This issue was corrected from previous inspection. DEA of Building 1 was re-accepted on 16 October 2022 by RSC. Concrete core was taken by the factory, which was covered in DEA. On 28-Sep-2025: Previously corrected. | Immediately | Corrected
Initial Inspection |  | 4 | Highly stressed column for irregular structural arrangement | A Detail Engineering Assessment (DEA) of Factory to be commenced - see attached Scope | Corrected | Mar 1 2016 | On 25/08/2015: The factory submitted DEA report and DEA is under review. On 17/02/2016: Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014. On 20/12/2016: DEA has been submitted to Accord and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. No discrepancy were found in as built drawings. On 21/10/2018: Corrected in previous follow up inspection. Core test had been done. DEA had been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was found completed. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. (See Item-44). On 21-Sep-2023: This issue was corrected from previous inspection. DEA of Building 1 was re-accepted on 16 October 2022 by RSC. (See Item no 44) On 28-Sep-2025: Previously corrected. | Immediately | Corrected
Initial Inspection |  | 5 | Highly stressed column for irregular structural arrangement | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | Corrected | Mar 1 2016 | On 25/08/2015: Presently found the loading below 30 psf after approval of DEA they should follow final load plan. On 17/02/2016: After approval of DEA, factory shall follow the final load plan. However, load plan have observed at 1st floor & roof only, At 2nd & 1st floor load was found around 42 psf.Factory requires to maintain the load below 42 psf before approval of DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: Load plan has been produced as a part of DEA which was accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Load plan has been produced along with DEA report. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. Factory required to follow final load plan. On 21/10/2018: Corrected in previous follow up inspection. Load plan had been produced along with DEA report. Factory had carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. Factory required to follow final load plan. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. Load plan has been produced and accepted as a part of DEA. During inspection, accepted load plan was found posted on every floor and live load was found below 2 kPa (allowable 2 kPa, 3 kPa and 4 kPa). On 21-Sep-2023: This issue was corrected from previous inspection. Load plan has been produced along with DEA report. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 16 October 2022 by RSC. As per accepted DEA recommendation, strengthening work was complete. During inspection, accepted load plan was found posted on every floor and live load was found below allowable limit (2kPa for Typical, 3kPa for dinning & 4kPa for stair). On 28-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 6 | Highly stressed column for irregular structural arrangement | A Detail Engineering Assessment (DEA) of Factory to be completed. | Corrected | Mar 1 2016 | On 25/08/2015: The factory submitted DEA report and DEA is under review. On 17/02/2016: Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: DEA has been submitted to Accord and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. No discrepancy were found in as built drawings. Factory required to follow final load plan. On 21/10/2018: Corrected in previous follow up inspection. Core test had been done. DEA had been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was found completed. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. (See Item-44). On 21-Sep-2023: This issue was corrected from previous inspection. DEA of Building 1 was re-accepted on 16 October 2022 by RSC. (See Item no 44). On 28-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 7 | Highly stressed column for irregular structural arrangement | Remove fixed loading as required by DEA. | Corrected | Mar 1 2016 | On 25/08/2015: Presently found the loading below 30 psf after approval of DEA they should follow final load plan. On 17/02/2016: After approval of DEA, factory shall follow the final load plan. However, load plan have observed at 1st floor & roof only, At 2nd & 1st floor load was found around 42 psf.Factory requires to maintain the load below 42 psf before approval of DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: DEA has been submitted to Accord and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: No high loading was found during inspection. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. Load plan was found posted. On 21/10/2018: Corrected in previous follow up inspection. High loading was not found during inspection. Factory had carried out revised Detail Engineering Assessment(DEA). DEA had been re-accepted on 07/02/2017 by Accord. Load plan was found posted. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. (See Item-44). On 21-Sep-2023: This issue was corrected from previous inspection. DEA of Building 1 was re-accepted on 16 October 2022 by RSC. (See Item no 44). On 28-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 8 | Highly stressed column for irregular structural arrangement | Complete any strengthening works arising from DEA. | Corrected | Mar 1 2016 | On 25/08/2015: Will cover in DEA On 17/02/2016: Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.After approval of DEA, if any strengthen works requires. Factory shall do accordingly. Previous timeline was 08-Aug-2014. On 20/12/2016: DEA has been submitted to Accord and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. After approval of revised DEA all retrofitting works shall be done. On 08/05/2017: Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. On 21/10/2018: Corrected in previous follow up inspection. DEA had been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was found completed. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. (See Item-44). On 21-Sep-2023: This issue was corrected from previous inspection. DEA of Building 1 was re-accepted on 16 October 2022 by RSC. As per DEA recommendation remedial works were completed for Building 1.(See Item no 44). On 28-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 9 | Highly stressed column for irregular structural arrangement | Continue to implement the load plan. | Corrected | Mar 1 2016 | On 25/08/2015: Presently found the loading below 30 psf after approval of DEA they should follow final load plan. On 17/02/2016: After approval of DEA, factory shall follow the final load plan. However, load plan have observed at 1st floor & roof only, At 2nd & 1st floor load was found around 42 psf.Factory requires to maintain the load below 42 psf before approval of DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: Load plan has been produced as a part of DEA which was accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Load pan found posted. Load was found below allowable load limit. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. Factory should follow final loading plan. On 21/10/2018: Corrected in previous follow up inspection. High loading was not found during inspection. Overall loading was found below 42 psf. Factory had carried out revised Detail Engineering Assessment(DEA). DEA had been re-accepted on 07/02/2017 by Accord. Load plan was found posted. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. See new findings below. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. During inspection, accepted load plan was found posted on every floor and live load was found below 2 kPa (allowable 2 kPa, 3 kPa and 4 kPa). On 21-Sep-2023: This issue was corrected from previous inspection. Load plan has been produced along with DEA report. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 16 October 2022 by RSC. As per accepted DEA recommendation, strengthening work was complete. During inspection, accepted load plan was found posted on every floor and live load was found below allowable limit (2kPa for Typical, 3kPa for dinning & 4kPa for stair). On 28-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 10 | Unclear structural systems and lack of relevant structural information | As part of DEA outlined in Item 1, as built structural information of existing structure to be generated and assessed. | Corrected | Mar 1 2016 | On 25/08/2015:The factory submitted DEA report and DEA is under review. On 17/02/2016: This issue will be covered in DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: DEA has been submitted to Accord and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. No discrepancy were found in as built drawings. On 21/10/2018: Corrected in previous follow up inspection. DEA had been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was found completed. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. (See Item-44). On 21-Sep-2023: This issue was corrected from previous inspection. DEA of Building 1 was re-accepted on 16 October 2022 by RSC. As per DEA recommendation remedial works were completed for Building 1. On 28-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 11 | Unclear structural systems and lack of relevant structural information | Building Engineer to determine capability of existing structure to resist gravity and lateral loading. Particular attention to structural adequacy of flat slab design and construction for column punching shear is required. | Corrected | Mar 1 2016 | On 25/08/2015:The factory submitted DEA report and DEA is under review. On 17/02/2016: This issue will be covered in DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: DEA has been submitted to Accord and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. On 21/10/2018: Corrected in previous follow up inspection. DEA had been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was found completed. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. (See Item-44). On 21-Sep-2023: This issue was corrected from previous inspection. DEA of Building 1 was re-accepted on 16 October 2022 by RSC. As per DEA recommendation remedial works were completed for Building 1.(See Item no 44). On 28-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 12 | Unclear structural systems and lack of relevant structural information | Update as built drawings as strengthening works are completed. | Corrected | Mar 1 2016 | On 25/08/2015:The factory submitted DEA report and DEA is under review. On 17/02/2016: This issue will be covered in DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: DEA has been submitted to Accord and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. No discrepancy were found in as built drawings. On 21/10/2018: Corrected in previous follow up inspection. DEA had been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was found completed. No discrepancy were found in as built drawings. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. (See Item-44). On 21-Sep-2023: This issue was corrected from previous inspection. On 28-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 13 | Unclear structural systems and lack of relevant structural information | Update as built drawings if further modifications are made to structural elements within the building. | Corrected | Mar 1 2016 | On 25/08/2015: Cover in DEA On 17/02/2016: This issue will be covered in DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: DEA has been submitted to Accord and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. No discrepancy were found in as built drawings. On 21/10/2018: Corrected in previous follow up inspection. DEA had been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was found completed. No discrepancy were found in as built drawings. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. (See Item-44). On 21-Sep-2023: This issue was corrected from previous inspection. DEA of Building 1 was re-accepted on 16 October 2022 by RSC. On 28-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 14 | Structural stability of Generator Building | All cracking in slabs between main factory building and Generator House to be monitored. | Corrected | Mar 1 2016 | On 25/08/2015: Cover in DEA On 17/02/2016: Factory requires to monitor & investigate any further cracking. Slab adequacy will be verify through DEA .Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: DEA has been submitted to Accord and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: As per factory engineer recommendation factory repaired crack. Factory required to proper monitoring on crack. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. On 21/10/2018: Corrected in previous follow up inspection. DEA had been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was found completed. As per factory engineer recommendation factory repaired crack. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. During inspection no further crack was observed. On 21-Sep-2023: This issue was corrected from previous inspection. During inspection, no cracks were found on structural elements. On 28-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 15 | Structural stability of Generator Building | As part of DEA outlined in Item 1, Building Engineer to determine capability of Generator House structure to resist gravity and lateral loading. | Corrected | Mar 1 2016 | On 25/08/2015: Cover in DEA On 17/02/2016: This issue will be covered in DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: DEA has been submitted to Accord and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. On 21/10/2018: Corrected in previous follow up inspection. DEA had been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was found completed. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. (See Item-44). On 21-Sep-2023: This issue was corrected from previous inspection. DEA of Building 1 was re-accepted on 16 October 2022 by RSC.(See Item no 44). On 28-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 16 | Structural stability of Generator Building | Complete strengthening works as required by DEA. | Corrected | Mar 1 2016 | On 25/08/2015:The factory submitted DEA report and DEA is under review. On 17/02/2016: Factory requires to implement any strengthening works after approval of DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory shall revised DEA within 1st March,2016..Previous timeline was 31-Jan-2015 On 20/12/2016: DEA has been submitted to Accord and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. After approval of revised DEA all retrofitting works shall be done. On 08/05/2017: Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. On 21/10/2018: Corrected in previous follow up inspection. DEA had been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was found completed. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. (See Item-44). On 21-Sep-2023: This issue was corrected from previous inspection. DEA of Building 1 was re-accepted on 16 October 2022 by RSC. (See Item no 44). On 28-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 17 | Structural stability of Generator Building | Repair cracks to Building Engineer’s specification as necessary. | Corrected | Mar 1 2016 | On 25/08/2015:The factory submitted DEA report and DEA is under review. On 17/02/2016: Factory requires to monitor & investigate any further cracking reqularly.Slab adequacy will be verify through DEA .Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: DEA has been submitted to Accord and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: As per factory engineer recommendation factory repaired crack and maintain a register so that further crack can't occur. On 21/10/2018: Corrected in previous follow up inspection. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. During inspection no further crack was observed. On 21-Sep-2023: This issue was corrected from previous inspection. During inspection, no cracks were found on structural elements. On 28-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 18 | Structural stability of Generator Building | Continue to monitor cracks in slabs between main factory building and Generator House. | Corrected | Mar 1 2016 | On 25/08/2015:The factory submitted DEA report and DEA is under review. On 17/02/2016: Factory requires to monitor & investigate any further cracking. Slab adequacy will be verify through DEA .Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: DEA has been submitted to Accord and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: On 08/05/2017: As per factory engineer recommendation factory repaired crack and maintain a register so that further crack can't occur. On 21/10/2018: Corrected in previous follow up inspection. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. During inspection no further crack was observed. On 21-Sep-2023: This issue was corrected from previous inspection. During inspection, no cracks were found on structural elements. On 28-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 19 | Localised areas of high loading | Create controlled loading plans for all floors, which account for solid partition loads and other fixed loads and designate where storage can be placed. | Corrected | Mar 1 2016 | On 25/08/2015: Presently found the loading below 30 psf after approval of DEA they should follow final load plan. On 17/02/2016: After approval of DEA, factory shall follow the final load plan. However, load plan have observed at 1st floor & roof only, At 2nd & 1st floor load was found around 42 psf.Factory requires to maintain the load below 42 psf before approval of DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: Load plan has been produced as a part of DEA which was accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Load pan found posted. Load was found below allowable load limit. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. Factory should follow final loading plan. On 21/10/2018: Corrected in previous follow up inspection. High loading was not found during inspection. Overall loading was found below 42 psf. Factory had carried out revised Detail Engineering Assessment(DEA). DEA had been re-accepted on 07/02/2017 by Accord. Load plan was found posted. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. Load plan has been produced and accepted as a part of DEA. On 21-Sep-2023: This issue was corrected from previous inspection. Load plan has been produced along with DEA report. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 16 October 2022 by RSC. As per accepted DEA recommendation, strengthening work was complete. During inspection, accepted load plan was found posted on every floor and live load was found below allowable limit (2kPa for Typical, 3kPa for dinning & 4kPa for stair). On 28-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 20 | Localised areas of high loading | Plans to take findings of DEA, as per Item 1, into account. | Corrected | Mar 1 2016 | On 25/08/2015: Presently found the loading below 30 psf after approval of DEA they should follow final load plan. On 17/02/2016:After approval of DEA, factory shall follow the final load plan. However, load plan have observed at 1st floor & roof only, At 2nd & 1st floor load was found around 42 psf.Factory requires to maintain the load below 42 psf before approval of DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: Load plan has been produced as a part of DEA which was accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Load pan found posted. Load was found below allowable load limit. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. Factory should follow final loading plan. On 21/10/2018: Corrected in previous follow up inspection. High loading was not found during inspection. Overall loading was found below 42 psf. Factory had carried out revised Detail Engineering Assessment(DEA). DEA had been re-accepted on 07/02/2017 by Accord. Load plan was found posted. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. On 21-Sep-2023: This issue was corrected from previous inspection. Load plan has been produced along with DEA report. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 16 October 2022 by RSC. As per accepted DEA recommendation, strengthening work was complete. During inspection, accepted load plan was found posted on every floor and live load was found below allowable limit (2kPa for Typical, 3kPa for dinning & 4kPa for stair). On 28-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 21 | Localised areas of high loading | Continue to implement load plans. | Corrected | Mar 1 2016 | On 25/08/2015: Presently found the loading below 30 psf after approval of DEA they should follow final load plan. On 17/02/2016:After approval of DEA, factory shall follow the final load plan. However, load plan have observed at 1st floor & roof only, At 2nd & 1st floor load was found around 42 psf.Factory requires to maintain the load below 42 psf before approval of DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: Load plan has been produced as a part of DEA which was accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Load pan found posted. Load was found below allowable load limit. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. Factory should follow final loading plan. On 21/10/2018: Corrected in previous follow up inspection. High loading was not found during inspection. Overall loading was found below 42 psf. Factory had carried out revised Detail Engineering Assessment(DEA). DEA had been re-accepted on 07/02/2017 by Accord. Load plan was found posted. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. During inspection, accepted load plan was found posted on every floor and live load was found below 2 kPa (allowable 2 kPa, 3 kPa and 4 kPa). On 21-Sep-2023: This issue was corrected from previous inspection. Load plan has been produced along with DEA report. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on16 October 2022 by RSC. As per accepted DEA recommendation, strengthening work was complete. During inspection, accepted load plan was found posted on every floor and live load was found below allowable limit (2kPa for Typical, 3kPa for dinning & 4kPa for stair). On 28-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 22 | Localised areas of high loading | Complete modifications required from DEA | Corrected | Mar 1 2016 | On 25/08/2015: Presently found the loading below 30 psf after approval of DEA they should follow final load plan. On 17/02/2016:After approval of DEA, factory shall follow the final load plan. However, load plan have observed at 1st floor & roof only, At 2nd & 1st floor load was found around 42 psf.Factory requires to maintain the load below 42 psf before approval of DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: Load plan has been produced as a part of DEA which was accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Load pan found posted. Load was found below allowable load limit. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. Factory should follow final loading plan. On 21/10/2018: Corrected in previous follow up inspection. High loading was not found during inspection. Overall loading was found below 42 psf. Factory had carried out revised Detail Engineering Assessment(DEA). DEA had been re-accepted on 07/02/2017 by Accord. Load plan was found posted. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. (See Item-44). On 21-Sep-2023: This issue was corrected from previous inspection. Factory has carried out revised Detail Engineering Assessment(DEA). DEA of Building 1 was re-accepted on 16 October 2022 by RSC. As per accepted DEA recommendation, strengthening work was completed. On 28-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 23 | Damage to structural elements | As part of DEA outlined in Item 1, all damage (cracking, damage to concrete cover zone, damage to beams at location of movable cranes etc.) to slabs, beams and columns to be identified. | Corrected | Mar 1 2016 | On 25/08/2015: Cover in DEA and DEA is under review. Without approval of DEA the factory should not start any remedial or strengthening works On 17/02/2016:Factory requires to implement any strengthening works after approval of DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory shall revised DEA within 1st March,2016..Previous timeline was 31-Jan-2015 On 20/12/2016: DEA has been submitted and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: As per factory engineer recommendation damage structural elements were repaired. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. On 21/10/2018: Corrected in previous follow up inspection. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. On 21-Sep-2023: This issue was corrected from previous inspection. As per DEA recommendation damage structural elements were repaired for Building 1. On 28-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 24 | Damage to structural elements | Remedial/strengthening details to be implemented as required by DEA. | Corrected | Mar 1 2016 | On 25/08/2015: Cover in DEA and DEA is under review. Without approval of DEA the factory should not start any remedial or strengthening works On 17/02/2016:Factory requires to implement any strengthening works after approval of DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory shall revised DEA within 1st March,2016..Previous timeline was 31-Jan-2015 On 20/12/2016: DEA has been submitted and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: As per factory engineer recommendation damage structural elements were repaired. Detail as built drawing was incorporated in DEA report. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. On 21/10/2018: Corrected in previous follow up inspection. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. (See Item-44). On 21-Sep-2023: This issue was corrected from previous inspection. As per DEA recommendation, damage structural elements were repaired for Building 1. On 28-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 25 | Damage to structural elements | Complete strengthening/remedial works as required by DEA. | Corrected | Mar 1 2016 | On 25/08/2015: Cover in DEA and DEA is under review. Without approval of DEA the factory should not start any remedial or strengthening works On 17/02/2016:Factory requires to implement any strengthening works after approval of DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory shall revised DEA within 1st March,2016..Previous timeline was 31-Jan-2015 On 20/12/2016: DEA has been submitted and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: As per factory engineer recommendation damage structural elements were repaired. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. On 21/10/2018: Corrected in previous follow up inspection. As per factory engineer recommendation damage structural elements were repaired. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. (See Item-44). On 21-Sep-2023: This issue was corrected from previous inspection. As per DEA recommendation, damage structural elements were repaired for Building 1. On 28-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 26 | Damage to structural elements | Continue to monitor structure for further cracking | Corrected | Mar 1 2016 | On 25/08/2015: Cover in DEA and DEA is under review. Without approval of DEA the factory should not start any remedial or strengthening works On 17/02/2016: Factory requires to monitor & investigate any further cracking. Structural adequacy will be verify through DEA .Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 08-Aug-2014 On 20/12/2016: DEA has been submitted and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: As per factory engineer recommendation damage structural elements were repaired. Detail as built drawing was incorporated in DEA report. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. On 21/10/2018: Corrected in previous follow up inspection. As per factory engineer recommendation damage structural elements were repaired. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. During inspection no further crack was observed. On 21-Sep-2023: This issue was corrected from previous inspection. During inspection no further crack was observed. On 28-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 27 | Canteen portal frame at roof level | As part of DEA outlined in Item 1, Building Engineer to review structural steelwork design, with particular attention to lateral stability of portal frame in both orthogonal directions. | Corrected | Mar 1 2016 | On 25/08/2015: Cover in DEA and DEA is under review. Without approval of DEA the factory should not start any remedial or strengthening works On 17/02/2016:This issue will be covered in DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 31-Jan-2015 On 20/12/2016: DEA has been submitted and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. No discrepancy were found in as built drawings. On 21/10/2018: Corrected in previous follow up inspection. As per factory engineer recommendation structural elements were repaired. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. On 21-Sep-2023: This issue was corrected from previous inspection. DEA has been re-accepted on 7 February 2017 by ACCORD. On 28-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 28 | Canteen portal frame at roof level | Supporting RC slabs, beams and columns to be checked for loads applied due to unreinforced masonry walls. | Corrected | Mar 1 2016 | On 25/08/2015: Cover in DEA and DEA is under review. Without approval of DEA the factory should not start any remedial or strengthening works On 17/02/2016:This issue will be covered in DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 31-Jan-2015 On 20/12/2016: DEA has been submitted and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. On 08/05/2017: Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. No discrepancy were found in as built drawings. On 21/10/2018: Corrected in previous follow up inspection. As per factory engineer recommendation structural elements were repaired. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. (See Item-44). On 21-Sep-2023: This issue was corrected from previous inspection. DEA has been re-accepted on 7 February 2017 by ACCORD. On 28-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 29 | Canteen portal frame at roof level | Carry out remedial works to portal frame as required. | Corrected | Mar 1 2016 | On 25/08/2015: Cover in DEA and DEA is under review. Without approval of DEA the factory should not start any remedial or strengthening works On 17/02/2016:Factory requires to implement remedial works after approval of DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016.Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 31-Jan-2015 On 20/12/2016: DEA has been submitted and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. After approval of revised DEA retrofitting works shall be done. On 08/05/2017: Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. On 21/10/2018: Corrected in previous follow up inspection. As per factory engineer recommendation structural elements were repaired. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. Retrofitting of the roof shed was completed long ago. On 21-Sep-2023: This issue was corrected from previous inspection. DEA has been re-accepted on 7 February 2017 by ACCORD. As per accepted DEA recommendation, strengthening work was completed. On 28-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 30 | Canteen portal frame at roof level | Carry out strengthening of supporting RC structure as required. | Corrected | Mar 1 2016 | On 25/08/2015: Cover in DEA and DEA is under review. Without approval of DEA the factory should not start any remedial or strengthening works On 17/02/2016:Factory requires to implement remedial works after approval of DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016.Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 31-Jan-2015 On 20/12/2016: DEA has been submitted and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. After approval of revised DEA retrofitting works shall be done. On 08/05/2017: Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. As per accepted DEA recommendation, strengthening work was complete. On 21/10/2018: Corrected in previous follow up inspection. As per factory engineer recommendation structural elements were repaired. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 07/02/2017 by Accord. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. Retrofitting of the roof shed was completed long ago. On 21-Sep-2023: This issue was corrected from previous inspection. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 7 February 2017 by ACCORD. As per accepted DEA recommendation, strengthening work was complete. On 28-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 31 | Non-engineered structures within the complex | Building Engineer to commence structural assessment of all sheds and outbuildings within complex. | Corrected | Mar 1 2016 | On 25/08/2015: Cover in DEA On 17/02/2016:This issue will be covered in DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 31-Jan-2015 DEA has been submitted and accepted. But during verification inspection some discrepancy were found in as built drawings. Factory were asked to submit the revised DEA to Accord as soon as possible. After approval of revised DEA retrofitting works shall be done. On 20/12/2016: As per DEA recommendation all the non-engineered structures need to demolished. During inspection one non-engineered structural found. Factory needs to submit the structural assessment of that non engineered structure if not decide to demolish. On 08/05/2017: Factory demolish all non-engineered structure. DEA has been re-accepted on 07/02/2017 by Accord. On 21/10/2018: Corrected in previous follow up inspection. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. All non engineered structures were demolished long ago. On 21-Sep-2023: This issue was corrected from previous inspection. All non-engineered structures were demolished. On 28-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 32 | Non-engineered structures within the complex | Loading on primary structure to be accounted for in DEA. | Corrected | Mar 1 2016 | On 25/08/2015: Cover in DEA and DEA is under review. Without approval of DEA the factory should not start any remedial or strengthening works On 17/02/2016:This issue will be covered in DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016. Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 31-Jan-2015 On 20/12/2016: As per DEA recommendation all the non-engineered structures need to demolished. During inspection one non-engineered structural found. Factory needs to submit the structural assessment of that non engineered structure if not decide to demolish. On 08/05/2017: Factory demolish all non-engineered structure. DEA has been re-accepted on 07/02/2017 by Accord. On 21/10/2018: Corrected in previous follow up inspection. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. All non engineered structures were demolished long ago. On 21-Sep-2023: This issue was corrected from previous inspection. All non-engineered structures were demolished. On 28-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 33 | Non-engineered structures within the complex | Carry out and complete strengthening works to sheds and outbuildings to Building Engineer’s specifications. | Corrected | Mar 1 2016 | On 25/08/2015: Cover in DEA and DEA is under review. Without approval of DEA the factory should not start any remedial or strengthening works On 17/02/2016:Factory requires to implement remedial works after approval of DEA. Factory have submitted DEA. Review mail has sent on 28th January,2016.Factory requires to submit revised DEA within 1st March,2016.Previous timeline was 31-Jan-2015 On 20/12/2016: As per DEA recommendation all the non-engineered structures need to demolished. During inspection one non-engineered structural found. Factory needs to submit the structural assessment of that non engineered structure if not decide to demolish. On 08/05/2017: Factory demolish all non-engineered structure. DEA has been re-accepted on 07/02/2017 by Accord. On 21/10/2018: Corrected in previous follow up inspection. On 1st December 2021 (Post Fire Inspection): Not checked. On 27-Dec-2021: Corrected from previous inspection. On 25-Jan-2022: Corrected previously. On 22-Mar-2022: This issue was corrected in previous follow-up inspection On 29-Nov-2022: Corrected from previous inspection. All non engineered structures were demolished long ago. On 21-Sep-2023: This issue was corrected from previous inspection. Factory had demolish all non-engineered structure. All non-engineered structures were demolished. On 28-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Special | Post Incident | 34 | New issue-1 (Post Fire Inspection): Severe damage and crack to ground floor columns: Columns at ground floor (grid: C-15, 16, 17, 18 and D-15,16) were severely damaged. | The factory must evacuate the column's surrounding area at grid C-16 on all floor levels immediately. All live loads must be removed from the indicated area and cordoned off until the completion of remediation work. | Corrected | Dec 2 2021 | On 1st-December-2021 (Post fire inspection): Severe damage and crack to ground floor columns. The factory must evacuate the column's surrounding area at grid C-16 on all floor levels immediately. All live loads must be removed from the indicated area and cordoned off until the completion of remediation work. On 27-Dec-2021: The factory consultant prepared an immediate props layout & details, and interim floor loading plan which was accepted by the RSC on 9 Dec 2021. As per the accepted interim floor load plan, the factory already evacuated all worker and machineries from the 1st floor level (including mezzanine area) and this floor was completely locked & restricted for general workers. The factory suspended all operations in all floors of the fire affected part (northern part) of the building though interim loading plan allow 20 psf (1kN/m2) live loads. On 25-Jan-2022:Factory received acceptance of prop layout plan and interim load plan for 5-storied building from RSC on 09-Dec-2021. During inspection on 27-Dec-2021 some mismatches were found between accepted prop layout plan and onsite condition. Later factory submitted revised prop layout plan along with fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. As per accepted interim load plan factory evacuated and cordoned off the ground floor & 1st floor (including mezzanine) and maintained load below 20 psf at 2nd, 3rd, 4th floor and roof. Issue remains corrected from previous inspection. On 22-Mar-2022: This issue was corrected in previous follow-up inspection. As per accepted investigation report and remediation plan, factory completed all remediation works therefore maintaining allowable floor loading plan of 42 psf on all floor levels. Issue remains corrected. On 29-Nov-2022: Corrected from previous inspection. Fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. Factory had already completed retrofitting of all beams and columns at fire affected area. At present factory is using all areas of the building as per load plan. On 21-Sep-2023: This issue was corrected from previous inspection. On 28-Sep-2025: Previously corrected. | (Immediate – Now) | Corrected
Special | Post Incident | 35 | New issue-2 (Post Fire Inspection): Severe damage and crack to ground floor columns: Columns at ground floor (grid: C-15, 16, 17, 18 and D-15,16) were severely damaged. | Factory must strictly maintain the live within 2 kPa (42 psf) throughout the rest of the fire-affected area on all floor levels, factory to submit a new load management plan. | Corrected | Dec 2 2021 | On 1st-December-2021 (Post fire inspection): Severe damage and crack to ground floor columns. Factory must strictly maintain the live within 2 kPa (42 psf) throughout the rest of the fire-affected area on all floor levels, factory to submit a new load management plan. On 27-Dec-2021: As per the accepted interim floor load plan, the factory allowed to maintain live loads below 20 psf (1 kN/m2) on all other floors of the fire affected part of the building except 1st floor mezzanine area. However, the factory suspended all operations in all floors of the fire affected northern part of the building. On 25-Jan-2022: Factory received acceptance of prop layout plan and interim load plan for 5-storied building from RSC on 09-Dec-2021. During inspection on 27-Dec-2021 some mismatches were found between accepted prop layout plan and onsite condition. Later factory submitted revised prop layout plan along with fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. As per accepted interim load plan factory evacuated and cordoned off the ground floor & 1st floor (including mezzanine) and maintained load below 20 psf at 2nd, 3rd, 4th floor and roof. Issue remains corrected from previous inspection. On 22-Mar-2022: This issue was corrected in previous follow-up inspection. As per accepted investigation report and remediation plan, factory completed all remediation works therefore maintaining allowable floor loading plan of 42 psf on all floor levels. Issue remains corrected. On 29-Nov-2022: Corrected from previous inspection. Fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. Factory had already completed retrofitting of all beams and columns at fire affected area. At present factory is using all areas of the building. During inspection live load was found below 2 kPa (allowable limit 2 kPa, 3kPa and 4 kPa). On 21-Sep-2023: This issue was corrected from previous inspection. Load plan has been produced along with DEA report. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on 16 October 2022 by RSC. As per accepted DEA recommendation, strengthening work was complete. During inspection, accepted load plan was found posted on every floor and live load was found below allowable limit (2kPa for Typical, 3kPa for dinning & 4kPa for stair). On 28-Sep-2025: Previously corrected. | (Immediate – Now) | Corrected
Special | Post Incident | 36 | New issue-3 (Post Fire Inspection): Severe damage and crack to ground floor columns: Columns at ground floor (grid: C-15, 16, 17, 18 and D-15,16) were severely damaged. | Immediately engage a Consultant to provide prop layout plan and prop details with necessary calculations for installation of props for the damaged structural members where required. Prop design drawings are required to be submitted to RSC that must be installed within three days of receiving acceptance from RSC. | Corrected | Dec 7 2021 | On 1st-December-2021 (Post fire inspection): Immediately engage a Consultant to provide prop layout plan and prop details with necessary calculations for installation of props for the damaged structural members where required. Prop design drawings are required to be submitted to RSC that must be installed within three days of receiving acceptance from RSC. On 27-Dec-2021: The factory consultant prepared an immediate props layout & details, and interim floor loading plan which was accepted by the RSC on 9 Dec 2021. As per the props layout, the factory already installed props for most of the columns. 2 props were not installed for the side columns (grid:D-15,16) and 5 props for the beams (grid: 15-BC, 16-BC, 17-BC, B-15~17). There were many mismatches in the column prop size and thickness for grid-14, 15, 16 &17. Also, mismatches were found in beam props. Anchorage were not done for ground floor props. The factory is required to update the props layout and details and revise the calculation send to RSC along with remedial action. On 25-Jan-2022: Factory received acceptance of prop layout plan and interim load plan for 5-storied building from RSC on 09-Dec-2021. During inspection on 27-Dec-2021 some mismatches were found between accepted prop layout plan and onsite condition. Later factory submitted revised prop layout plan along with fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. During inspection props were found installed satisfactorily as per revised prop layout plan. On 22-Mar-2022: This issue was corrected in previous follow-up inspection. As per accepted fire investigation report & remediation plan(accepted on 5-Jan-2022) ground floor and 1st floor were required to cordoned off(live load 0 psf). And for other floors accepted loading limits were 20 psf. During inspection operation in all floors including ground floor and 1st floor were observed. Loading was observed more than 0 psf in ground floor and 1st floor. Accepted load plans(0 psf for ground floor and 1st floor, 20 psf for other floors) were not posted. However loading was within 20psf from 2nd to top floor. Retrofitting was completed(required only in ground floor). Propos were installed in all floors except ground floor. On 22-Mar-2022: This issue was corrected in previous follow-up inspection. Props were installed previously in all floors. Remediation is completed and props are removed from ground floor. Issue remains corrected. On 29-Nov-2022: Corrected from previous inspection. Fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. Factory had already completed retrofitting of all beams and columns at fire affected area. On 21-Sep-2023: This issue was corrected from previous inspection. Fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. Factory had completed retrofitting of all beams and columns at fire affected area. On 28-Sep-2025: Previously corrected. | (Immediate – Now) | Corrected
Special | Post Incident | 37 | New issue-4 (Post Fire Inspection): Spalling of plaster from column (grid C-14, 15, 16 & 17 at ground floor), spalling of concrete from 1st floor beam (grid C-15~16 & C-16~17) | The factory must immediately engage a Consultant to investigate the spalling of concrete, and damage of steel members. Any safety measures, if required as suggested by the Consultant, must be taken immediately to ensure safety. | Corrected | Dec 7 2021 | On 1st-December-2021 (Post fire inspection): Spalling of plaster from column and spalling of concrete from beam was observed. The factory must immediately engage a Consultant to investigate the spalling of concrete, and damage of steel members. Any safety measures, if required as suggested by the Consultant, must be taken immediately to ensure safety. On 27-Dec-2021: The factory consultant already investigated the distress concrete and steel members, did some testing, collected necessary information but final set of remedial scheme has not submitted to RSC yet. However, the factory is required to submit investigation report with remedial actions to RSC without further delay. On 25-Jan-2022: Factory received acceptance of revised prop layout plan along with fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. On 22-Mar-2022: This issue was corrected in previous follow-up inspection. As per accepted fire investigation report & remediation plan(accepted on 5-Jan-2022) ground floor and 1st floor were required to cordoned off(live load 0 psf). Retrofitting was completed(required only in ground floor columns and 1sf floor beams). Issue remains corrected. On 29-Nov-2022: Corrected from previous inspection. Fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. Factory had already completed retrofitting of all beams and columns at fire affected area. On 21-Sep-2023: This issue was corrected from previous inspection. Fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. Factory had completed retrofitting of all beams and columns at fire affected area. On 28-Sep-2025: Previously corrected. | (Immediate – Now) | Corrected
Special | Post Incident | 38 | New issue-5 (Post Fire Inspection): Spalling of plaster from column (grid C-14, 15, 16 & 17 at ground floor), spalling of concrete from 1st floor beam (grid C-15~16 & C-16~17) | Factory must repair the damaged area as per guidance by factory engineer. | Corrected | Dec 7 2021 | On 1st-December-2021 (Post fire inspection): Factory must repair the damaged area as per guidance by factory engineer. On 27-Dec-2021: The factory consultant is required to submit remedial scheme to RSC. After acceptance of the remedial scheme, the factory must implement the actions immediately. On 25-Jan-2022: Factory received acceptance of revised prop layout plan along with fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. During inspection remediation works were found ongoing. Factory is required to complete all remedial works within given timeline (28-Feb-2022). On 22-Mar-2022: As per accepted retrofitting drawings, factory completed retrofitting work. Retrofitting material test reports and completion certificate were provided after inspection. On 29-Nov-2022: Corrected from previous inspection. Fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. Factory had already completed retrofitting of all beams and columns at fire affected area. On 21-Sep-2023: This issue was corrected from previous inspection. Fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. Factory had completed retrofitting of all beams and columns at fire affected area. On 28-Sep-2025: Previously corrected. | (Immediate – Now) | Corrected
Special | Post Incident | 39 | New issue-6 (Post Fire Inspection): Longitudinal crack on 1st floor beam at grid 15,16 (B to D) | The factory must immediately engage a Consultant to investigate the crack, and damage of steel members. Repair the crack with a suitable method suggest by the factory engineer. | Corrected | Dec 7 2021 | On 1st-December-2021 (Post fire inspection): Longitudinal crack was observed on 1st floor beam. The factory must immediately engage a Consultant to investigate the crack, and damage of steel members. Repair the crack with a suitable method suggest by the factory engineer. On 27-Dec-2021: The factory consultant already investigated the distress concrete and steel members, did some testing, collected necessary information but final set of remedial scheme has not submitted to RSC yet. However, the factory is required to submit investigation report with remedial actions to RSC without further delay. On 25-Jan-2022: Factory received acceptance of revised prop layout plan along with fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. During inspection remediation works were found ongoing. Factory is required to complete all remedial works within given timeline (28-Feb-2022). On 22-Mar-2022: As per accepted retrofitting drawings, factory completed retrofitting work for the cracked beams. Retrofitting material test reports and completion certificate were provided after inspection. On 29-Nov-2022: Corrected from previous inspection. Fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. Factory had already completed retrofitting of all beams and columns at fire affected area. On 21-Sep-2023: This issue was corrected from previous inspection. Fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. Factory had completed retrofitting of all beams and columns at fire affected area. On 28-Sep-2025: Previously corrected. | (Immediate – Now) | Corrected
Special | Post Incident | 40 | New issue-7 (Post Fire Inspection): Buckling and warping of steel column at ground floor (isolated mezzanine floor) | The factory must not use the steel mezzanine floor, and the mezzanine floor area must be cordoned off immediately. | Corrected | Dec 2 2021 | On 1st-December-2021 (Post fire inspection): Buckling and warping of steel column was observed at isolated mezzanine floor. The factory must not use the steel mezzanine floor, and the mezzanine floor area must be cordoned off immediately. On 27-Dec-2021: The mezzanine floor (1st floor level) already been cordoned off. The floor is locked and entry restricted. On 25-Jan-2022: Corrected from previous inspection. During inspection mezzanine floor was found evacuated and entry restricted. On 22-Mar-2022: Corrected from previous inspection The factory demolished the steel mezzanine floor. A new steel mezzanine floor was constructed. Issue remains corrected. On 29-Nov-2022: Corrected from previous inspection. Factory has demolished the fire affected mezzanine and constructed a new mezzanine floor. On 21-Sep-2023: This issue was corrected from previous inspection. Fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. Factory had completed retrofitting of all beams and columns at fire affected area. On 28-Sep-2025: Previously corrected. | (Immediate – Now) | Corrected
Special | Post Incident | 41 | New issue-8 (Post Fire Inspection): Buckling and warping of steel column at ground floor (isolated mezzanine floor) | The factory must immediately engage a Consultant to investigate the damage of steel members. Damaged steel members must be replaced by the suggestion by the factory engineer. | Corrected | Dec 7 2021 | On 1st-December-2021 (Post fire inspection): The factory must immediately engage a Consultant to investigate the damage of steel members. Damaged steel members must be replaced by the suggestion by the factory engineer. On 27-Dec-2021: The mezzanine floor is deflected vertically about 110 mm (4 inch) between grid 14 & 15. Steel column and beam of mezzanine floor is severely buckled, warped and distorted. After completion of immediate propping works for RC building, the factory is required to demolish the mezzanine floor following H&S guidelines. The factory engineer is required to provide necessary H&S guideline to ensure safe demolition of steel mezzanine floor. On 25-Jan-2022: Factory received acceptance of revised prop layout plan along with fire investigation report & remediation plan from RSC on 05-Jan-2022. As per accepted remediation plan factory is required to demolish the mezzanine floor within given timeline (28 February 2022). Currently, the steel mezzanine floor is vacant and additional props have been provided to support the steel mezzanine floor. On 22-Mar-2022: The factory demolished the steel mezzanine floor. A new steel mezzanine floor was constructed. On 29-Nov-2022: Corrected from previous inspection. Factory has demolished the fire affected mezzanine and constructed a new mezzanine floor. On 21-Sep-2023: This issue was corrected from previous inspection. Fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. Factory had completed retrofitting of all beams and columns at fire affected area. On 28-Sep-2025: Previously corrected. | (Immediate – Now) | Corrected
Special | Post Incident | 42 | New issue-9 (Post Fire Inspection): Deflection of steel beam and deck slab at ground floor (isolated mezzanine floor) | The factory must immediately engage a Consultant to investigate the damage of steel members. Damaged steel members must be replaced by the suggestion by the factory engineer. | Corrected | Dec 7 2021 | On 1st-December-2021 (Post fire inspection): Deflection of steel beam and deck slab was observed isolated mezzanine floor. The factory must immediately engage a Consultant to investigate the damage of steel members. Damaged steel members must be replaced by the suggestion by the factory engineer. On 27-Dec-2021: The factory consultant investigated the steel mezzanine floor. Demolition or replacement has not been done yet. On 25-Jan-2022: Factory received acceptance of revised prop layout plan along with fire investigation report & remediation plan from RSC on 05-Jan-2022. As per accepted remediation plan factory is required to demolish the mezzanine floor within given timeline (28 February 2022). Currently, the steel mezzanine floor is vacant and additional props have been provided to support the steel mezzanine floor. On 22-Mar-2022: The factory demolished the steel mezzanine floor. A new steel mezzanine floor was constructed. On 29-Nov-2022: Corrected from previous inspection. Factory has demolished the fire affected mezzanine and constructed a new mezzanine floor. On 21-Sep-2023: This issue was corrected from previous inspection. Fire investigation report & remediation plan which was accepted from RSC on 05-Jan-2022. Factory had completed retrofitting of all beams and columns at fire affected area. On 28-Sep-2025: Previously corrected. | (Immediate – Now) | Corrected
Follow Up Inspection |  | 43 | New issue-10: Loading more than 42 psf (2 kN/m2) on 2nd floor of southern part of the building. | Continue to implement floor loading to all floor of southern part of the building. | Corrected | Feb 15 2022 | .On 27-Dec-2021: During inspection loading more than 42 psf (2kN/m2) was observed in 2nd floor of the southern part of the building. Also, the dining area was used for finishing sections. Also, there many finished goods were piled on the aisles area. The factory is required to remove the additional loading from the 2nd floor and maintain RSC accepted floor loading plan. On 25-Jan-2022: During inspection loading was found below allowable limit (42 psf). Dining area is still being used for finishing section. And finished goods were stacked at aisles area. Factory is required to keep aisles always free from obstacles. On 22-Mar-2022: Loading was found within 42 psf. Dinning area was not being used as storage area. Finished goods were stacked at aisles area. Factory is required to remove finished goods from aisles areas. On 29-Nov-2022: During inspection accepted load plan was found posted at every floor and live load was found below 2 kPa (allowable limit 2 kPa, 3kPa and 4 kPa). On 21-Sep-2023: This issue was corrected from previous inspection. Load plan has been produced along with DEA report. Factory has carried out revised Detail Engineering Assessment(DEA). DEA has been re-accepted on16 October 2022 by RSC. As per accepted DEA recommendation, strengthening work was complete. During inspection, accepted load plan was found posted on every floor and live load was found below 2 kPa (allowable 2 kPa, 3 kPa and 4 kPa). On 28-Sep-2025: Previously corrected. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 44 | New issue -11: Retrofitting of ground floor columns & beams, newly built steel mezzanine floor and distress in existing steel bracing connection was observed. | The factory is required to incorporate all the changes in the Detail Engineering Assessment (DEA) documents and submit to RSC for review. Implement remedial works if required by the DEA. | Corrected As per recommendation of findings 45 we have submitted DEA with all related documents and RSC engineering team has acceptance DEA. Acceptance mail here is attached. | May 3 2022 | On 22-Mar-2022: Factory submitted revised DEA for main building and new steel mezzanine floor. As per review comments factory is required to re-submit revised DEA. Factory is required to carry out remediation works(if required) as per recommendation from accepted DEA. On 29-Nov-2022: DEA of the factory has been re-accepted from RSC on 16 October 2022 (after fire incident). Factory has completed all retrofitting works. However, during inspection discrepancy was observed in both steel Mezzanine-1 and Mezzanine-2. In Mezzanine-1, columns are shifted to original position at end grid (south most). In Mezzanine-2, Web of MB-4 was measured as 150mm instead 175mm. Also, bracing was missing in south west corner. Building engineer is required to survey the onsite condition, update the as-built drawing and analysis report accordingly and submit to RSC for review within 14 days of receiving the report. On 21-Sep-2023: This issue will be covered by DEA. As per verification inspection on 29th November 2022 some discrepancy was observed in both steel Mezzanine-1 and Mezzanine-2. Factory has submitted revised DEA report for steel mezzanine-1 & 2 of ground floor, which was under review for pre-submission. A meeting has been called on 25th September 2023. On 28-Sep-2025: DEA of Mezzanine 1, 2 and 3 was re-accepted form RSC on 25 March 2025. Retrofitting was found completed as per DEA recommendation. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 45 | New issue-12: New steel Mezzanine found at Ground floor (Boiler Area). | Produce as-built drawing and check the structural stability of the structure. Also, implement remediation work if required. | Corrected As per recommendation of findings 45 we have submitted DEA with all related documents and RSC engineering team has acceptance DEA. Acceptance mail here is attached. | Jan 10 2023 | On 29-Nov-2022: During inspection a new separate steel Mezzanine was found inside Ground floor (Boiler Area). Building engineer is required to produce as-built drawing and check the structural stability of the structure. Also, implement remediation work if required. On 21-Sep-2023: This issue will be covered by DEA. Factory has submitted revised DEA report for steel mezzanine of ground floor (Boiler room), which was under review for pre-submission. A meeting has been called on 25th September 2023. Also during inspection, a fire pump room & underground water reservoir was found in premises. Factory is required to review that slab over UGWT is designed to carry the imposed impact load . On 28-Sep-2025: DEA of Mezzanine 1, 2 and 3 was re-accepted form RSC on 25 March 2025. Retrofitting was found completed as per DEA recommendation. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 46 | New issue-13: New Structure: Single storied Wastage Area (900 sft0 & Fire control room and Canopy 1, 2 & 3 (1680 sft total). Lack of lateral stability and as-built drawing. | The building engineer is required to prepare as-built drawings, also check the lateral stability, connection adequacy and member adequacy and submit to RSC for review. | We have already submitted the all documents as per requirement | Nov 20 2025 | On 28-Sep-2025: During inspection, several new structure was found in the factory premises. No design documents and as-built drawings were found on site, also lack of lataral stability was observed in the roof structure. The building engineer is required to prepare as-built drawings, also check the lateral stability, connection adequacy and member adequacy and submit to RSC for review. RPO Comments: On 12-Apr-2026: The documents are currently under RSC’s review. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 47 | New issue-14: New Structure: Wastage area (900 sft0 & Fire control room and Canopy 1, 2 & 3 (1680 sft total). Lack of lateral stability and as-built drawing. | Carryout remedial works if required. | We have already submitted the all documents as per requirement | May 7 2026 | On 28-Sep-2025: After acceptance of the documents, the factory will carry out remedial works if required. RPO Comments: On 12-Apr-2026: The documents are currently under RSC’s review. | (within 6 months) | In Progress

## Fire
Date
12-Apr-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Ripon Knitwear Ltd, Jarun, Konabari, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-04-29
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The generator and boiler rooms on the ground floors are not separated form the south eastern exit discharge by means of fire-rated construction (fire rated doors and unprotected openings). | Separate the boiler, generator from the working areas and egress routes by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | Corrected | May 19 2016 | On 25/09/2017: Corrected as on previous follow ups. On 25/02/2018: Corrected as per previous follow-up. On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 2 | Areas used for combustible storage are not separated by firerated construction. The dedicated storage areas on the 3rd floor (Bonded warehouse, Finished fabrics store), 2nd floor (Accessories store, Knitting section store), 1st floor (Metal free zone) and the ground floor (Godown areas) were not separated by fire-rated construction (unprotected openings and fire rated doors). The transient storage areas on the 3rd floor (Fabrics relaxing area) and 2nd floor (Knitting section) exceeded the permitted limits and was open to the working areas. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Corrected | Jul 25 2016 | On 25/09/2017: Corrected. Transient storage area is not found and store rooms found fire separated. On 25/02/2018: Corrected as per previous follow-up. Note: Factory shall ensure in-process storage area as per recommendation. On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected. On 29/11/2022: Corrected. On 21/09/2023: Corrected. Refer to issue#14. | Within 3 months | Corrected
Initial Inspection |  | 3 | The exit stairs were not separated from work areas on each floor by fire-rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automaticclosing devices tied to the fire alarm system. | Corrected. Now our all Fire doors are closing properly and all fire doors are connected in magnetic nope. | Jul 25 2016 | On 25/02/2018: Fire door installation is on going at mezzanine floor (newly constructed) in stair-2. Fire door has been found open with external source in ground floor. Gap below fire door shall be maintained as per standard. On 21/10/2018: Fire door installation almost done. On 14/07/2019: Fire door installation has been done and interfacing with FACP is going on. On 01/12/2021(Post-fire inspection): Due to fire affected fire doors, the separation was not confirmed in the warehouse area to exit stair. On 22/03/2022: In progress. One fire door newly installed & other affected fire door replacement is ongoing due to fire accident in the warehouse at GF. Moreover some non rated channel were found at 2nd & 1st floor and a desk is on the staircase_3 (N-W side) On 29/11/2022: Non rated channel are sealed at 2nd & 1st floor. New fire door are installed at warehouse after fire accident. Some fire door are not properly working in a few location. On 21/09/2023: Few fire doors are not properly closing with exit stairs. Few fire doors are found tied with rope and external sources. On 28-Jan-2024: Corrected based on site condition. Fire Rated Door has been found interfaced with the FADS and functional properly through out all factory premises. | Within 3 months | Corrected
Initial Inspection |  | 4 | Various penetrations and openings were located in the south western and south eastern exit stair enclosures. Example: On the ground floor, the landing of both the stairs are used to access the storage areas. The south western exit stair enclosure was exposed to the generator room by means of unprotected openings. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | Corrected | Jul 25 2016 | On 25/09/2017: Corrected as on previous follow ups. On 25/02/2018: Corrected as per previous follow-up. On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected as per previous FU. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Refer to the Issue# 24. | Within 3 months | Corrected
Initial Inspection |  | 5 | Egress doors / gates with locking features were found in building exits, along egress routes and in the exit discharges on all floors. All gates/doors were found to be open and unlocked during the inspection. | Remove locking features from all egress doors / gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Feb 17 2016 | On 25/09/2017: Corrected as on previous follow ups. On 25/02/2018: Corrected. On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 6 | Collapsible gates / sliding doors are provided at all building exits, exit stairs and at exit discharges. | Replace all gates / sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | May 25 2016 | On 25/09/2017: Corrected as per previous follow ups. Note: All the glass sliding doors shall be replaced with swing door. On 25/02/2018: Corrected. On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 7 | General storage was located inside the north eastern exit stair enclosures on the 2nd floor and ground floor. | Remove all storage from exit stairs and egress paths. | Corrected | Jul 25 2016 | On 25/09/2017: Corrected as on previous follow ups. On 25/02/2018: Corrected as per previous follow-up. On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 8 | The north and south eastern exit stair doors on the 4th floor did not swing in the direction of egress travel. | Modify the egress door to swing in the direction of egress travel. | Corrected | Jul 25 2016 | On 25/09/2017: Corrected as on previous follow ups. Note: Exit discharge door on stair-3 shall be outward swing and push bar is needed. On 25/02/2018: Corrected as per previous follow-up. Note: Exit discharge door on stair-3 shall be outward swing and push bar is needed. On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected as per previous FU. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 9 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | the factory is ready for full functional T&C for fire alarm & detection system(FADS). | Jun 19 2016 | On 25/02/2018: Factory has informed that installation of the system has been almost completed. Testing and commissioning of the system is pending. On 21/10/2018: Installation almost completed and pending for T&C. On 14/07/2019: Installation almost completed and pending for T&C. On 01/12/2021(Post-fire inspection): The fire alarm and detection system were fully burnt in the warehouse. There was no existence of detectors in the ground floor. On 22/03/2022: In progress. Installation of FADS is ongoing in the warehouse at ground floor. Other floor installation are completed. On 29/11/2022: Pre-T&CVI found that FADS is not ready for full T&CVI. See the details Pre-T&CVI report. On 21/09/2023: Full T&CVI of FADS has been conducted. Final verification is required. For details, see the T&CVI report. On 15/11/2023: Final verification inspection (FVI) of FADS found that system is approved. For details, see the FVI report. On 28-Jan-2024: Corrected on previous inspection. FACP has been found functional. | Design within 4 months, install within 9 months. | Corrected
Initial Inspection |  | 10 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Remove single-station smoke alarms. Provide automatic smoke detection through out the building in accordance with NFPA-72. | Corrected | Jun 19 2016 | On 25/09/2017: Corrected as per previous follow ups. On 25/02/2018: Corrected as per previous follow-up. However, it is an integrated part of fire alarm system. On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected as per previous FU. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 11 | Inspection, testing, and maintenance for the fire alarm system was not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | Corrected | Jun 19 2016 | On 25/09/2017: Corrected as on previous follow ups. On 25/02/2018: Corrected as per previous follow-up. On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 12 | Manual on-off switch is provided for emergency lighting units present inside the exit stair enclosures. | Remove manual on/off switches from emergency lighting units to prevent them from being switched off. | Corrected | Feb 17 2016 | On 25/09/2017: Corrected as per previous follow ups. Shall be removed from all emergency lights and exit signs. On 25/02/2018: Issue is reopened as a new finding (Issue no: 21). On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 13 | Inspection, testing, and maintenance records for the emergency lighting system were not available. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | Corrected | Jul 25 2016 | On 25/09/2017: Corrected as on previous follow ups. On 25/02/2018: Corrected. On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 14 | New Finding: Storage rooms used for combustible storage were not separated by fire-rated construction on the several floors(Unprotected penetrations & openings, non-rated doors). | Provide dedicated storage rooms separated by minimum1-hr fire-rated construction. | "Corrected. Now our all process storage management are properly keeping at ground floor. " | May 30 2016 | On 25/09/2017: Corrected as on previous follow ups. On 25/02/2018: Corrected as per previous follow-up. On 21/10/2018: Corrected. On 14/07/2019: Issue has been reopened. Location: 1st floor. On 22/03/2022: Improper store management were found at first & ground floor. On 29/11/2022: Corrected. Maintaining. On 21/09/2023: Improper in-process storage management were found at ground floor. On 28-Jan-2024: Progress has been observed but not corrected yet. In process storage has been found on ground floor in few location. Moreover, Storage room has been found not separated from exit discharge yet (Stair-3). RPO Comments On 22-APR-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Follow Up Inspection |  | 15 | New Finding: The day-care room is located in the 3rd floor does not the direct access to an exit stair. | Relocate day-care room to ground floor with a maximum travel distance of 9 meter (30 feet). Or Relocate to first floor where direct access to an exit enclosure is provided. | Corrected | Jul 25 2016 | On 25/09/2017: Corrected as on previous follow ups. On 25/02/2018: Corrected as per previous follow-up. On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Within 3months | Corrected
Follow Up Inspection |  | 16 | New Finding: The building has an occupied floor greater than 10 meter (33 feet) and its not provided with standpipe system as per NFPA 14 & 20. | Provide standpipe and hose system as per NFPA 14 & 20. | Corrected, Installation Stand pipe and hose system has completed | Jun 25 2016 | On 25/02/2018: Civil work is on going for water reservoir and fire pump room. Factory has informed that they will complete installation of the system within April, 2018. By RCCH: On 05/05/2018: Factory Asking the final time line 30-June-2018. Time extension is not accepted. Corrective action plan should be completed as per Accord's required remediation or safety findings with immediate concern. On 21/10/2018: Installation work is on going. On 14/07/2019: Pending for T&C On 22/03/2022:In progress. Installation of SUPS is ongoing in the warehouse at ground floor. Other floor installation are completed. On 29/11/2022: Pre-T&CVI found that SUPS is not ready for full T&CVI. See the details Pre-T&CVI report. On 21/09/2023: Pre-T&CVI has been conducted and found that SUPS is ready for full T&CVI. See the details in Pre-T&CVI report. On 15/11/2023: T&CVI of fire protection system found that the system is approved. For details, see the T&CVI report. On 28-Jan-2024: Corrected on previous inspection. System has been found functional. | Within 2 months (for design submission) & Within 4 months (for installation). | Corrected
Follow Up Inspection |  | 17 | New Finding (3rd Follow Up): Building did not have stair designation signs and occupant load signs at required locations. | Provide stair designation signs and occupant load signs at required locations. | Corrected, Now we have made proper drainage system in pump room. | Apr 28 2016 | On 25/09/2017: Corrected as on previous follow ups. On 25/02/2018: Corrected as per previous follow-up. On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 18 | New Finding (3rd Follow Up): Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected | May 25 2016 | On 25/09/2017: Corrected as on previous follow ups. On 25/02/2018: Corrected as per previous follow-up. On 21/10/2018: Corrected. On 01/12/2021(Post-fire inspection): The emergency light unit was fully burnt in the warehouse area. On 22/03/2022: In progress. Emergency light installation is ongoing in the ware house at ground floor. Other floors installation are completed. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 19 | New Finding (3rd Follow Up): Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records on-site, in accordance with NFPA 10. | Corrected | May 25 2016 | On 25/09/2017: Corrected as on previous follow ups. On 25/02/2018: Corrected. On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 20 | New Finding: Parapets or guards are provide in occupiable roof does not meet Accord Standard. | Provide parapets or guards with a minimum height of 1067mm (42 inch.). | Corrected | Oct 25 2017 | On 25/09/2017: New Finding. On 25/02/2018: Corrected. Parapet height has been found 42 inch. On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 21 | New Finding (9th Follow Up): Manual on-off switch is provided for [emergency lighting / exit signage] units. | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. | Corrected | Mar 25 2018 | On 25/02/2018: New Finding On 21/10/2018: Corrected. On 14/07/2019: Corrected. On 22/03/2022: Corrected. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 22 | New Finding (9th Follow Up): Storage located in the dining area. | Remove storage from the dining area. | Corrected | Mar 4 2018 | On 25/02/2018: New Finding On 21/10/2018: Not corrected, On 14/07/2019: Dinning area shall be separated from other area. On 22/03/2022: Partially Corrected. Dining area are properly separated. But Prayer area are not separated from storage at 4th Floor. On 29/11/2022: Corrected. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. Not found. | Within 1 week | Corrected
Special | Post Incident | 23 | New Finding (Post-Fire Inspection): The exterior exit is not separated from the building in west exit ground floor. | Exterior exit shall be separated by minimum 2-hr fire-rated construction and the rating of the exterior wall shall extend 3.05 m (10 ft.) beyond the end of the exit structure. Provide minimum 2-hr fire rated doors to separate the exit from work areas. Ensure that the fire doors are self-closing, positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. | Corrected | Feb 20 2021 | On 01.12.2021: New Finding On 22/03/2022: In progress. Civil work is ongoing after fire accident. On 29/11/2022: Corrected. Sealed. On 21/09/2023: Corrected. On 28-Jan-2024: Corrected. | Within 2 months | Corrected
Special | Post Incident | 24 | New Finding (Post-Fire Inspection): The fire pump installed below grade is not provided with adequate drainage of escaping water away from critical equipment such as the pump, driver, controller, and so forth. | Provide the below grade fire pump room with a properly sized underground sump tank (relative to fire pump room or pump house) and properly sized automatic sump pump with hard piped drainpipe to discharge water to a frost-free location. quantity does not meet the system requirements. | Corrected, Installation Stand pipe and hose system has completed | Feb 20 2021 | On 01.12.2021: New Finding On 22/03/2022: Adequate drainage system are not started yet. On 29/11/2022: It is integrated part of protection system On 21/09/2023: It is an integrated part of fire protection system. On 15/11/2023: T&CVI of fire protection system found that the system is approved. For details, see the T&CVI report. On 28-Jan-2024: Corrected on previous inspection. Fire Pump has been found functional. | Within 2 months | Corrected
Special | Safety Complaint | 25 | New Finding (OSH Inspection On 08/02/2023 ): Cartons and finished goods were observed on aisles on several floors including 1st floor. Also, storage was observed in west-middle exit stair (stair-2) enclosure on the 4th floor & ground floor of the building. | Remove all storage from aisles, exit stairs and egress paths. | Corrected, Now we have made proper drainage system in pump room. | Feb 19 2023 | On 08/02/2023: During inspection storages (Cartons & finished goods) were observed on aisles on several floors including west-middle exit stair enclosure on 4th & ground floor respectively. On 27/03/2023: During inspection storages (Cartons, fabric, work station and finished goods) were observed on aisles on several floors including 1st floor. Also, storage was observed in west-middle exit stair (stair-2) as well as north exit stair enclosure on the several floors including 4th floor & ground floor of the building, storage also observed in prayer room (previously it was dining). On 21/09/2023: Corrected. No storages (Cartons, fabric, work station and finished goods) were found on aisles, exit stair enclosures and prayer room during the inspection. On 28-Jan-2024: Corrected. Factory shall ensure that 36 inch clear width of aisle has been maintained on 3rd Floor. | Immediately | Corrected
Follow Up Inspection |  | 26 | New Finding (14th Follow Up): Directional signs are not provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious at all floors in main production building. | Directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious. | Corrected. Direction sign are provided properly to all section of production building. | Nov 10 2023 | New Finding (On 21/09/2023) On 28-Jan-2024: Corrected as per site condition. Directional Exit Signs has been provided. | Within 1 month | Corrected
Follow Up Inspection |  | 27 | New Finding (15th FUI): Unsealed penetrations and openings are located in the exit stair enclosures. Location: Several floor of Stair-1 and 3. | Seal all penetrations and openings in exit stair enclosure by 2Hr fire rated separation by fire rated material | Corrected we have removed all unsealed penetrations and opening from exit in stair-1 and 3 | Feb 28 2024 | On 28-Jan-2024: New Finding. RPO Comments On 22-APR-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification

## Electrical
Date
12-Apr-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Ripon Knitwear Ltd, Jarun, Konabari, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-04-29
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Main LT service cables not supported. | Install covered cable tray (supported on wall) to support the main service cables from pole mounted distribution transformer to LT metering panel in order to protect the cables’ insulation from any physical damage. Ensure the insulation of the cable does not get damaged during installation work. | Corrected | May 31 2016 | On 17/02/2016: Not corrected. New timeline given till 30/03/2016 to close this issue. On 19/04/2016: Not corrected. New committed timeline is given till 31/05/2016. On 21/08/2016: Not Corrected. On 31/10/2016: Not corrected. On 20/12/2016: Not Corrected Factory Asking the final time line: 28/02/2017.Time extension is not accepted. Corrective action plan should be completed as per Accord's recommendation with immediate concern. On 08/05/2017: Corrected. All previous LT service cables have removed. | Within 3 months | Corrected
Initial Inspection |  | 2 | Inadequate safety clearance (setback) of building edges from 11kV overhead line. | Sufficient clearance between the HT over head line and building must be maintained. | Corrected | May 31 2016 | On 17/02/2016: Not corrected. New timeline given till 30/03/2016 to close this issue. On 19/04/2016: Not corrected. New committed timeline is given till 31/05/2016. On 21/08/2016: Not Corrected. On 31/10/2016: Not corrected. On 20/12/2016: Not Corrected Factory Asking the final time line: 28/02/2017 Time extension is not accepted. Corrective action plan should be completed as per Accord's recommendation with immediate concern. On 08/05/2017: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 3 | Protective device(s) mounted on wall without enclosures. | Protective devices should be encased in metal casing made of 20 SWG thickness metal sheets. | Corrected | Aug 8 2014 | On 25/08/2015: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 4 | Gland holes in cable base plates left open. | Provide cable gland according to the respective cable size for cable entry and exit so that the cables are not stressed on the sharp edges of the hole of panels. Provide covers (of non-combustible material) if any additional gap remains after installing cable glands. | Corrected | Aug 8 2014 | On 25/08/2015: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 5 | Panel base plates removed to allow cable entry. | Panel base-plate must be installed. Make circular hole at the base-plate of panels and provide cable gland according to the respective cable size for cable entry and exit so that the cables are not stressed on the sharp edges of the hole of panels. Provide covers (of non-combustible material) if any additional gap remains after installing cable glands. | Corrected | Aug 8 2014 | On 25/08/2015: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 6 | Burnt sign visible at terminal(s) inside panel. | Remove the burnt cable connector from the panel; install proper sized and good quality cable connector according to the connected cable size. Periodic inspection is needed to identify all the loose connection and tighten up all the connections. Overloading may be one of the causes. | Corrected | Aug 8 2014 | On 25/08/2015: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 7 | Excessive cables arranged haphazardly inside panel. | Wires terminating to devices inside panel must be connected firmly and wires approaching devices must be securely fastened to avoid unintentional contact with live parts. Install slotted wiring duct to latch the cable inside the duct. | Corrected | Aug 8 2014 | On 25/08/2015: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 8 | Barrier/ separators between different phases are not installed. | Install separators between different phases of MCCB to avert flashover. Standard separators provided by the MCCB manufacturer must be used. | Corrected | Aug 8 2014 | On 25/08/2015: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 9 | Multiple cables connected at a terminal of the bus bar. | Remove all the multiple connections made at a single point of bus bar and connect individual branch cables to individual points on bus bar using individual lug according to the respective cable size. | Corrected | Aug 8 2014 | On 25/08/2015: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 10 | Panel door not connected with earth bond. | Provide earth connection for body and doors of metallic distribution boards using green cables preferably braid so that the metallic door remains at zero potential all the time. | Corrected | Aug 8 2014 | On 25/08/2015: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 11 | Panels not securely fixed to the foundation. | Panel must be securely fixed with the foundation, using appropriate (in-flammable) material. | Corrected | Aug 8 2014 | On 25/08/2015: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 12 | Excessive dust, lint and cobwebs found in cable trench. | Disconnect the power source of the cable laid into channel and clean dust and debris, combustible material of all interior components. Establish a periodic cleaning program and maintain records of the activities. | Corrected | Aug 8 2014 | On 25/08/2015: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 13 | Excessive dust, lint and cobwebs found in cable duct. | Disconnect the power source of the cable laid into channel and clean dust and debris of all interior components. Establish a periodic cleaning program and maintain records of the activities. Provide cover made of non-combustible material on the channel for preventing ingress of dust and debris in future. | Corrected | Oct 15 2015 | On 17/02/2016: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 14 | Flexible PVC conduit wiring not supported. | Use covered cable duct/ladder to support the cable at bottom of the panel. Flexible conduit must not be used for long point wiring (except for special wirings).Use industrial graded flexible pipes instead of using normal flexible pipes (if required). | Corrected | Oct 15 2015 | On 17/02/2016: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 15 | New Finding: Cables passing through wall/ floor slab are not protected at the entry/exit point(s) | Cables passing through permanent wall/floor slab must be protected. Seal the opening by fire rated material protecting power cables thus no smoke can pass through this | Corrected | Jun 25 2016 | On 17/02/2016: Not corrected. New timeline given till 30/03/2016 to close this issue. On 19/04/2016: Not corrected. New committed timeline is given till 31/05/2016. On 21/08/2016: Not Corrected. On 31/10/2016: Not Corrected. On 20/12/2016: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 16 | New Finding: Cable in store room / storage areas is uncovered. | Cable in store room / storage areas shall be covered | Corrected | Oct 15 2015 | On 17/02/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 17 | New Finding: Inadequate working clearance around the generators | Working clearance around each generator should be 1.07m. If multiple generators are installed then the gap between two generators must be equal to the width of bigger generator. | Corrected | Mar 30 2016 | On 17/02/2016: Not corrected. New timeline given till 30/03/2016 to close this issue. On 19/04/2016: Corrected. Mentioned generator has been removed from this location. | 3 Months | Corrected
Follow Up Inspection |  | 18 | New Finding: Generator body has been earthed by inadequate /improper sized (type) cable | Ensure minimum two earthing connection for generator body (consult with your generator supplier). | Corrected | Mar 30 2016 | On 17/02/2016: Not corrected New timeline given till 30/03/2016 to close this issue. On 19/04/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 19 | New Finding: Cables in service are joined (splicing) between terminations. | Existing cables with joints must be spliced using butt splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. | Corrected | Mar 30 2016 | On 17/02/2016: Not corrected New timeline given till 30/03/2016 to close this issue. On 19/04/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 20 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals | Corrected | Jun 25 2016 | On 17/02/2016: Not corrected. New timeline given till 30/03/2016 to close this issue. On 19/04/2016: Not corrected. New committed timeline is given till 31/05/2016. On 21/08/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 21 | New Finding: LAN Cables & power cables use same cable tray | Make a separation between LAN and power cable either by using separate tray/ladder or in the same tray keep distance between them as much as possible. Even you can use separate conduit only for earth cable in the same cable tray | Corrected | Nov 11 2015 | On 17/02/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 22 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/ undersize | Resize earth lead cable/ECC for LT panel/MDB/DB; follow BNBC 2006 Part 8 chapter 2 section 2.8 for sizing your earthing cables (Usually ECC should be equal to the half of the respective phase cable). | Corrected | Nov 18 2015 | On 17/02/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 23 | New Finding: Power cables are bent excessively | Avoid power cable bending in electrical system; in unavoidable case bend cables without any stress but not less than 135 degree. | Corrected | Oct 16 2015 | On 17/02/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 24 | New Finding: Lightning Protection System (LPS) drawing is unavailable | Design LPS as built and share with Accord to get information any necessary modification | Corrected | Aug 25 2016 | On 17/02/2016:Not corrected New timeline given till 30/03/2016 to close this issue. On 19/04/2016: LPS drawing is available but need few modification. New committed timeline is given till 31/05/2016. On 21/08/2016: Corrected. | 4 Months | Corrected
Follow Up Inspection |  | 25 | New Finding: Insulation resistance test of electrical cables is not performed | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off) | Corrected | Apr 30 2016 | On 17/02/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 26 | New Finding: Earth Pit resistance record is unavailable | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. | Corrected | Jun 25 2016 | On 17/02/2016: Factory has inadequate earthing system. New timeline given till 30/04/2016 to increase the no of earth pit and overall earthing system for the whole factory. On 19/04/2016: Not corrected. New committed timeline is given till 31/05/2016. On 21/08/2016: Not Corrected. On 31/10/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 27 | New Finding: Thermal inspection record is unavailable. | Thermal inspection is needed to be conducted and recorded bi-annually (at least twice a year). Record/Ask for the calibration certificate of the scanner. | Corrected | May 25 2016 | On 17/02/2016: Although thermal inspection conducted, but no records found against the rectification of hot points. New timeline given till 10/03/2016 to close this issue. On 19/04/2016: Not corrected. New committed timeline is given till 31/05/2016. On 21/08/2016: Not Corrected. On 31/10/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 28 | New Finding: Electric safety training program is not initiated/ conducted. | Electrical safety training and awareness program for the electrical personal and workers must be initiated and recorded | Corrected | May 31 2016 | On 17/02/2016: Not corrected. New timeline given till 30/03/2016 to close this issue. On 19/04/2016: Not corrected. New timeline given till 31/05/2016 to close this issue. On 21/08/2016: Not Corrected. On 31/10/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding: Battery terminals are filled with rust and left open. | Clean battery terminals and Use insulated rubber cap to cover all the battery terminals | Corrected | Mar 30 2016 | On 19/04/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 30 | New Finding: Indicator lamps and other loads connected without protection | Provide fuse or circuit breaker for individual lamp and load. | Corrected | Jun 25 2016 | On 19/04/2016: Not corrected. New committed timeline is given till 31/05/2016. On 21/08/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 31 | New Finding: Light in store room / storage areas is uncovered. | Lights in store room / storage areas shall be covered | Corrected | May 25 2016 | On 19/04/2016: Not corrected. New committed timeline is given till 31/05/2016. On 21/08/2016: Corrected. | 1 Months | Corrected
Follow Up Inspection |  | 32 | New Finding: Magnetic ballast in cable channel | Remove the ballast from the cable channel and install it in a safe location. | Corrected | May 25 2016 | On 19/04/2016: Not corrected. Factory is working on this issue. New committed timeline is given till 31/05/2016. On 21/08/2016: Not Corrected. On 31/10/2016: Not corrected. Cable duct is not covered. On 20/12/2016: Corrected | 1 Months | Corrected
Follow Up Inspection |  | 33 | New Finding: Circuit breaker rating is not identifiable. | Replace the old breaker with a new one so that anyone can know the ampacity of the breaker. | Corrected | Apr 30 2016 | On 19/04/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 34 | New Finding: Light and power socket powered by same circuit. | Light and power socket shall be powered by separate protection. | Corrected | May 31 2016 | On 19/04/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 35 | New Finding: Bus bar and nut, bolt. Washer are rusted. | Factory shall clean the rusted bus bar and replace all rusted nut-bolt by good one. | Corrected | May 31 2016 | On 19/04/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 36 | New Finding: Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. Power cable must be distributed through cable trench. Cable trench must be covered properly. | Corrected | Jan 30 2017 | On 20/12/2016: Not Corrected. New committed time line is given till 30/01/2017 to close this issue. On 08/05/2017:Not Corrected. On 25/09/2017: Not corrected. Work is pending in a few places. On 25/02/2018:Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: 1. Distribution Board's top/bottom is left open (typical issue). 2. Oversized circuit breakers or Circuit breakers are not adjusted accordingly. | 1. Seal each distribution board's top/bottom; and use cable glands holding/supporting cables. 2. Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals | Corrected | Jan 30 2017 | On 20/12/2016: Not Corrected. New committed time line is given till 30/01/2017 to close this issue. Factory Asking the final time line: 28/02/2017 Time extension is not accepted. Corrective action plan should be completed as per Accord's recommendation with immediate concern. On 08/05/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. | Amend Electrical SLD properly. Mention all required information by qualified engineer and get it reviewed by Accord. It shall be an as-built drawing (if currently modified) in the factory. | Corrected | Dec 30 2016 | On 20/12/2016: Not Corrected. On 08/05/2017: Not Corrected. Electrical power cables are not identified properly. On 25/09/2017: Not corrected. Set-point shall be updated for adjustable breaker. On 25/02/2018: Not corrected. Factory is working on this issue. On 21/10/2018: Not Corrected. On 14/07/2019: Not Corrected. Need to add few SDB in the drawing. On 09/02/2021: Not Corrected. No progress observed. On 22/03/2022: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 39 | New Finding: Light in store room / storage areas is uncovered. | Lights in store room / storage areas shall be covered | Corrected | Nov 30 2016 | On 20/12/2016: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: Cables inside distribution board are disorganized. | Cables inside each distribution board shall be well organized. | Corrected | Feb 28 2017 | Time line accepted from 30/01/2017 to 28/02/2017 On 08/05/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Multiple cables connected/ terminated at the bus bar through single cable lug. | Each power cable shall be terminated at bus bar through single cable. | Corrected | Jan 30 2017 | On 08/05/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/ undersize | Earth lead cable/ Earth Continuity Conductor (ECC) shall be resized by half of the phase cable. Cable size shall be selected depending on the CB's response time and phase cables' size. | Corrected | Jan 30 2017 | On 08/05/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation (not less than 3mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) must be ensured. | Corrected | Jan 30 2017 | On 08/05/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: 1. Inadequate working space around transformer for performing maintenance work 2. Panel/ Distribution boxes are inaccessible or cannot be opened to perform any maintenance work. | 1. Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained 2. Each electrical distribution board/panel must be easily accessible. In case of height its top shall not be higher than 2m from base; and door opening shall be at least 90 degree. | Corrected | Jun 10 2017 | On 25/09/2017: 1- Not corrected. 2- corrected. On 25/02/2018: Not corrected. Working space around transformer is inadequate. On 21/10/2018: Not Corrected On 14/07/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Phase barrier/ separators are missing in MCCBs | Phases must be separated by insulator (a rubber type no-flammable materials shall be used for it) | Corrected | Jun 10 2017 | On 25/09/2017: Not corrected. Phase separator provided but do not cover the unexposed busbar. Busbar not insulated. On 25/02/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Substation room has inadequate ventilation | Adequate ventilation must be maintained in sub-station room. Cross/forced ventilation must be ensured. For exhaust fan, the fan diameter must not be less than 18 inch. | Corrected | Jun 10 2017 | On 25/09/2017: Not corrected. Temperature in substation is in excess of 43°C. On 25/02/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected | May 25 2017 | On 25/09/2017: Corrected. Not found. | 2 Weeks | Corrected
Follow Up Inspection |  | 48 | New Finding: 1. Distribution boards have no clear identification markings. 2. List of circuit or SLD of existing circuits are not available on each electrical panel/board. | 1. All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. 2. List of circuit or SLD of respective circuits shall be available for each electrical panel/board. | Corrected | Jun 10 2017 | On 25/09/2017: Not corrected. Panel ID not provided in substation. Wrong voltage level written on HT panel. On 25/02/2018: Not corrected. Factory is working on this issue. On 21/10/2018: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Electrical power cables are not identified properly. | Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables used in the system according to SLD. | Corrected | Nov 25 2017 | On 25/02/2018: Not corrected. On 21/10/2018: Not Corrected On 14/07/2019: Not Corrected. Work in progress. On 09/02/2021: Not Corrected. Identification provided without preparing as built SLD. On 22/03/2022: Corrected | 2 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Periodicity of Thermography survey is not continued. | Thermography survey must be done and recorded at least twice in a year. | Corrected | Oct 25 2017 | On 25/02/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Insulation resistance record (cable information) doesn't match with field. | Field information must be reflected in the record and significantly lower sized cables' record shall be avoided. | Corrected | Oct 25 2017 | On 25/02/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Electric safety training program is not continued. | Electrical safety training and awareness program for the electrical personnel must be initiated. It is a periodic task which factory has to continue to improve overall electrical safety situation for the staffs. | Corrected | Oct 25 2017 | On 25/02/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: Safety program is initiated but has limited/no influence in the factory. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. | Corrected | Aug 14 2019 | On 14/07/2019: New Finding On 09/02/2021: Not Corrected. Adequate training module is not available. On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Corrected | Aug 14 2019 | On 14/07/2019: New Finding On 09/02/2021: Not Corrected. No progress observed. On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding: Unprotected cables terminated at sockets. Power sockets are left hanging without proper support. | Proper protection must be ensured for unprotected cables termination. PVC pipe or metal duct can be used or it. Power socket has to be installed on rigid support/base securely and at minimum 200mm above floor level. | Corrected | Aug 14 2019 | On 14/07/2019: New Finding On 09/02/2021: Not Corrected. No progress observed. On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 56 | New Finding: Periodicity of Transformer Oil Test (dielectric strength, moisture content and flash point) survey is not continued. | Transformer oil test (dielectric strength, moisture, and flash point test for oil) shall be done at least once in a year. If the operation of transformer is 24/7 in the facility twice in a year is a better practice. | Corrected | Mar 15 2021 | On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: Earth Pit resistance record is not available. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be available to the Inspector when required. | Corrected | Mar 15 2021 | On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: Insulation resistance test report of electrical power cables is not available. | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | Corrected | Mar 15 2021 | On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: Thermography scanning report is unavailable. | Thermography survey must be done and recorded at least twice in a year. | Corrected | Mar 15 2021 | On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: Previous test reports (Earthing resistance test, Insulation resistance test, Thermography scanning report) are not available on site. | Factory shall keep all previous test report available on site (at least for last 2 years). | Corrected | Mar 15 2021 | On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Equipment earth cable (for generator) size is inadequate. | At least two separate earth pits shall be ensured for generator; The earth cable size shall be determined according to BNBC or Adiabatic method (considering related factors). Number of earth pits shall be determined by the size of connected earth cable. | Corrected | Mar 15 2021 | On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Generator output cables are not supported properly. | Service cables from generator must be supported at its own breaker's terminal through terminal box base/top plate using proper sized cable glands (metal/PVC).and cable tray. | Corrected | Mar 15 2021 | On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Combustible material and water pot attached with cable tray/channels. | Cable channels/tray must be kept neat and clean; these must be free from combustible material and water pot. | Corrected | Mar 15 2021 | On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 64 | New Finding: Manually operated machines (may have chance to be touched by operator/user) have no earth connection. | Each manually operated machine (may have chance to be touched by user/operator) must have earth connection. Cable selection shall be made per CB response and circuit's power demand. | Corrected | Mar 15 2021 | On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 65 | New Finding: Compressor machine mounted on wheel & is not locked. | Compressor machine mounted on wheel must be anchored or the wheels must be locked to prevent from trolling. | Corrected | Mar 15 2021 | On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 66 | New Finding: Inadequate working space around (or in front of) board/panels and access to the board/panels is obstacles. | At least 1 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel. | Corrected | Mar 15 2021 | On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 67 | New Finding: MCCBs/MCBs are not selected/adjusted per load demand. | All the MCCBs/MCBs must be selected/adjusted as per connected load current; if adjustment is not possible, replacement will be the only way. | Corrected | Mar 15 2021 | On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 68 | New Finding: Inadequate Copper conductor (4.25 mm=14.18 mm2) used as main conductor of Lightning Protection System (LPS) | For class 1 building (below 75 ft), minimum 29 mm2 (6.1 mm or 10 mm x 3 mm) Cu conductor need to use as already mentioned in the drawing. | Corrected | Mar 15 2021 | On 22/03/2022: Corrected | 1 Month | Corrected
Special | Post Incident | 69 | New Finding: Uncovered/PVC pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Corrected | Jan 10 2022 | On 22/03/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 70 | New Finding: Lightning Protection System (LPS) is not installed where the risk index equal or greater than 40 (According to BNBC risk index is 42). | Factory shall design Lightning Protection System (LPS) for the whole factory (where the Risk index is equal or greater than 40). Once LPS is designed properly, installation must be done accordingly. | Corrected Already we have installed LPS System in the Building -2 | Nov 25 2023 | On 28/01/2024: Corrected. | 2 Months. | Corrected

## Boiler
Date
12-Apr-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Ripon Knitwear Ltd, Jarun, Konabari, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2022-07-27
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 9418 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Mar 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 12743 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Mar 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 9418 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Mar 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 12743 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Mar 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 9418 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Feb 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 12743 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Feb 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 9418 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Jan 20 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 12743 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Jan 20 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 9418 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Feb 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 12743 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Feb 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 9418 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Mar 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 12 | BB 12743 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Mar 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 13 | BB 9418 | Boiler's initial registration certificate was not available on-site during the inspection. | Boiler registration certificate from the government authority which was provided after the installation shall be available on-site during the inspection. | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Mar 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 14 | BB 9418 | Inconsistency was observed between makers stamping data & the CIoB provided certificate (renewal) copy for the boiler regarding heating surface. | Information provided in the stamping data and in the CIoB provided certificate shall be consistent. Any alteration shall be approved from the CIoB and a copy to be preserved on site. | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Mar 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 15 | BB 15279 | The boiler room did not have an adequate drainage system for spilt liquids. | An appropriate drainage system for the boiler room directed outside shall be provided. | A suitable drainage system has been installed in the boiler room, through which waste water, blowdown water, and condensate are safely discharged outside. | Apr 6 2026 | Comments on 09-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. RPO Comments On 12-Apr-2026: This item will be verified in the next inspection. | 3 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 16 | BB 15279 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | The existing pressure gauge has been removed, and a new pressure gauge has been installed. The measurement range of the new pressure gauge is twice the maximum allowable working pressure of the boiler and complies with international standards. | Feb 6 2026 | Comments on 12-Apr-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. RPO Comments On 12-Apr-2026: This item will be verified in the next inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 17 | BB 12743 | Salt and scale formation was observed on the waterside. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Feb 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 18 | BB 9418 | Salt and medium scale formation was observed on the waterside (fire tubes and boiler shell) of the boiler. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Feb 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 19 | BB 9418 | The inside of the boiler was found corroded due to inadequate water treatment. | Feed water must be externally or internally treated. The boiler operator should blow down regularly as per the manufacturer’s recommendation. Rapid boiling should be avoided. Shell and end plate thicknesses must be within the allowable limit specified by | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Feb 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 20 | BB 15279 | Salt and scale formation was observed on the waterside (tubes and boiler shell). | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | We will soon conduct a complete cleaning program to remove dirt and scale accumulated in the boiler and related pipelines. For this purpose, we will establish a regular cleaning schedule and maintain proper records of the cleaning activities. We are carrying out regular water treatment to ensure the quality of feed water before it enters the boiler. Timeline is May 30, 2026. | Feb 6 2026 | Comments on 09-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 21 | BB 15279 | The inside of the boiler was found corroded due to inadequate water treatment. | Feed water must be externally or internally treated. The boiler operator should blow down regularly as per the manufacturer’s recommendation. Rapid boiling should be avoided. Shell and end plate thicknesses must be within the allowable limit specified by | We are currently treating the feed water internally, and the treated water is being supplied to the boiler under the supervision of the boiler operator. The thickness of the boiler shell and end plate is within the permissible limits as specified by the manufacturer. | Feb 6 2026 | Comments on 09-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. RPO Comments On 12-Apr-2026: This item will be verified in the next inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 22 | BB 12743 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Feb 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 23 | BB 12743 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Feb 6 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 24 | BB 12743 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We have already applied for the scrapping of boiler registration numbers B.B. 9418 and B.B. 12743 on November 11, 2025.In response to the said application, the Boiler Inspector inspected the above-mentioned boilers on January 25, 2026.During the inspection, he informed us that the registration of both boilers would be cancelled as soon as possible and the boilers would be declared as scrapped. The boiler scrapping application is attached herewith for your kind reference. | Jan 13 2026 | Comments on 09-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification