## Structural
Date
01-May-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | SAMS FASHION LTD, KEOWA PASHIM KHANDA(KOROITOLA), MAWNA, SREEPUR, GAZIPUR, Gazipur, Dhaka
Date of Inspection |  | 2014-06-02
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Inconsistencies between the drawings and the actual as-built conditions of Building 1. | Factory Engineer to survey the actual conditions and revise the drawings. | Done | Jul 25 2015 | On 10/06/2015: All the drawing should be included in Engineering Assessment. Factory authority has engaged consultant to perform Engineering Assessment for building 1. Factory will submit Engineering Assessment report within 25 July 2015 On 03/04/2017: Factory management has submitted revised Engineering Assessment for building 1 to ACCORD on 30th January, 2017. But building 1 is being vertically extended. 1st floor is under construction and the factory management has confirmed verbally that they will extend it up to 2nd floor. Therefore, factory shall submit revised DEA as per BNBC & construction must be stopped till the outcome of revised DEA. On 02/01/2018: As-built drawings have been prepared as part of DEA. Factory has submitted revised DEA to ACCORD on 18/12/2017 which required some more revisions. Factory is required to resubmit revised documents within 07/01/2018. On 02/05/2018: As - Built drawings was prepared as a part of DEA which was accepted by ACCORD on 15 - Feb-2018. During verification inspection, some discrepancies were observed on As- Built drawing. Factory is required to revise the drawings as per verification report and submit to ACCORD. On 03/07/2018: Factory had prepared a set of as built drawing as a part of DEA and got acceptance from ACCORD on 15/02/2018. But during verification inspection dated on 02/05/2018, some discrepancies were observed on the As-Built drawing. The factory was advised to submit revised drawings as per the verification report of Accord. During the inspection, it was found that the factory did not submit the revised drawings to Accord. Factory is required to submit the revise drawing immediately. On 24/11/2018: Factory had submitted the revised as built drawing and DEA report to ACCORD and received review comment on 17/11/2018. As per review comment factory has advised to submit the revised DEA within 2/12/2018. Factory is required to submit the revised DEA by the given timeline. On 17/12/2018: As per last review comments, factory submitted revised DEA with as built drawing which was re-accepted by Accord On 4 Dec 2018, On 31/01/2019: As-built drawing has been prepared along with DEA which was re-accepted on 04/12/2018. Issue remains corrected. On 14/11/2019: This issue was corrected in 7th follow up inspection. As-built drawings were prepared as pert of DEA which was re-accepted from ACCORD on 04/12/2018. On 31-Oct-2024: Corrected previously. On 12-Apr-2026: Previously corrected. | PRIORITY 2 ( WITHIN 6-WEEKS) | Corrected
Initial Inspection |  | 2 | Inconsistencies between the drawings and the actual as-built conditions of Building 1. | Factory Engineer to review design and lateral loads to confirm stability of this building under lateral loading. | Done | Jul 25 2015 | On 10-06-2015: Factory authority has engaged consultant to perform Engineering Assessment for building 1. Factory will submit Engineering Assessment report within 25 July 2015 On 03-04-2017: Factory management shall submit revised DEA as per BNBC & construction must be stopped till the outcome of revised DEA. On 02/01/2018: This issue is required to be covered under DEA. Factory has submitted revised DEA to ACCORD on 18/12/2017 which required some more revisions. Factory is required to resubmit revised documents within 07/01/2018. On 02/05/2018: Factory prepared DEA and submitted to ACCORD which was accepted on 15-Feb-2018. During verification inspection, some discrepancies were observed on As- Built drawing. Factory is required to revise the drawings as per verification report and submit to ACCORD. On 03/07/2018: Factory had conducted DEA and got acceptance from ACCORD on 15/02/2018.During verification inspection dated on 02/05/2018, some discrepancies were observed on the As-Built drawing. The factory was advised to submit revised drawings as per the verification report to Accord. During the inspection, it was found that the factory did not submit the revised drawings to Accord. On 24/11/2018: Factory had submitted the revised DEA report to ACCORD and received review comment on 17/11/2018. As per review comment factory has advised to submit the revised DEA within 2/12/2018. Factory is required to submit the revised DEA by the given timeline. However, factory has completed remedial works as per previously accepted DEA recommendation. On 17-12-2018: As per last review comments, factory submitted revised DEA with as built drawing which was re-accepted by Accord. Factory is required to carry out remedial works as per recommendations from re-accepted DEA. Final time line for completing remedial works was January 6, 2019. Remedial works were found ongoing during inspection. Factory is required to take proper safety measures (including propping) during remedial works. On 31-Jan-2019: DEA was re-accepted on 4th December 2018. As per accepted DEA, factory has completed the remedial works. During inspection, original cylinder test reports performed during retrofitting work were available. On 14/11/2019: This issue was corrected in 8th follow up inspection. DEA of the factory was re-accepted from ACCORD on 04/12/2018. Factory has completed all the remedial works as per recommendation of accepted DEA. On 31-Oct-2024: Corrected previously. On 12-Apr-2026: Previously corrected. | PRIORITY 2 ( WITHIN 6-WEEKS) | Corrected
Initial Inspection |  | 3 | Inconsistencies between the drawings and the actual as-built conditions of Building 1. | Continue to implement load plan. | Done | Mar 20 2018 | On 10-06-2015: Factory authority has engaged consultant to perform Engineering Assessment for building 1. Factory will submit Engineering Assessment report within 25 July 2015 And they are not occupying the 1st & upper floor for production yet. On 03-04-2017: 1st floor is under construction. Load plan shall be incorporated with the revised DEA. Factory management shall submit revised DEA as per BNBC & construction must be stopped till the outcome of revised DEA. On 02/01/2018: Load plan has been prepared as part of DEA. Factory has submitted revised DEA to ACCORD on 18/12/2017 which required some more revisions. Factory is required to resubmit revised documents within 07/01/2018. However, load was found below 42psf. On 07/05/2018: Load plan was prepared as a part of DEA which was accepted by ACCORD on 15/02/2018. During inspection, loading was observed below the mentioned loading limit of before retrofitting load plan(80 psf). Factory will implement after retrofitting load plan after completion of retrofitting. On 03/07/2018: Factory had prepared floor loading plan as a part of DEA and submitted to ACCORD which was accepted on 15-Feb-2018.During the inspection, it was found that floor load was within the allowable limit (80 psf before retrofitting) as per previously accepted DEA dated on 15-February -2018 . The factory is required to maintain the final load plan (after retrofitting) after the completion of retrofitting. On 24/11/2018: Floor loading plan has been prepared as apart of DEA and got acceptance on 15/02/2018.As some discrepancy were found during DEA verification, factory revised the DEA and received review comment on 17/11/2018. Factory is required to submit the revised DEA by the given timeline in review comment. However during inspection floor loading was found below 80 psf. On 17-12-2018: Load was found below 80 psf. Load plan was produced and submitted to Accord. Factory is required to follow final load plan after completing retrofitting works. On 31/01/2019: Load plan has been prepared along with DEA. Factory has completed all the remediation. Final load plan is required to be followed as they have completed remediation. During inspection, floor loading was found below allowable limit of final load plan. On 14/11/2019: This issue was corrected in 8th follow up inspection. Load plan was prepared as part of DEA which was re-accepted from ACCORD on 04/12/2018. Factory has completed all the remedial works as per recommendation of accepted DEA. Factory is now following final load plan (2 kPa). Load was found below the allowable load limit. On 31-Oct-2024: Corrected previously. During inspection, load plan found posted in each floor and loading was found below allowable accepted loading limit (2kPa). On 12-Apr-2026: Previously corrected. | PRIORITY 3 ( WITHIN 6-MONTHS) | Corrected
Initial Inspection |  | 4 | Overall stability system | Request that an engineering assessment of the overall building to be carried out and in particular, stability and foundation aspects should be investigated in detail. | Done | Mar 20 2018 | On 10/06/2015: Factory authority has engaged consultant to perform Engineering Assessment for building 1. Factory will submit Engineering Assessment report within 25 July 2015 On 03/04/2017: Factory management shall submit revised DEA as per BNBC & construction must be stopped till the outcome of revised DEA. On 02/01/2018: This issue is required to be covered under DEA. Factory has submitted revised DEA to ACCORD on 18/12/2017 which required some more revisions. Factory is required to resubmit revised documents within 07/01/2018. On 02/05/2018: This issue was covered in DEA. Factory prepared DEA and submitted to ACCORD which was accepted on 15-Feb-2018. As per accepted DEA, retrofitting is required on columns of the factory building-1 which was not started till inspection date. During verification inspection, some discrepancies were observed on As- Built drawing. Factory is required to revise the drawings as per verification report and submit to ACCORD. On 03/07/2018: During the inspection, recommended retrofitting (columns only) was found completed as per previously accepted DEA dated on 15/02/2018. But some discrepancies were observed on the As-built drawing during verification inspection dated on 02/05/2018. The factory was advised to submit revised drawings and DEA as per the verification report to Accord. During the inspection, it was found that the factory did not submit the revised DEA to Accord. The factory is required to submit the above mentioned revised DEA to Accord within 10 days. On 24/11/2018: Factory had submitted the revised DEA report to ACCORD and received review comment on 17/11/2018. As per review comment factory has advised to submit the revised DEA within 2/12/2018. Factory is required to submit the revised DEA by the given timeline. However, factory has completed remedial works as per previously accepted DEA recommendation. On 17-12-2018: As per last review comments, factory submitted revised DEA with as built drawing which was re-accepted by Accord. Factory is required to carry out remedial works as per recommendations from re-accepted DEA. Final time line for completing remedial works was January 6, 2019. Remedial works were found ongoing during inspection. On 31/01/2019: DEA was re-accepted on 4th December 2018. As per accepted DEA, factory has completed the remedial works. During inspection, original cylinder test (performed during retrofitting works) reports were available. On 14/11/2019: This issue was corrected in 8th follow up inspection. DEA of the factory was re-accepted from ACCORD on 04/12/2018. Factory has completed all the remedial works as per recommendation of accepted DEA. On 31-Oct-2024: Corrected previously. On 12-Apr-2026: Previously corrected. | PRIORITY 2 ( WITHIN 6-WEEKS) | Corrected
Initial Inspection |  | 5 | Reinforcement is left exposed at top level of Building 1. | Remove rust from rebar before further construction. | Done | Feb 4 2015 | On 10-06-2015: Rust has been removed and rust proof paint has been applied to the exposed reinforcements on roof. On 03-04-2017: This issue has been corrected as per 1st follow up inspection. On 02/01/2018: This issue has been corrected as per 1st follow up inspection. Factory has repainted exposed rebars. On 07/05/2018: Corrected previously. Factory painted the exposed rebar. On 03/07/2018: This issue has been corrected in the previous inspection. However, during the inspection, exposed rebars were observed painted. On 24/11/2018: Found corrected from previous follow up inspection. On 17-12-2018: This issue is corrected in previous follow-up inspection. On 31-Jan-2019: Rust proof paint has been provided at exposed rebar. Issue remains corrected. On 14/11/2019: This issue has been corrected as per 1st follow up inspection. Factory has repainted all the exposed rebars. On 31-Oct-2024: Corrected previously. Factory has applied rust proof paint to the exposed reinforcements on roof. On 12-Apr-2026: Previously corrected. | PRIORITY 3 ( WITHIN 6-MONTHS) | Corrected
Initial Inspection |  | 6 | Reinforcement is left exposed at top level of Building 1. | For both durability and serviceability, rust proof paint or any appropriate methods is recommended. | Done | Feb 4 2015 | On 10-06-2015: Rust has been removed and rust proof paint has been applied to the exposed reinforcements on roof. On 03-04-2017: This issue has been corrected as per 1st follow up inspection. On 02/01/2018: This issue has been corrected as per 1st follow up inspection. Factory has repainted exposed rebars. On 07/05/2018: Corrected previously. Factory painted the exposed rebar. On 03/07/2018: This issue has been corrected in the previous inspection. However, during the inspection, exposed rebars were observed painted. On 24/11/2018: Found corrected from previous follow up inspection. On 17-12-2018: This issue is corrected in previous follow-up inspection. On 31-Jan-2019: Rust proof paint has been provided at exposed rebar. Issue remains corrected. On 14/11/2019: This issue has been corrected as per 1st follow up inspection. Factory has repainted all the exposed rebars. On 31-Oct-2024: Corrected previously. Factory has applied rust proof paint to the exposed reinforcements on roof. On 12-Apr-2026: Previously corrected. | PRIORITY 3 ( WITHIN 6-MONTHS) | Corrected
Initial Inspection |  | 7 | No waterproofing material applied at top level. | Factory engineer to inspect water damaged structures and repair with a suitable method. | Done | Jul 25 2015 | On 10-06-2015: Factory authority has engaged consultant to perform Engineering Assessment. Factory will submit Engineering Assessment report within 25 July 2015 On 03-04-2017: No waterproofing material has been applied yet. However, construction of 1st floor of building 1 was going on. On 02/01/2018: Building-1 is under construction. Factory is required to apply waterproofing after completion of construction works. On 07/05/2018: During inspection. no waterproofing membrane observed on roof of B-1. Construction of B-1 1st floor was found completed. On 03/07/2018: During the inspection, there was no waterproofing membrane observed on the roof of building-1. The factory is required to apply waterproofing membrane on the roof of building-1 as per recommendation. On 24/11/2018: Factory has improved the drainage system of roof. During inspection no sign of water ponding was found and no water damage structure was noticed. On 17-12-2018: This issue is corrected in previous follow-up inspection. On 31-Jan-2019: Issue was found corrected from previous follow up inspection. On 14/11/2019: This issue has been corrected as per 6th follow up inspection. During inspection no sign of water ponding was found and no water damage structure was noticed. On 31-Oct-2024: Corrected previously. During inspection no sign of water ponding was found and water proofing membrane was observed on roof. On 12-Apr-2026: Previously corrected. | PRIORITY 3 ( WITHIN 6-MONTHS) | Corrected
Initial Inspection |  | 8 | No waterproofing material applied at top level. | Waterproofing on the roof slub is recommended. Moreover the slab drainage system should be investigated. | Done | Jul 25 2015 | On 10/06/2015: No water proofing materials has been applied yet. Factory authority is suggested to apply it within 25/07/2015. On 03-04-2017: No waterproofing material has been applied yet. However, construction of 1st floor of building 1 was going on. On 02/01/2018: Building-1 is under construction. Factory is required to apply waterproofing after completion of construction works. On 07/05/2018: During inspection. no waterproofing membrane observed on roof of B-1. Construction of B-1 1st floor was found completed. On 03/07/2018: During the inspection, there was no waterproofing membrane observed on the roof of building-1. The factory is required to apply waterproofing membrane on the roof of building-1 as per recommendation. On 24/11/2018: No waterproofing layer was provided on roof. On 17/12/2018: No action has been taken regard this issue. Factory is required to provide water proofing layer on rooftop. On 31/01/2019: Water proofing was not provided. As they will go vertical extension, factory has improved drainage system to avoid water ponding. During inspection, no water ponding was found. On 14/11/2019: Factory has provided water proofing membrane on roof top. During inspection no sign of water ponding was found. On 31-Oct-2024: Corrected previously. During inspection no sign of water ponding was found and water proofing membrane was observed on roof. On 12-Apr-2026: Previously corrected. | PRIORITY 3 ( WITHIN 6-MONTHS) | Corrected
Initial Inspection |  | 9 | No waterproofing material applied at top level. | Mainyain standard of quality control. | Done | Jul 25 2015 | On 10-06-2015: No water proofing materials has been applied yet. Factory authority is suggested to apply it within 25 July 2015. On 03-04-2017: No waterproofing material has been applied yet. However, construction of 1st floor of building 1 was going on. On 02/01/2018: Building-1 is under construction. Factory is required to apply waterproofing after completion of construction works. On 07/05/2018: During inspection. no waterproofing membrane observed on roof of B-1. Construction of B-1 1st floor was found completed. On 03/07/2018: During the inspection, there was no waterproofing membrane observed on the roof of building-1. The factory is required to apply waterproofing membrane on the roof of building-1 as per recommendation. On 24/11/2018: No waterproofing layer was provided on roof. No action has been taken regard this issue. Factory is required to provide water proofing layer on rooftop. On 31/01/2019: Water proofing was not provided. As they will go vertical extension, factory has improved drainage system to avoid water ponding. During inspection, no water ponding was found. On 14/11/2019: Factory has provided water proofing membrane on roof top. During inspection no sign of water ponding was found. On 31-Oct-2024: Corrected previously. During inspection no sign of water ponding was found and water proofing membrane was observed on roof. On 12-Apr-2026: Previously corrected. | PRIORITY 3 ( WITHIN 6-MONTHS) | Corrected
Follow Up Inspection |  | 10 | New finding: Cracks in peripheral load bearing walls in building 2 has been observed in numerous locations. The cracks has been observed in both faces of the walls in several locations. | The causes and recommendations for remediation of the wall crack should be incorporated in DEA. | Done | Jul 25 2015 | On 10-06-2015: Factory Engineer is to investigate cause of cracks and suggest the remedial work. On 03/04/2017: Cracks were repaired but no documentation regarding cause of cracks were found. Some cracks have not been repaired yet. Factory Engineer shall investigate the cause of cracks. On 02/01/2018: Factory has repaired the cracks. But no documentation has been found regarding the reason of cracks and the remedial measures implemented for this purpose. Factory is required to prepare a documentation stating the reason and recommending proper remedial measure. On 07/05/2018: During inspection, some cracks was observed on load bearing wall of B-2. Some repairing work was also observed. But no investigation report was observed. Factory is required to investigate the extent of cracks and carry out remedial works as per engineer's advice. On 03/07/2018: During the inspection, some cracks were observed on the load bearing wall of B-2. Some repairing works were also observed during inspection. But there was no investigation report. Factory engineer is required to investigate the extent of cracks and recommend remediation if any. On 24/11/2018: Factory management has repaired the crack. They also prepared a crack investigation report and found the cracks are non structural. On 31-Jan-2019: Cracks were repaired. Issue remains corrected. On 14/11/2019: This issue has been corrected as per 7th follow up inspection. Cracks were repaired. On 31-Oct-2024: Corrected previously. Cracks were found repaired. On 12-Apr-2026: Previously corrected. | 6 Weeks | Corrected
Follow Up Inspection |  | 11 | New finding 2: Reinforcement is left exposed at the top of building 1 & utility building. | Rust proof paint or any other appropriate method is recommended for both durability and serviceability | Done | Apr 18 2017 | On 03-04-2017: During inspection reinforcement was found exposed on the top floor of building 1 and utility building. 1st floor of building 1 is under construction. On 02/01/2018: Factory has covered the exposed reinforcements at the top of utility building. 1st floor of building 1 is under construction. Factory is required to cover the exposed reinforcements at the top of building 1 after completion of construction works. Presently construction of the building is oh hold. Factory has painted the exposed reinforcements at the top of building 1 for this interval. On 07/05/2018: Corrected from previous inspection. Factory covered the exposed rebar on roof of utility building by cement mortar and painted the exposed rebar of B-1. On 03/07/2018: This issue has been corrected in the previous inspection. During the inspection, exposed rebars on the roof of utility building were observed covered with concrete casting along with plastering. On 24/11/2018: Found corrected from previous follow up inspection. On 17-12-2018: This issue is corrected in previous follow-up inspection. On 31-Jan-2019: Rebars were painted with rust proof paint. Issue remains corrected. On 14/11/2019: This issue has been corrected as per 3rd follow up inspection. On 31-Oct-2024: Corrected previously. Factory has applied rust proof paint to the exposed reinforcements on roof. On 12-Apr-2026: Previously corrected. | 6 Weeks | Corrected
Follow Up Inspection |  | 12 | New Findings-3: No edge protection observed on roof of B-1 | Provide edge protection (railing or parapet wall) on roof to avoid falling hazard on roof | Done | May 23 2018 | On 07/05/2018: During inspection, no edge protection was observed on roof of B-1. Factory is required to provide edge protection (railing or parapet wall) on roof to avoid falling hazard on roof On 03/07/2018: During the inspection, there was no edge protection observed on the roof of B-1. The factory is required to provide edge protection (railing or parapet wall) on the roof to avoid falling hazard. On 24/11/2018: Edge protection has been provided at the edge of roof. On 17-12-2018: This issue is corrected in previous follow-up inspection. On 31-Jan-2019: Issue was found corrected from previous follow up inspection. On 14/11/2019: This issue was corrected as per 6th follow up inspection. On 31-Oct-2024: Corrected previously. Factory has provided parapet wall at the edge of roof. On 12-Apr-2026: Previously corrected. | (Immediate – Now) | Corrected
Follow Up Inspection |  | 13 | New Findings-4: Safety railing was not observed at stair portion from GF to roof of Building-1. | Install safety railing on stair portion to avoid falling hazard | Done | May 23 2018 | On 07/05/2018: During inspection, safety railing was not found installed on stair portion from GF to roof. Factory is required to Install safety railing on stair portion to avoid falling hazard. On 03/07/2018: During inspection, there was no safety railing observed installed on stair portion from GF to roof. Factory is required to install safety railing on stair portion to avoid falling hazard. On 24/11/2018: Safety railing has been provided at stair. On 17-12-2018: This issue is corrected in previous follow-up inspection. On 31/01/2019: Railing has been provided at stair. Issue was found corrected from previous follow up inspection. On 14/11/2019: This issue was corrected as per 6th follow up inspection. On 31-Oct-2024: Corrected previously. Factory has provided railing at the stair portion.. On 12-Apr-2026: Previously corrected. | (Immediate – Now) | Corrected
Follow Up Inspection |  | 14 | New finding-5: Exposed rebar prone to corrosion (Building-1). | Provide rust-proof paint on exposed rebar. |  | May 24 2026 | On 12-Apr-2026: Exposed rebar prone to corrosion (Building-1). Provide rust-proof paint on exposed rebar. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 15 | New finding-6: Dampness on brick walls (Building-1). | Repair dampness with a suitable method. |  | May 24 2026 | On 12-Apr-2026: Dampness was found on brick walls (Building-1). Repair dampness with a suitable method. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 16 | New finding-7: New structure found in factory premises (Compressor & Boiler Room: Single-storied RC structure, area 1000 sft, construction 2017). | Prepare a full set of as-built drawings for (Compressor & Boiler Room) and keep on site for further verification. |  | May 24 2026 | On 12-Apr-2026: New structure found in factory premises (Compressor & Boiler Room: Single-storied RC structure, area 1000 sft, construction 2017). Prepare a full set of as-built drawings for (Compressor & Boiler Room) and keep on site for further verification. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 17 | New finding-8: Nonstructural elements (plastic water tank) without anchorage/bracing (Building-1, Building-2). | Anchor/brace all nonstructural elements, including the plastic water tank. |  | May 24 2026 | On 12-Apr-2026: Nonstructural elements (plastic water tank) without anchorage/bracing (Building-1, Building-2). Anchor/brace all nonstructural elements, including the plastic water tank. | (within 6 weeks) | In Progress

## Fire
Date
01-May-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | SAMS FASHION LTD, KEOWA PASHIM KHANDA(KOROITOLA), MAWNA, SREEPUR, GAZIPUR, Gazipur, Dhaka
Date of Inspection |  | 2014-05-27
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The boiler room is not separated from the working areas ( Finishing section) by means of fire-rated construction (un protected openings and non rated door). The compressior room is not separated from the discharge pathway of the north eastern exit stair by means of fire rated construction ( non rated door). | Separate the boiler & compressor room from the adjacent working area and discharge pathway by a minimum 2-hr fire-rated constructiion. Seal and/or protected all openings to maintain the required fire separations. | Done | Jun 30 2015 | On 14/03/2016: No action has been taken yet for boiler separation or compressor separation. On 12/06/2016: No action has been taken yet. Compressor room in front of exit-2 and boiler inside the production floor are not properly separated by fire rated construction. Factory didn't even open L/C for fire doors yet. On 01-09-2016: No action has been taken yet Factory asked for time extension till 30/06/2017. Time extension is not accepted. On 18.12.2016: Corrected as per site observation. Boiler has been shifted to utility shed which is more than 10 feet away from production building and other occupancies. On 03.04.2017: Corrected as per site observation. On 17/07/2017: Corrected in 5th follow up. On 12/02/2018: Corrected. On 29/07/2018: Corrected as on previous follow ups. On 31/01/2019: Separated On 26/07/2022: Corrected. On 05-Nov-24: Corrected. On 22-Apr-26: Corrected. | within 3 months | Corrected
Initial Inspection |  | 2 | Dedicated storage areas ( Bonded store and finishing goods store) on the ground floor were not separated from the working area by means of fire rated construction (non rated door and unprotected openings). | Provide dedicated storage rooms separated by minimum 1- hr fire -rated construction. | Done | Jun 30 2015 | On 14/03/2016: No action has been taken yet. Fire door order has not been finalized yet. Factory shall open LC for fire doors within committed timeline. On 12/06/2016: No action has been taken yet. Bonded ware house and finish goods store are not properly separated with the production floor. L/C for fire door has not been finalized yet. On 01-09-2016: In progress. Fire has been installed but unprotected opening was found during follow up inspection. Factory asked for time extension till 31/10/2017. Time extension is not accepted. On 18.12.2016: Corrected as per site observation. Civil construction and fire door installation is completed to provide proper fire separation. On 03.04.2017: Corrected as per site observation. On 17/07/2017: Corrected in 5th follow up. On 12/02/2018: Corrected. On 31/01/2019: Separated On 29/07/2018: Corrected as on previous follow ups. On 26/07/2022: Corrected. On 05-Nov-24: Corrected. Bonded ware house and finishing goods store found separated from working area by fire rated construction and fire rated door. Fire rated door has been found functional. On 22-Apr-26: Corrected. | within 3 months | Corrected
Initial Inspection |  | 3 | Transient storage areas (Packing area) on the ground floor are not separated from the adjacent working areas by means of fire rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire rated construction where separate storage rooms are not feasible provide defined storage areas and limit the storage arrangments as follows: Maximum height of 2.4 m and maximum area of 23 m2, if sprinkle protected : Maximum height of 3.66 m and maximum area of 93 m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Done | Dec 31 2014 | On 14/03/2016: During follow-up inspection, in-process goods were not organized as per Accord recommendation. On 12/06/2016: In-process storages were found on the production floor as well as on the means of egress during the 3rd follow-up inspection. Factory shall follow the recommended storage arrangement for in-process storage. On 01-09-2016: It has been found same as before. On 18.12.2016: Corrected as per site observation. Storage was found in compliant way during inspection. On 03.04.2017: Corrected as per site observation. On 17/07/2017: Corrected in 5th follow up. On 12/02/2018: Corrected. On 29/07/2018: Corrected as on previous follow ups. On 31/01/2019: Completed On 26/07/2022: Corrected. On 05-Nov-24: Corrected. On 22-Apr-26: Corrected. | within 3 months | Corrected
Initial Inspection |  | 4 | E Gress doors and gates with locking features are provided at all building exits and exit discharges. | Remove locking features from all egress doors /gates. If locks are required for security rasons, utilize speacial door locking features complying with NFPA 101. | Done | Dec 15 2014 | On 14/03/2016: In progress. During follow-up inspection, locking features were spotted on all exit doors. On 12/06/2016: Locking features were found on the main exits during the 3rd follow-up inspection. On 01-09-2016: Corrected. On 18.12.2016: Corrected as per site observation. On 03.04.2017: Corrected as per site observation. On 17/07/2017: Corrected as per 4th follow up. On 12/02/2018: Corrected. On 29/07/2018: Corrected as on previous follow ups. On 31/01/2019: Removed On 26/07/2022: Corrected. On 05-Nov-24: Corrected. No locking features has been found during the inspection. On 22-Apr-26: Corrected. | Immeadiate | Corrected
Initial Inspection |  | 5 | Collapsible gates and sliding doors are provided at all building exits and exit discharges. | Replace all gates/ sliding doors along the means of egress with side- hinged, swinging egress doors,if locks are required for security reasons, utilize speacial door locking features complying with NFPA 101. | Done | Feb 11 2014 | On 14/03/2016: Corrected. On 12/06/2016: Sliding gate was found at exit-3 during the time of 3rd follow-up inspection. On 01-09-2016: Corrected. On 18.12.2016: Corrected as per site observation. On 03.04.2017: Corrected as per site observation. On 17/07/2017: Corrected in 1st follow up. On 12/02/2018: Corrected. On 29/07/2018: Corrected as on previous follow ups. On 31/01/2019: Replaced On 26/07/2022: Corrected. On 05-Nov-24: Refer to the issue no. 18 On 22-Apr-26: Refer to the issue no. 18. | within 1 month | Corrected
Initial Inspection |  | 6 | The western and north eastern exit stair door does not swing in the direction of egress travel. | Modify the egress door to swing in the direction of egress travel. | Done | Jun 25 2015 | On 14/03/2016: No action has been taken yet. On 12/06/2016: Partially corrected. The western exit door does not swing in the direction of egress. On 01-09-2016: Corrected. On 18.12.2016: Corrected as per site observation. On 03.04.2017: Corrected as per site observation. On 17/07/2017: Corrected in 4th follow up. On 12/02/2018: Corrected. On 29/07/2018: Corrected as on previous follow ups. Stairs shall be separated prior to occupy the 1st floor. On 31/01/2019: Comments same as before On 26/07/2022: Corrected. Stairs shall be separated prior to occupy the 1st floor. On 05-Nov-24: Corrected. Egress door swings in the direction of egress travel. Note: Stair shall be separated by fire rated door prior to occupy 1st floor. On 22-Apr-26: Corrected. The first floor is still unoccupied & entry is restricted. | within 3 months | Corrected
Initial Inspection |  | 7 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | Done | Jun 25 2015 | On 14/03/2016: In progress. Fire Alarm System drawings were not present during follow-up inspection. Factory informed that as-built drawings are being modified and will be submitted to Accord for review. Factory shall submit drawings within committed timeline. On 12/06/2016: No action has been taken yet. Factory didn't even submit the design to ACCORD for review yet. On 01-09-2016: No action has been taken yet On 18.12.2016: Design has been rejected once by Accord but factory management failed to show the rejection letter or any proof of submitting the design to Accord. On 03.04.2017: Design has been submitted to Accord for approval. On 17/07/2017: Only design has been reviewed by Accord. On 12/02/2018: In progress. Design reviewed by Accord. Required euipments L/C order has been placed on 11th February, 2018. On 29/07/2018: Installation will be started soon. On 31/01/2019: T&C has been done and system has found functional. On 26/07/2022: Corrected as per previous follow-up. Note: Fire alarm control panel was not clear of abnormal system conditions. Continuous trouble (supervisory) signal was observed for battery failure. Wiring that enters the fire alarm control equipment is not protected from mechanical damage chaffing. The fire alarm control equipment AC power supply was not locked. On 05-Nov-24: Refer to the issue no. 19. On 22-Apr-26: Refer to the issue no. 19. | Design within 4 months, install within 9 months. | Corrected
Initial Inspection |  | 8 | The building is equipped with single station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupations. | Remove single station smoke alarms. Provide automatic smoke detection through out the building, tied into the fire alarm system, in accordance with NFPA 72. | Done | Feb 11 2014 | On 01-09-2016: No action has been taken yet On 18.12.2016: It is an integrated part of addressable fire alarm system. On 03.04.2017: It is an integrated part of addressable fire alarm system. On 17/07/2017: It is an integrated part of addressable fire alarm system. On 12/02/2018: It is an integrated part of addressable fire alarm system. On 29/07/2018: Installation will be started soon. On 31/01/2019: Removed and installed automatic detectors On 26/07/2022: Corrected. On 05-Nov-24: Corrected. On 22-Apr-26: Corrected. | within 1 month | Corrected
Initial Inspection |  | 9 | Fire protection inspection, testing and maintenance of the fire alarm system is not in accordance with NFPA 72. | Inspect , test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | Done | Dec 31 2014 | On 01-09-2016: It is an integrated part of fire alarm system. On 18.12.2016: It is an integrated part of addressable fire alarm system. On 03.04.2017: It is an integrated part of addressable fire alarm system. On 17/07/2017: It is an integrated part of addressable fire alarm system. On 12/02/2018: It is an integrated part of addressable fire alarm system. On 29/07/2018: Installation will be started soon. On 31/01/2019: Maintaining On 26/07/2022: Corrected as per previous follow-up. On 05-Nov-24: Corrected. On 22-Apr-26: Corrected. | within 3 months | Corrected
Initial Inspection |  | 10 | Inspection, testing and maintenance for the emergency lighting system were not in accordance with the accord standard. | inspect, test and maintain the emergency lighting system in accordance with the accord standard. Keep written records on-site. | Done | Jun 20 2015 | On 14/03/2016: Factory maintains documentation but they are not as per code. Factory shall maintain proper documentation as per code within committed timeline. On 12/06/2016: Factory was unable to show any kind of document regarding ITM. On 01-09-2016: No action has been taken yet On 18.12.2016: No action has been taken yet. On 03.04.2017: Corrected. On 17/07/2017: Corrected in 6th follow up. On 12/02/2018: Corrected. On 29/07/2018: Corrected as on previous follow ups. On 31/01/2019: Corrected as per previous follow-up On 26/07/2022: Corrected as per previous follow-up. On 05-Nov-24: Corrected. On 22-Apr-26: Refer to issue no#20. | within 3 months | Corrected
Initial Inspection |  | 11 | Based on the number and location of emergency lights cbserved, adequate illumination levels are not anticipated along egress routes on the ground floor. | Test the emergency lighting system on each floor and provide additional emergency fixture to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Done | Dec 31 2014 | On 14/03/2016: Corrected. On 12/06/2016: Corrected. On 01-09-2016: Corrected. On 18.12.2016: Corrected as per site observation. On 03.04.2017: Corrected as per site observation. On 17/07/2017: Corrected in 1st follow up. On 12/02/2018: Corrected. On 29/07/2018: Corrected as on previous follow ups. On 31/01/2019: Tested On 26/07/2022: Corrected. On 05-Nov-24: Corrected. On 22-Apr-26: Corrected. | within 3 months | Corrected
Follow Up Inspection |  | 12 | New Finding (2nd Follow-up): Storage (electrical panels and combustible goods) was located under exit stairs. | Remove electrical panels and combustible storage from exit stairs and egress path. | Done | Mar 21 2016 | On 14/03/2016: New Finding On 12/06/2016: No action has been taken yet. On 18.12.2016: No action has been taken yet. On 03.04.2017: No action has been taken yet. On 17/07/2017: Work is in progress although its applicable when factory occupied the 1st floor also stair separation is required at that time. On 12/02/2018: Corrected. (Removed.) On 29/07/2018: Corrected as on previous follow up. Cable trench/riser shall be removed from stair enclosure prior to occupy the 1st floor. On 31/01/2019: Comments same as before On 26/07/2022: Corrected. Cable trench/riser shall be removed from stair enclosure prior to occupy the 1st floor. On 05-Nov-24: Corrected. Note: Cable tray shall be removed from stair enclossure prior to occupy 1st floor. On 22-Apr-26: Corrected. The first floor is still unoccupied & entry is restricted. | Immediately | Corrected
Follow Up Inspection |  | 13 | New Finding (2nd Follow-up): Manual on-off switch is provided for emergency lighting/ exit signage units. | Remove manual on/off switches from emergency lighting/ exit signage units to prevent them from being switched off. | Done | Apr 14 2016 | On 14/03/2016: New Finding On 12/06/2016: No action has been taken yet. On 01-09-2016: No action has been taken yet. On 18.12.2016: Corrected as per site observation. On 03.04.2017: Corrected as per site observation. On 17/07/2017: Corrected in 5th follow up. On 12/02/2018: Corrected. On 29/07/2018: Corrected as on previous follow ups. On 31/01/2019: Removed On 26/07/2022: Corrected. On 05-Nov-24: Corrected. On 22-Apr-26: Corrected. | within 1 month | Corrected
Follow Up Inspection |  | 14 | New Finding (2nd Follow-up): Emergency lighting did not function in test mode (burned out, broken, etc.). | Reguarly test the emergency lighting system and replace/repair lights as needed. | Done | Apr 14 2016 | On 14/03/2016: New Finding On 12/06/2016: Partially corrected. Manual on/off switches were found in one of the emergency exit signage during the follow-up inspection. On 01-09-2016: Manual on off switch was found for emergency lights. On 18.12.2016: Corrected as per site observation. On 03.04.2017: Corrected as per site observation. On 17/07/2017: Corrected in 5th follow up. On 12/02/2018: Corrected. On 29/07/2018: Corrected as on previous follow ups. On 31/01/2019: Completed On 26/07/2022: Corrected. On 05-Nov-24: Corrected. On 22-Apr-26: Corrected. | within 1 month | Corrected
Follow Up Inspection |  | 15 | New Finding (2nd Follow-up): The generator and transformer rooms are not separated by fire-rated construction from the office building (openings/ penetrations). | Separate the generator and transformer rooms by a minimum 2-hr fire-rated construction. Seal and/or protect all openings to maintain the required fire separation. | Done | Jun 14 2016 | On 14/03/2016: New Finding On 12/06/2016: No action has been taken yet. It was found same as it was before. On 01-09-2016: In progress. Factory has sealed most of the unprotected opening in the office building but still few openings were found during follow up inspection. More over diesel storage was found without any proper fire separation. Factory asked for time extension till 30/11/2016.time extension request is not accepted. On 18.12.2016: Corrected as per site observation. No penetration was found during inspection. On 03.04.2017: Corrected as per site observation. On 17/07/2017: Corrected in 5th follow up. On 12/02/2018: Corrected. On 29/07/2018: Corrected as on previous follow ups. On 31/01/2019: Separated On 26/07/2022: Corrected. On 05-Nov-24: Corrected. On 22-Apr-26: Corrected. | within 3 months | Corrected
Follow Up Inspection |  | 16 | New Finding in 3rd Follow-up: Parapets or guards are not provide in occupiable roof | Provide parapets or guards with a minimum height of 1067mm (42 inch.). | Done | Jul 12 2016 | New Finding On 01-09-2016: No action has been taken yet Factory asked for time extension till 31/10/2016.time extension request is not accepted. On 18.12.2016: Corrected as per site observation. 1st floor is under construction and the stair leading to 1st floor was found close during inspection. Factory management informed that they will provide parapets above 1st floor as per standard after 1st floor construction is finished. On 03.04.2017: Corrected as per site observation. On 17/07/2017: Corrected as per 5th follow up. Required when factory occupies the 1st floor. On 12/02/2018: Corrected as per previous inspection. On 29/07/2018: Corrected as on previous follow ups. Both side handrail shall be provided prior to occupy the 1st floor. On 31/01/2019: Completed On 26/07/2022: Corrected. Both side handrail shall be provided prior to occupy the 1st floor. On 05-Nov-24: Corrected. On 22-Apr-26: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 17 | New Finding (6th Follow-Up): Compressor furnace room is not properly separated by fire rated construction from east exit path. | Compressor or other heat producing equipment shall be separated from other occupancies by a minimum 1-hr (2-hr for highrise building) fire rated construction (wall, floor, slab etc). Seal all penetrations and openings (door, window etc.) should be protected by 0.75-hr (45 min) fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. Or Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. | Done | May 3 2017 | On 03.04.2017: NEW FINDING. On 17/07/2017: Found same as before. On 12/02/2018: Corrected. Removed from said location and relocated to a safe location. On 29/07/2018: Corrected as on previous follow up. On 31/01/2019: Separated On 26/07/2022: Corrected. On 05-Nov-24: Corrected. On 22-Apr-26: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 18 | New Findings (12th FUI):Collapsible gates has been provided in the generator room, | Replace all gates/ sliding doors along the means of egress with side- hinged, swinging egress doors,if locks are required for security reasons, utilize speacial door locking features complying with NFPA 101. | For security reasons, the removal of collapsible gates along the means of egress is currently under consideration. We are also reviewing for solution. And, we are request to RSC for consider this issue. | Dec 5 2024 | On 05-Nov-2024: New Findings. On 22-Apr-26: No remediation action has been taken yet. Collapsible, shutter-type doors were observed in the generator, diesel storage, and substation room. | within 1 month | In Progress
Follow Up Inspection |  | 19 | New Findings (12th FUI): Fire alarm control panel has been found in abnormal conditions. Continuous trouble (supervisory) signal has been observed for power failure. This issue will be verified by follow up inspection. | Fire alarm control panel shall be kept in normal condition and free from any trouble. | We are now maintaining for fire alarm control panel. | Feb 5 2025 | On 05-Nov-2024: New Findings. On 22-Apr-26: Battery trouble was observed on the FACP during the inspection. Battery backup was not available, as also reported during the previous inspection. When the AC power was disconnected, the control panel shut down. According to the factory, this issue is related to a power supply failure. The issue must be resolved immediately. System functionality will be verified through T&CVI in the next follow-up inspection to confirm proper operation of the FADS. The factory management shall ensure that the system is fully functional and inform RSC accordingly. | within 3 months | In Progress
Follow Up Inspection |  | 20 | New Finding (13th FUI): Inspection, testing, and maintenance for the fire alarm system are not available in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with NFPA 72 and RSC Technical Guidelines (Standard)¹ V1.0. |  | May 22 2026 | On 22-Apr-26: New Finding. | Within 1month | In Progress
Follow Up Inspection |  | 21 | New Finding (13th FUI): Inspection, testing, and maintenance of portable fire extinguishers is not available on-site in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records on- site, in accordance with NFPA 10 and RSC Technical Guidelines (Standard)¹ V1.0. |  | May 22 2026 | On 22-Apr-26: New Finding. | Within 1month | In Progress
Follow Up Inspection |  | 22 | New Finding (13th FUI): Inspection, testing, and maintenance for the exit sign and emergency lighting system were not available on-site in accordance with the RSC Technical Guidelines (Standard)¹ V1.0. | Inspect, test, and maintain the exit sign and emergency lighting system in accordance with the RSC Technical Guidelines (Standard)¹ V1.0. Keep written records on-site. |  | May 22 2026 | On 22-Apr-26: New Finding. | Within 1month | In Progress

## Electrical
Date
01-May-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | SAMS FASHION LTD, KEOWA PASHIM KHANDA(KOROITOLA), MAWNA, SREEPUR, GAZIPUR, Gazipur, Dhaka
Date of Inspection |  | 2014-09-03
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | 1. As-built electrical SLD, wiring layout designs and drawings, machine layouts are not prepared. 2. Thermo graphic scanning of the entire electrical system has not been performed. 3. Insulation resistance test of electrical equipment is not performed. 4. Electrical safety program is not initiated. | 1. The factory must have As-built electrical SLD with electrical wiring layout designs and drawings. 2. Thermo graphic scanning of the entire electrical system must be performed on tri-annual basis and recorded. 3. Insulation resistant test of all the cables must be performed once every 5 year cycle and recorded. 4. Electrical safety training and awareness program for the electrical personal and workers must be initiated and recorded. | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016. On 12-06-2016: This issue is not corrected. Factory is behind schedule. On 01/09/2016: Not Corrected. Factory asked for time extension till 15/11/2016.Time extension request is not accepted. On 18/12/2016: Not corrected(issue no 1 & 4). On 03/04/2017: Not corrected. On 17/07/2017: Not Corrected. On 12/02/2018: Corrected. | 12 WEEKS | Corrected
Initial Inspection |  | 2 | Silica gel of transformer breather becomes discolored. Also transformer breather’s oil cup empty. | Silica gel in breather must be changed and oil cup must be filled with transformer oil as per the instruction of the manufacturer. | Done | Oct 23 2014 | On 10-06-2015: Corrected. | 3 WEEKS | Corrected
Initial Inspection |  | 3 | No cover on cable trench. | Provide cover made of non-combustible material preferably metallic sheet (checkered plate) to protect the cables' insulation from physical damage as well as prevent ingress of debris, dust and lint. | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016 to close this issue. On 12-06-2016: This issue is not corrected. Factory is behind schedule. On 01/09/2016: Corrected. | 5 WEEKS | Corrected
Initial Inspection |  | 4 | Cables terminated to bus bar without lugs. | Terminate cables to bus bar by using proper sized lugs and punch the lugs by proper hand puncher or hydraulic puncher. Periodic inspection is needed to keep all the contacts tight. | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016 to close this issue. On 12-06-2016: Corrected. | 5 WEEKS | Corrected
Initial Inspection |  | 5 | High earth loop impedance measured. | Check the earthing connection (for loose connections) and rectify as required. | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016 to close this issue. On 12-06-2016: This issue is not corrected. Factory is behind schedule. On 01/09/2016: Corrected. | 3 WEEKS | Corrected
Initial Inspection |  | 6 | Cables passing through wall not protected and supported with remaining gaps around the cable /wiring not sealed. | Cables passing through permanent walls must be protected in steel/PVC pipes and remaining holes around the pipe must be sealed. Seal all the penetrations using appropriate fire rated material and ensure the cable insulation does not get damaged during sealing work. | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016. On 12-06-2016: This issue is not corrected. Factory is behind schedule. On 01/09/2016: Not Corrected. Factory asked for time extension till 25/10/2016.Time extension request is not accepted. On 18/12/2016: Corrected. | 5 WEEKS | Corrected
Initial Inspection |  | 7 | Cable duct installed close to steam lines. | Power cables installed near boiler steam lines must be protected from external heat and moisture (may keeping sufficient clearance between steam pipes and cable/installing adequate thermal-insulation on the steam pipe). | Done | Jul 20 2015 | On 14-03-2016: Corrected. | 12 WEEKS | Corrected
Initial Inspection |  | 8 | Cables terminated to generator output box are directly laid on the floor. | Construct a cable trench to terminate the generator output cables and provide covers made of non-combustible material preferably concrete slab to protect the cables’ insulation from physical damage as well as prevent entering debris, dust and lint. | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016 to close this issue. On 12-06-2016: This issue is not corrected. Factory is behind schedule. On 01/09/2016: Not Corrected. Cables are buried under concrete. On 18/12/2016: Found corrected. | 5 WEEKS | Corrected
Initial Inspection |  | 9 | Generator frame not connected to earth two points. | Generator frame must be connected to earth securely two points. | Done | May 11 2014 | On 10-06-2015: Corrected. | 5 WEEKS | Corrected
Initial Inspection |  | 10 | Cable entry-exit point to the Change-Over-Switch not sealed. | Provide cable gland according to the respective cable size for cable entry and exit so that the cables are not stressed on the sharp edges of the hole of panels. Provide covers (of non-combustible material) if any additional gap remains after installing cable glands. | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016 to close this issue. On 12-06-2016: Cable entry and exit point to the COS found sealed. | 5 WEEKS | Corrected
Initial Inspection |  | 11 | Openings in the top plate after the cable passage not sealed. | Make circular hole at the base plate/top plate of panels and provide cable gland according to the respective cable size for cable entry and exit so that the cables are not stressed on the sharp edges of the hole of panels. Provide covers (of non-combustible material) if any additional gap remains after installing cable glands. | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016 to close this issue. On 12-06-2016: This issue is not corrected. Factory is behind schedule. On 01/09/2016: Corrected. | 5 WEEKS | Corrected
Initial Inspection |  | 12 | Insulation damaged cables are found inside the panel. | Remove the damage cable from the panel; install proper sized and good quality cable according to the size of Protective device and load capacity. The cable shall not be bent such as the bending is detrimental to the insulation of the cable. | Done | Jul 30 2015 | On 14-03-2016: Corrected. | 5 WEEKS | Corrected
Initial Inspection |  | 13 | Multiple cables terminating to MCCB in panel. | Multiple cables connecting at a MCCB terminal must be removed. Individual circuit breaker must used for each load according to the respective cable-size. | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016 to close this issue. On 12-06-2016: Corrected. | 5 weeks | Corrected
Follow Up Inspection |  | 14 | New Finding: Loop connection has used powering multiple MCBs/MCCBs. | Eliminate loop cables; use single cable for each MCBs/MCCBs. You may use bus bar to avoid multiple termination. | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016 to close this issue. On 12-06-2016: Corrected. | 3 months | Corrected
Follow Up Inspection |  | 15 | New Finding: Transformer Arcing horn has not installed. | Install transformer arcing horn with proper alignment (maintain not less than 2 inch gap between two horns.) | Done | Jul 25 2015 | On 14-03-2016: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 16 | New Finding: Panel base plates removed to allow cable entry. | Panel base plates must be installed, at all time, and cables entering panel must be firmly fixed with cable gland. | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016 to close this issue. On 12-06-2016: This issue is not corrected. Factory is behind schedule. On 01/09/2016: Corrected. On 29/07/2018: Seal bottom of the terminal box of generator and use cable glands for holding/supporting cables. | 4 months | Corrected
Follow Up Inspection |  | 17 | New Finding: Phase barrier/ separator has not installed. | Put purposely made phase separator (rubber type) between two phases; also terminate cables by proper sized cable lugs and cover cable lugs by heat shrink. | Done | Aug 25 2015 | On 14-03-2016: Corrected. | 2 months | Corrected
Follow Up Inspection |  | 18 | New Finding: Battery terminals are left open. | Use insulated rubber cap to cover all the battery terminals. | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016 to close this issue. On 12-06-2016: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 19 | New Finding: Earth busbar kept unused (Factory has no earth connections in some areas). | Use proper size cable for earthing and ensure that all electrical installations are properly earthed. | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016 to close this issue. On 12-06-2016: This issue is not corrected. Factory is behind schedule. On 01/09/2016: Not Corrected. Undersized cables are used for earth connections. On 18/12/2016: Not corrected. On 03/04/2017:Corrected. | 2 months | Corrected
Follow Up Inspection |  | 20 | New Finding: Cable tray is overloaded and are uncovered. | Use proper size cable tray and cover those. | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016 to close this issue. On 12-06-2016: This issue is not corrected. Factory is behind schedule. On 01/09/2016: Corrected. | 4 months | Corrected
Follow Up Inspection |  | 21 | New Finding: Earth pits are not identifiable and earth Pit resistance record is unavailable. | Identify each earth pit and mark it for periodic maintenance purpose. All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years. | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016 to close this issue. On 12-06-2016: This issue is not corrected. Factory is behind schedule. On 01/09/2016: Corrected. | 3 months | Corrected
Follow Up Inspection |  | 22 | New Finding: There is no programmed schedule for periodical inspection & testing of electrical equipment. | Develop an electrical maintenance program that includes inspections and testing of the electrical systems (preventive, proactive and breakdown maintenance). | Done | Apr 20 2016 | On 14-03-2016: Not corrected. New timeline given till 20/04/2016. On 12-06-2016: This issue is not corrected. Factory is behind schedule. On 01/09/2016: Not Corrected. On 18/12/2016: Not corrected. On 03/04/2017: Not corrected. On 17/07/2017: Not Corrected. On 12/02/2018: Not completed. On 29/07/2018: Corrected. | 3 months | Corrected
Follow Up Inspection |  | 23 | New Finding: Panel doors are not connected with earth. | All metal panel doors shall have earth connection by at least 4 rm earth cable. | Done | Jul 14 2016 | On 12-06-2016: This issue is not corrected. New committed timeline is given till 14-07-2016. On 01/09/2016: Not Corrected. Factory asked for time extension till 31/10/2016.Time extension request is not accepted. On 18/12/2016: Not corrected. On 03/04/2017: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 24 | New Finding: Cables in service are joined (splicing) between terminations. | Existing cables with joints must be spliced using butt splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. | Done | Jul 14 2016 | On 12-06-2016: This issue is not corrected. New committed timeline is given till 14-07-2016. On 01/09/2016: Not Corrected. Factory asked for time extension till 31/10/2016.Time extension request is not accepted. On 18/12/2016: Corrected. | 2 months | Corrected
Follow Up Inspection |  | 25 | New Finding: MCCBs are not adjusted accordingly. | Adjust all the MCCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. | Done | May 25 2016 | On 12-06-2016: Corrected. On 29/07/2018: All the MCCBs must be adjusted per cable current ampacity and load current. | 2 months | Corrected
Follow Up Inspection |  | 26 | New Finding: Panel/Distribution boxes are not installed at compliant location. | Take necessary initiative thus every panel/distribution board can be easily accessible . | Done | May 25 2016 | On 12-06-2016: Corrected. | 2 months | Corrected
Follow Up Inspection |  | 27 | New Finding: Light in store room / storage areas is uncovered. | Lights in store room / storage areas shall be covered. | Done | Apr 25 2016 | On 12-06-2016: Corrected. On 29/07/2018: All the MCCBs must be adjusted per cable current ampacity and load current. | 1 month | Corrected
Follow Up Inspection |  | 28 | New Finding: Cables laid on sub station room floor. | Use a cable tray to ensure adequate support. This shall not be routed/supported through the equipment' working clearance area. | Done | Jun 25 2016 | On 12-06-2016: Corrected. | 3 months | Corrected
Follow Up Inspection |  | 29 | New Finding: Transformer Oil Test report is unavailable. | Check the transformer oil condition by performing oil test. Do it once in a year and keep the record. | Done | Jul 14 2016 | On 12-06-2016: This issue is not corrected. New committed timeline is given till 14-07-2016. On 01/09/2016: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 30 | New Finding: Circuit is drawn from bus bar without Circuit breaker or any protective means. | For distribution board, along with the main circuit breaker all outgoing circuits shall have individual outgoing circuit breaker. | Done | Jul 14 2016 | On 01/09/2016: Not Corrected. Factory asked for time extension till 31/10/2016.Time extension request is not accepted. On 18/12/2016: Not corrected. On 03/04/2017: Not corrected. On 17/07/2017: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 31 | New Finding: Hot spot was found at the termination point of MCCB. | Check the connection and load of the phases, replace the MCCB, if required. | Done | Jul 14 2017 | On 01/09/2016: Not Corrected. Factory asked for time extension till 31/10/2016.Time extension request is not accepted. On 18/12/2016: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 32 | New Finding: No/Inadequate rubber (insulation) mat on the working area of distribution board/panel. | Put electrical insulation (rubber mat) on the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries). | Done | Sep 30 2016 | On 18/12/2016: Not corrected. On 03/04/2017: Corrected. | 3 WEEKS | Corrected
Follow Up Inspection |  | 33 | New Finding: Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | Hang this instruction near all electrical equipment (LT panel, MDB, FDB, DB, SDB) on a visible location. | Done | Sep 30 2016 | On 18/12/2016: Not corrected. On 03/04/2017: Not corrected. On 17/07/2017: Not Corrected. On 12/02/2018: Corrected. | 3 WEEKS | Corrected
Follow Up Inspection |  | 34 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly. | Adjust or replace all the MCCBs/ MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. | Done | Oct 10 2016 | On 18/12/2016: Not corrected. On 03/04/2017: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 35 | New Finding: Transformer Silica gel is discolored. | Replace silica gel by a new one; or dry it under sun and reuse it, if color regains. | Done | Sep 30 2016 | On 18/12/2016: Corrected. | 3 WEEKS | Corrected
Follow Up Inspection |  | 36 | New Finding: No separation between LT panels and HT units (Transformer, HT switchgear). | Make a brick built separation between LT and HT units; ensure that after making separator you have adequate ventilation (cross ventilation) and working clearance around each electrical equipment. | Done | Oct 20 2016 | On 18/12/2016: Not corrected. On 03/04/2017: Not corrected. On 17/07/2017: Not Corrected. On 12/02/2018: Not completed. On 29/07/2018: Not Corrected On 31/01/2019: Not Corrected. On 26/07/2022: Corrected. | 6 WEEKS | Corrected
Follow Up Inspection |  | 37 | New Finding: Sub station room has inadequate illumination. | Ensure adequate illumination in the sub station room thus any maintenance can be done comfortably (150 lux should be maintained). | Done | Jan 30 2017 | On 03/04/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: Maintenance movement is obstacle due to improper cable trench cover in the utility area (Generator/ Substation/ Boiler/ Compressor). | Covered cable trench must be equal to working floor height. If not, extended area must be sloped at both sides to avoid obstacle. | Done | May 31 2017 | On 03/04/2017: Not corrected. Time extension is given till 31/05/2017 to solve the issue. On 17/07/2017: Not Corrected. On 12/02/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 39 | New Finding: Earth connections for different electrical installation are not segregated. HT & Lt cables are not separated. | All the earth connections (transformer, generator and electrical systems) must be segregated and clearly marked (for TT earthing system). Separate cable tray shall be arranged for HT & LT cables maintaining adequate distance. | Done | May 31 2017 | On 03/04/2017: Not corrected. Time extension is given till 31/05/2017 to solve the issue. On 17/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ Busbar. | Each electrical circuit must be terminated at single MCB/MCCB terminals. | Done | Jan 30 2017 | On 03/04/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Power Cables are hanging without proper support. Wooden support used for electrical installation/ element. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. Replace wooden support and it is preferable to fix each electrical devices with noncombustible support. | Done | May 30 2017 | On 03/04/2017: Not corrected. Time extension is given till 31/05/2017 to solve the issue. On 17/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Power bus bar are installed congested; and power cables touch opposite phased bus bar. | Ensure that no power cable touches bare bus bar. Use insulated bus bar (just covering existing bus bar by heat shrink). | Done | Sep 25 2017 | On 12/02/2018: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 43 | New Finding: Substation & generator room has inadequate ventilation. | Adequate ventilation must be maintained in sub-station room and generator room. Cross/forced ventilation must be ensured. For exhaust fan, the fan diameter must not be less than 18 inch. | Done | Sep 25 2017 | On 12/02/2018: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 44 | New Finding: Equipment earth cable (for generator) size is inadequate. | Equipment earth connection for generator shall be drawn from at least two separate point of generator; and the cable size shall be less than or equal to half of the phase cable (depends on fault clearing time). You may use equivalent sized bare copper conductor. Number of earth pits shall be determined by the size of connected earth cable. | Done | Sep 25 2017 | On 12/02/2018: Not completed. On 29/07/2018: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 45 | New Finding: Cable trench is found wet or filled with water. | Cable trench must be kept always dry, and shall be covered by checkered plate. | Done | Sep 25 2017 | On 12/02/2018: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 46 | New Finding: Transformer Oil Test (dielectric strength test) report is not satisfactory. | Change transformer oil immediately once it dielectric strength goes below the reference value. | Done | Jul 25 2017 | On 12/02/2018: Corrected. | 7 Days | Corrected
Follow Up Inspection |  | 47 | New Finding: Circuit do not have any identification. Distribution boards have no clear identification markings. Haphazard cable dressing found inside panel. | Provide circuit directory for each board indicating current rating of circuit and size of fuse element/ breaker and specified load of each circuit. Means of identification may be done by providing separate color coding, marking tape, tagging, or other approved means. All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. Cables inside panel have to be dressed and guided properly. |  | May 9 2018 | On 31/01/2019: Not Corrected. On 26/07/2022: Not Corrected. Some progress has been observed. Circuit identification is not done properly. Distribution board identification is missing in a few places. RPO Comments On 16-Oct-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 05/11/2024: Not Corrected. Although cables are organized and identified but Panel identification is still missing. RPO Comments on 22-Dec-2024 : The factory management reported the remediation completion. This item will be verified in the next inspection. On 03/06/2025: Corrected. Cables & Distribution boards are identified. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Uneven working space in front of board/ panels and access to the board/panels is obstacles. | At least 1.07 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel and the working clearance shall not be uneven. | Done | May 9 2018 | On 31/01/2019: Not Corrected. On 26/07/2022: Not Corrected. Some progress has been observed. Working clearance is not provided properly in front of panel board. On 05/11/2024: Not Corrected. No Progress observed. On 03/06/2025: Not Corrected. Progress remain unchanged since last follow up inspection. RPO Comments on 05-Apr-2026: Though the factory reported this CAP item as completed in the factory action plan, but no pictorial evidence has been provided for this CAP item. Therefore, the CAP item will remain "In Progress" & hence the corrective action plan should be completed as per the given recommendation with immediate concern. On 12/04/2026: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Periodicity of Thermography survey is not continued. | Thermography survey must be done and recorded at least twice in a year. | Done | Jul 8 2018 | On 31/01/2019: Corrected. | 07 Days | Corrected
Follow Up Inspection |  | 50 | New Finding: Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained. | Done | May 20 2019 | On 26/07/2022: Not Corrected. Some progress has been observed. Factory is working on it. On 05/11/2024: Not Corrected. No Progress observed. Submit a layout of transformer room for approval . On 03/06/2025: Not Corrected. The factory submitted transformer room layout to RSC and current status is "Need Modifications". RPO Comments on 05-Apr-2026: Though the factory reported this CAP item as completed in the factory action plan, but no pictorial evidence has been provided for this CAP item. Therefore, the CAP item will remain "In Progress" & hence the corrective action plan should be completed as per the given recommendation with immediate concern. On 12/04/2026: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 51 | New Finding: Periodicity of Transformer Oil Test (dielectric strength, moisture content and flash point) survey is not continued. | Transformer oil test (dielectric strength, moisture, and flash point test for oil) shall be done at least once in a year. If the operation of transformer is 24/7 in the facility twice in a year is a better practice. | Done | Aug 30 2022 | On 05/11/2024: Not Corrected. Transformer oil was last tested on 18/09/2017. On 03/06/2025: Not Corrected. The transformer oil has been tested and found to have a critically low breakdown voltage. Immediate action is needed either centrifuge the oil or replace it entirely. RPO Comments on 05-Apr-2026: Though the factory reported this CAP item as completed in the factory action plan, but no pictorial evidence has been provided for this CAP item. Therefore, the CAP item will remain "In Progress" & hence the corrective action plan should be completed as per the given recommendation with immediate concern. On 12/04/2026: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 52 | New Finding: Lightning Protection System (LPS) is not installed where the risk index equal or greater than 40 (According to BNBC). | Factory shall design Lightning Protection System (LPS) for the whole factory (where the Risk index is equal or greater than 40). Once LPS is designed properly, installation must be done accordingly. |  | Nov 7 2022 | On 05/11/2024: Not Corrected. No Progress observed. On 03/06/2025: Not Corrected. No progress has been observed. RPO Comments on 05-Apr-2026: Though the factory reported this CAP item as completed in the factory action plan, but no pictorial evidence has been provided for this CAP item. Therefore, the CAP item will remain "In Progress" & hence the corrective action plan should be completed as per the given recommendation with immediate concern. On 12/04/2026: Not Corrected. No significant progress was observed. The factory installed one air terminal and one earth pit in building-1. No standard (LPS) design drawing was found for the facility. | 3 Months | In Progress
Follow Up Inspection |  | 53 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/ undersize. | Earth lead cable/ Earth Continuity Conductor (ECC) shall be determined according to BNBC or Adiabatic method (considering CB's response time, fault current & type of earth conductor other factors). |  | Oct 4 2022 | On 05/11/2024: Not Corrected. No Progress observed. On 03/06/2025: Not Corrected. Panel body earthing is inadequate. RPO Comments on 05-Apr-2026: Though the factory reported this CAP item as completed in the factory action plan, but no pictorial evidence has been provided for this CAP item. Therefore, the CAP item will remain "In Progress" & hence the corrective action plan should be completed as per the given recommendation with immediate concern. On 12/04/2026: Not Corrected. Significant progress was observed. The factory has increased ECC conductor in few panels. Still panel body earthing is inadequate in Generator panel, COS panel, MDB panel and LT panel and few other panels. | 2 Months | In Progress
Follow Up Inspection |  | 54 | New Finding: Distribution Board's top/bottom is left open (typical issue). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. | Done | Oct 4 2022 | RPO Comments On 16-Oct-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 05/11/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 55 | New Finding: Uninsulated electrical tools are used by maintenance personnel in the factory. | For maintenance purposes, all the electrical tools shall be properly insulated and these insulations shall be checked periodically. | Done | Oct 4 2022 | On 05/11/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 56 | New Finding: Periodicity of earth Pit resistance test record is not continued. | All earthing systems must be tested for resistance on a dry day at least once every two years. Records of each earthing test and its results must be available for inspection when required. | We will try to solve this issue as soon as possible. | Dec 20 2024 | Earth pit resistance record was found which was tested on 30.04.2022 RPO Comments on 17-May-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. On 03/06/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: Periodicity of insulation resistance test record is not continued. | Insulation resistance testing of all cables (excluding those less than 25 sq.mm) must be conducted once every two years, with records maintained. This testing may require power shutdown to ensure accurate results and safety. | We will try to solve this issue as soon as possible. | Dec 20 2024 | Insulation resistance record was found which was tested on 24.04.2022 RPO Comments on 17-May-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. On 03/06/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: Periodicity of thermographic survey is not continued. | Thermography survey of the entire electrical system must be conducted and documented by bi-annual, including real-time and scanned images with recommendations for corrective actions. This helps identify overheating, loose connections, and safety hazards, preventing equipment failure and reducing downtime. | We will try to solve this issue as soon as possible. | Dec 20 2024 | Last Tharmal scanning was performed on 15/09/2018 RPO Comments on 17-May-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. On 03/06/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: There is no programmed schedule for periodical inspection & testing of electrical equipment. | Electrical maintenance program shall be developed to include regular inspections and testing of electrical systems, focusing on preventive and proactive measures. | We will try to solve this issue as soon as possible. | Dec 20 2024 | RPO Comments on 17-May-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. On 03/06/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: No policies for PPE/LOTO (Lock-Out-Tag-Out) are introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement PPE (Personal Protective Equipment) and LOTO (Lock-Out-Tag-Out) policy using LOTO devices to ensure personnel safety during maintenance activities. All LOTO usage records must be maintained for compliance and safety monitoring. |  | Dec 20 2024 | On 03/06/2025: Not Corrected. No policies for PPE/LOTO (Lock-Out-Tag-Out) are introduced. RPO Comments on 05-Apr-2026: Though the factory reported this CAP item as completed in the factory action plan, but no pictorial evidence has been provided for this CAP item. Therefore, the CAP item will remain "In Progress" & hence the corrective action plan should be completed as per the given recommendation with immediate concern. On 12/04/2026: Not Corrected. Significant progress has been observed. The factory has prepared LOTO and PPE policies. But, LOTO devices have not yet been introduced in the factory, and PPE is also inadequate. | 1 Month | In Progress
Follow Up Inspection |  | 61 | New Finding: Lint and dust deposited on and around the transformer. | Transformer top and around it shall be kept neat and clean. | Done | Dec 20 2024 | On 03/06/2025: Not Corrected. No progress has been observed. RPO Comments on 05-Apr-2026: Though the factory reported this CAP item as completed in the factory action plan, but no pictorial evidence has been provided for this CAP item. Therefore, the CAP item will remain "In Progress" & hence the corrective action plan should be completed as per the given recommendation with immediate concern. On 12/04/2026: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Transformer Silica gel is discolored. | Discolored Silica gel needs to be changed. | Done | Dec 20 2024 | On 03/06/2025: Not Corrected. No progress has been observed. RPO Comments on 05-Apr-2026: Though the factory reported this CAP item as completed in the factory action plan, but no pictorial evidence has been provided for this CAP item. Therefore, the CAP item will remain "In Progress" & hence the corrective action plan should be completed as per the given recommendation with immediate concern. On 12/04/2026: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Transformer body earthing (equipment earthing) cable is not available. | The size of the earth cable shall be determined according to BNBC or the Adiabatic method. The number of earth pits shall be calculated based on acknowledged standards to ensure effectiveness. |  | Dec 20 2024 | On 03/06/2025: Not Corrected. Progress remain unchanged since last follow up inspection. RPO Comments on 05-Apr-2026: Though the factory reported this CAP item as completed in the factory action plan, but no pictorial evidence has been provided for this CAP item. Therefore, the CAP item will remain "In Progress" & hence the corrective action plan should be completed as per the given recommendation with immediate concern. On 12/04/2026: Not Corrected. The factory has provided body earthing for the transformer but the earthing is inadequate. | 1 Month | In Progress
Follow Up Inspection |  | 64 | New Finding: Generator body earthing (equipment earthing) cable is inadequate. | Ensure that the generator is equipped with at least two separate earth pits. The size of the earth cable shall be determined according to BNBC or the Adiabatic method. The number of earth pits shall be calculated based on acknowledged standards to ensure effectiveness. |  | Dec 20 2024 | On 03/06/2025: Not Corrected. Found same as before. RPO Comments on 05-Apr-2026: Though the factory reported this CAP item as completed in the factory action plan, but no pictorial evidence has been provided for this CAP item. Therefore, the CAP item will remain "In Progress" & hence the corrective action plan should be completed as per the given recommendation with immediate concern. On 12/04/2026: Not Corrected. The factory has increased generator body earthing. But Earth pit Electrode size is inadequate. Also generator neutral earthing is missing. | 1 Month | In Progress
Follow Up Inspection |  | 65 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/not available. | Earth lead cable/ Earth Continuity Conductor (ECC) shall be determined according to BNBC or Adiabatic method (considering CB's response time, fault current & type of earth conductor other factors). |  | Jan 20 2025 | On 03/06/2025: Not Corrected. Inadequate Ecc found at LT panel, MDB panel. RPO Comments on 05-Apr-2026: Though the factory reported this CAP item as completed in the factory action plan, but no pictorial evidence has been provided for this CAP item. Therefore, the CAP item will remain "In Progress" & hence the corrective action plan should be completed as per the given recommendation with immediate concern. On 12/04/2026: Not Corrected. Significant progress was observed. The factory has increased ECC conductor in few panels. Still panel body earthing is inadequate in Generator panel, COS panel, MDB panel and LT panel and few other panels. | 2 Months | In Progress
Follow Up Inspection |  | 66 | New Finding: Panel doors are not connected with earth. | All metal components within the electrical system must be securely connected to the earth. This earthing is essential to mitigate the risk of electrical shock or electrocution by providing a safe path for fault currents to dissipate. |  | Dec 20 2024 | On 03/06/2025: Not Corrected. Some panels does not have earth connection. RPO Comments on 05-Apr-2026: Though the factory reported this CAP item as completed in the factory action plan, but no pictorial evidence has been provided for this CAP item. Therefore, the CAP item will remain "In Progress" & hence the corrective action plan should be completed as per the given recommendation with immediate concern. On 12/04/2026: Not Corrected. Door earthing was missing in Generator panel, boiler panel & compressor panel and few other panels in building-1. | 1 Month | In Progress
Follow Up Inspection |  | 67 | New Finding: Non rated and non-certified comb bar used for powering multiple MCB. | For connecting multiple MCB use rated and listed comb bar. |  | Jan 20 2025 | On 03/06/2025: Not Corrected. Recommended to use listed combo busbar. RPO Comments on 05-Apr-2026: The design documents (SLD) are pending to be submitted to RSC and the corrective action plan should be completed as per the given recommendation with immediate concern. On 12/04/2026: Not Corrected. Non rated comb busbar was observed in few MCDB panel boards. Moreover, excess comb busbar live parts are exposed, creating a hazard. Cut and remove excess busbar and install insulated end caps on all terminations. | 2 Months | In Progress
Follow Up Inspection |  | 68 | New Finding: Significant changes of the electrical system is observed from accepted SLD. | As-built Electrical Single Line Diagram (SLD) must be prepared by a qualified engineer, incorporating all essential details of the electrical system. The diagram must be reviewed and approved by the RSC. Once approved, the SLD must be implemented within the facility. Additionally, the SLD must be promptly updated to reflect any modifications made to the system to ensure accuracy and compliance. |  | Jun 12 2026 |  | 2 Months | In Progress
Follow Up Inspection |  | 69 | New Finding: Earth pit resistance test record doesn't match with field (System). | Field information must be accurately reflected in the record. All earthing systems must be tested for resistance on a dry day at least once every two years. Records of each earthing test and its results must be available for inspection when required. |  | May 12 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 70 | New Finding: Earth pit resistance record is not available. (LPS) | All earthing systems must be tested for resistance on a dry day at least once every two years. Records of each earthing test and its results must be available for inspection when required. |  | May 12 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 71 | New Finding: Periodicity of thermographic survey is not continued. | Thermography survey of the entire electrical system must be conducted and documented by bi-annual, including real-time and scanned images with recommendations for corrective actions. This helps identify overheating, loose connections, and safety hazards, preventing equipment failure and reducing downtime. |  | May 12 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 72 | New Finding: Distribution board's top/bottom is left open (typical issue). | Each electrical distribution board or panel must be sealed to prevent the ingress of fluffs and dust. Adequate ventilation must also be ensured to maintain optimal operating temperatures. Cable glands should be used where required to secure cables and maintain the integrity of the seal. |  | May 12 2026 |  | 1 Month | In Progress
Follow Up Inspection |  | 73 | New Finding: Circuit breaker has no capacity information. | Each circuit breaker must be clearly labeled with its capacity information. |  | May 12 2026 |  | 1 Month | In Progress