## Structural
Date
18-May-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | SPRING TRADE LTD., Konapara, Plot: 42,Zirani Bazar, B.K.S.P, Savar, Savar, Dhaka
Date of Inspection |  | 2014-04-28
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Preliminary load take-down calculations suggest that the typical columns in two buildings are very close to having a ‘red’ warning. The typical columns possess very little spare capacity. | • Carry out a full Detailed Engineering Assessment of the entire building including any intrusive testing required. | DEA is accepted by Accord on 12th May 2016. | Jul 2 2014 | On 18/07/16: The DEA has been accepted by Accord on 12 May,2016. Retrofitting work has not been started yet. On 25/09/2016: DEA has been done and accepted by ACCORD. Retrofitting work has not started till inspection date On 01/12/2016: Retrofitting work is going on. Final timeline of remedial work was 31 October 2016. Factory management told that they would complete all the remedial works within February 2017. On 21/08/2017: Factory prepared DEA and submitted to ACCORD which was accepted on 12 May, 2016. During inspection, retrofitting work was found completed as per accepted retrofitting drawings. On 10-Feb-2022: This issue was corrected from previous inspection. Factory prepared DEA and submitted to ACCORD which was accepted on 12 May, 2016. During inspection, retrofitting work was found completed as per accepted retrofitting drawings. On 23-Oct-2023: Corrected in the previous inspection. Factory got DEA acceptance from ACCORD on 12 May, 2016. On 21-May-2024: Corrected previously. DEA of the Building 1 and Building 2 was accepted by ACCORD on 12-May-2016. | (within 6 – weeks) | Corrected
Initial Inspection |  | 2 | Preliminary load take-down calculations suggest that the typical columns in two buildings are very close to having a ‘red’ warning. The typical columns possess very little spare capacity. | • Carry out full survey of all structural elements to check the loading capacity of the overall structural system. | Corrected. This issue has coverd under DEA. | Jul 2 2014 | On 18/07/16:The adequacy of all structural elements has been checked with DEA which has got acceptance from Accord on 12 May,2016. Retrofitting work has not been started yet. On 25/09/2016: DEA has been done and accepted by ACCORD. Retrofitting work has not started till inspection date. On 01/12/2016: This issue has covered in DEA and DEA has been accepted on 12 May 2016. As per the recommendation of the consultant, remedial work is going on. On 21/08/2017: Factory prepared DEA and submitted to ACCORD which was accepted on 12 May, 2016. During inspection, retrofitting work was found completed as per accepted retrofitting drawings. On 10-Feb-2022: This issue was corrected from previous inspection. Factory prepared DEA and submitted to ACCORD which was accepted on 12 May, 2016. During inspection, retrofitting work was found completed as per accepted retrofitting drawings. On 23-Oct-2023: Corrected in the previous inspection. On 21-May-2024: Corrected previously. DEA of the Building 1 and Building 2 was accepted by ACCORD on 12-May-2016. | (within 6 – weeks) | Corrected
Initial Inspection |  | 3 | Preliminary load take-down calculations suggest that the typical columns in two buildings are very close to having a ‘red’ warning. The typical columns possess very little spare capacity. | • The Factory Engineer to review design, loads and columns stresses in entire building in accordance with BNBC regulations. | DEA is accepted by Accord on 12th May 2016. | Jul 2 2014 | On 18/07/16: The DEA with detailed model analysis has got acceptance from Accord on 12 May,2016.Retrofitting work has not been started yet. On 25/09/2016: DEA has been done and accepted by ACCORD. Retrofitting work has not been started till inspection date. On 01/12/2016: Retrofitting work is going on. Final timeline of remedial work was 31 October 2016. Factory management told that they would complete all the remedial works within February 2017. On 21/08/2017: Factory prepared DEA and submitted to ACCORD which was accepted on 12 May, 2016. During inspection, retrofitting work was found completed as per accepted retrofitting drawings. On 10-Feb-2022: This issue was corrected from previous inspection. Factory prepared DEA and submitted to ACCORD which was accepted on 12 May, 2016. On 23-Oct-2023: Corrected in the previous inspection. On 21-May-2024: Corrected previously. | (within 6 – weeks) | Corrected
Initial Inspection |  | 4 | Preliminary load take-down calculations suggest that the typical columns in two buildings are very close to having a ‘red’ warning. The typical columns possess very little spare capacity. | • Provided loading plan must be strictly maintained | We are strictly maintaining the provided loading plan from the report date. | Dec 18 2014 | On 18/07/16: Load plan for each floor was prepared and during follow up visit, loading at all floors were found as per as built load plan which has got approval with DEA from Accord. On 25/09/2016: Corrected from previous follow up inspection. During inspection loading was found satisfactory as per intermediate load plan. On 01/12/2016: Corrected in previous inspection. Intermediate load plan has been posted and load was found within allowable limit (30 psf). Final load plan will be implemented after completion of remedial works. On 21/08/2017:Corrected from previous follow up inspection. Load plan has been prepared as a part of DEA which was accepted by ACCORD on 12 May, 2016. Factory has completed retrofitting works. During inspection, Loading was found within limit as per mentioned load on final load plan (42psf). Load plan was found posted on each floor. Load marking was observed on storage areas. On 10-Feb-2022: This issue was corrected from previous inspection. Load plan has been prepared as a part of DEA which was accepted by ACCORD on 12 May, 2016. Factory has completed retrofitting works. During inspection, Loading was found within limit as per mentioned load on final load plan (42psf). Load plan was found posted on each floor. Load marking was observed on storage areas. On 23-Oct-2023: Corrected in the previous inspection. Load plan was found posted & loading was observed bellow allowable limit (42 psf). On 21-May-2024: Corrected previously. During inspection, load plan was found posted in each floor of Building 1 & Building 2 and loading was found within allowable limit of accepted load plan (42 psf). | (within 6-months) | Corrected
Initial Inspection |  | 5 | There are many visible cracks at the middle of the beams on the soffit of the 5th floor in Building 1. It could be due to poor construction or under-design of these beams. | • Carry out the steps noted in Item 1 | This issue will be covered in DEA | Jul 2 2014 | On 18/07/16 : During inspection we have not found any visible crack in the beam which has been clarified in DEA. The DEA was accepted on 12 May 2016. On 25/09/2016: Corrected from previous follow up inspection report. During inspection, no such cracking was found. On 01/12/2016: Previously corrected. On 21/08/2017:Corrected from previous follow up inspection report. During inspection, no visible crack was found. On 10-Feb-2022: This issue was corrected from previous inspection. During inspection, no visible crack was found. On 23-Oct-2023: Corrected in the previous inspection. No further crack was observed. On 21-May-2024: Corrected previously. During inspection, no crack was found. | (within 6 – weeks) | Corrected
Initial Inspection |  | 6 | There are many visible cracks at the middle of the beams on the soffit of the 5th floor in Building 1. It could be due to poor construction or under-design of these beams. | • The Factory Engineer to review design, loads to figure out the reasons of the crack formation | This issue will be covered in DEA | Jul 2 2014 | On 18/07/16 : During inspection we have not found any visible crack in the beam which has been clarified in DEA. The DEA was accepted on 12 May 2016. On 25/09/2016: Corrected from previous follow up inspection report. During inspection, no such cracking was found. On 01/12/2016: Previously corrected. On 21/08/2017:Corrected from previous follow up inspection report. During inspection, no visible crack was found. On 10-Feb-2022: This issue was corrected from previous inspection. During inspection, no visible crack was found. As per DEA report beams found adequate. On 23-Oct-2023: Corrected in the previous inspection. On 21-May-2024: Corrected previously. This issue has been covered in DEA which was accepted by ACCORD on 12-May-2016 for Building 1. | (within 6 – weeks) | Corrected
Initial Inspection |  | 7 | There are many visible cracks at the middle of the beams on the soffit of the 5th floor in Building 1. It could be due to poor construction or under-design of these beams. | • As per result of design check, building engineer to propose the strengthening or repairing works for those beam with cracks accordingly. | This issue will be covered in DEA | Dec 18 2014 | On 18/07/16 : During inspection we have not found any visible crack in the beam which has been clarified in DEA. The DEA was accepted on 12 May 2016. On 25/09/2016: Corrected from previous follow up inspection report. During inspection, no such cracking was found. On 01/12/2016: Previously corrected. On 21/08/2017:Corrected from previous follow up inspection report. During inspection, no visible crack was found. On 10-Feb-2022: This issue was corrected from previous inspection. During inspection, no visible crack was found. As per DEA report beams found adequate. Cracks were repaired by new plastering layer. On 23-Oct-2023: Corrected in the previous inspection. This issue was covered under DEA which got accepted on 12 May 2016. On 21-May-2024: Corrected previously. Factory has completed all the retrofitting works as per recommendation of accepted DEA. | (within 6-months) | Corrected
Initial Inspection |  | 8 | There are many visible cracks at the middle of the beams on the soffit of the 5th floor in Building 1. It could be due to poor construction or under-design of these beams. | • Consider to remove the old plaster and reapply the new plastering layer. | This issue will be covered in DEA | Dec 18 2014 | On 18/07/16 : During inspection we have not found any visible crack in the beam which has been clarified in DEA. The DEA was accepted on 12 May 2016. On 25/09/2016: Corrected from previous follow up inspection report. During inspection, no such cracking was found. On 01/12/2016: Previously corrected. On 21/08/2017: Corrected from previous follow up inspection report. During inspection, no visible crack was found. On 10-Feb-2022: This issue was corrected from previous inspection. During inspection, no visible crack was found. As per DEA report beams found adequate. Cracks were repaired by new plastering layer. On 23-Oct-2023: Corrected in the previous inspection. No further crack was observed. On 21-May-2024: Corrected previously. | (within 6-months) | Corrected
Initial Inspection |  | 9 | There is a lack of any lateral support design for two buildings. It could lead to serious damage in a wind or earthquake event. | • As per the results of structural analysis, the building needs to be revised to accord with BNBC building codes with regard to lateral stability. | We have already finished all retrofitting work for both of our building- I & building- II and awaiting for Accord varification visit. | Dec 18 2014 | On 18/07/16: The DEA with detailed model analysis has got acceptance from Accord on 12 May,2016.Retrofitting work has not been started yet. On 25/09/2016: DEA has been done and accepted by ACCORD. Retrofitting work has not been started till inspection date. On 01/12/2016: This issue has covered in DEA and DEA has been accepted on 12 May 2016. As per the recommendation of the consultant, remedial work is going on. Final timeline of retrofitting work was 31 October 2016. Factory management told that they would complete all the remedial works within February 2017. On 21/08/2017:This issue was covered in DEA. Factory prepared DEA and submitted to ACCORD which was accepted on 12 May, 2016. During inspection, retrofitting work (Column strengthening of both buildings(B-1&2) & Installation of bracings of B-1) was found completed as per accepted retrofitting drawings. On 10-Feb-2022: This issue was corrected from previous inspection. This issue was covered in DEA. Factory prepared DEA and submitted to ACCORD which was accepted on 12 May, 2016. During inspection, retrofitting work (Column strengthening of both buildings(B-1&2) & Installation of bracings of B-1) was found completed as per accepted retrofitting drawings. On 23-Oct-2023: Corrected in the previous inspection. Retrofitting works have been completed. Factory provided a retrofitting completion certificate. On 21-May-2024: Corrected previously. This issue has been covered in DEA which was accepted by ACCORD on 12-May-2016 for Building 1 and Building 2. | (within 6-months) | Corrected
Follow Up Inspection |  | 10 | New finding 1: Undocumented pump room and wastage room found. | Carry out full survey of all structural elements to check the loading capacity of the overall structural system. | * We have already submited EA report to RSC on 11-May-2023 accordingly. * As per EA firm instruction, we have already completed the retrofitting work. | Mar 28 2022 | On 10-Feb-2022: During inspection, a undocumented pump room and wastage room was found in the factory premises. There is heavy loading(Plastic water tank capacity 8000 litters) found at the roof of pump house. Factory engineer is required to check the adequacy of the all structural members and submit to RSC. Also plastic water tank supporting steel structure seems to be inadequate. Either relocate the water tank or improve the water tank supporting steel structure by engineered way. On 23-Oct-2023: EA of Pump room & Wastage room was accepted by RSC on 21-Aug-2023. Factory did not start any remedial works. Remediation works completion timeline is extended to 30-Nov-2023, On 21-May-2024: This issue has been covered in EA. EA of the Pump and Wastage Room was accepted by RSC on 21-Aug-2023. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 11 | New finding 2: Undocumented pump room and wastage room found. | Make structural alterations if required as advised by Factory Engineer | * We have already submited EA report to RSC on 11-May-2023 accordingly. * As per EA firm instruction, we have already completed the retrofitting work. | Aug 16 2022 | On 10-Feb-2022: Any remediation work raised from EA is required to be completed after getting acceptance of EA. On 23-Oct-2023: EA of Pump room & Wastage room was accepted by RSC on 21-Aug-2023. Factory did not start any remedial works. Remediation works completion timeline is extended to 30-Nov-2023, On 21-May-2024: Factory has completed all the retrofitting works as per recommendation of accepted EA. During inspection, retrofitting works have been verified and found satisfactory. Also, retrofitting completion certificate, concrete cylinder test report and rebar test report was available on site. | (within 6 months) | Corrected
Follow Up Inspection |  | 12 | New finding 3: Undocumented boiler room found. | Produce as built drawing of the boiler shed | * As per EA firm instruction, we have started the retrofitting work and hopefully it will be completed by November 2023. | Mar 28 2022 | On 10-Feb-2022: Factory engineer is required to produce as built drawing for the boiler shed and submit to RSC. On 23-Oct-2023: As built drawings have been produced and submitted to RSC which was accepted along with EA of pump room and wastage room. During inspection no mis-match was found. On 21-May-2024: Corrected previously. As built drawings of Boiler room was accepted by RSC on 21-Aug-2023. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 13 | New findings 4: non-structural elements (racks) at several floors not adequately anchored and braced in both Building 1 & 2 | Adequately anchor and brace all non-structural elements (racks) to resist earthquake force | We will fix up all of the non-structural elements (racks) with floor or side wall which as best applicable to resist earthquake force. | Dec 17 2023 | On 23-Oct-2023: During inspection, non-structural elements (racks) at several floors found unanchored at both Building 1 & 2. Factory is required to anchor/brace all the non-structural elements. On 21-May-2024: During inspection, it was found that factory has anchored all the non-structural elements in Building 1 and 2. | (within 6 weeks) | Corrected

## Fire
Date
18-May-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | SPRING TRADE LTD., Konapara, Plot: 42,Zirani Bazar, B.K.S.P, Savar, Savar, Dhaka
Date of Inspection |  | 2014-05-03
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The exit stairs are not separated from work areas, on each floor by fire-rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | Installation of magnetic door holder has been completed and interfacing with FACP has been completed by 31/07/2017. During last follow up inspection some Doors were found open manually which is now corrected. Now the system running on test basis. | Jun 24 2016 | On 15/05/2017: The factory has installed most of the fire doors. Installation of magnetic door holder interfaced with FACP has not been completed yet. On 21/08/2017: Doors were found open manually. On 27/11/2017: Corrected. Fire door installation and interfacing with FACP has been done. On 12/03/2018: Corrected as per previous follow-up. On 27/05/2018: Corrected as per previous follow-up. On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 2 | The storage room is not separated by fire-rated construction. Storage room is located in the ground floor. | Separate the storage room by a minimum 1-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations | Corrected as per recommendation | Dec 22 2015 | On 14-02-2017: Corrected. Defined storage area has been found within limit. Dedicated storage has not been found in Building-I. On 15/05/2017: Corrected. Defined storage area has been found within limit. Dedicated storage has not been found in Building-I. On 21/08/2017: Corrected. On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. Dedicated storage room has not been found in Building-1. On 27/05/2018: Corrected. On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 3 | The generator and transformer room is not separated by fire-rated construction due to unprotected openings. Room is located at ground floor. | Separate the generator and transformer room by a minimum 2-hr fire-rated construction. Seal and/or construction. Seal and/or protected all openings to maintain the required fire separations | Done | Dec 22 2015 | On 15/05/2017: Corrected as per last follow-up inspection. On 21/08/2017: Corrected. On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. On 27/05/2018: Corrected.Note: Due to rework for new higher capacity generator installation the door has been found dismantled for the time being. On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | The boiler room is not separated by fire-rated construction unprotected openings and penetrations. Boiler room is located in the ground floor. | Separate the boiler room by a minimum 1-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations | Already corrected again | Dec 22 2015 | On 14-02-2017: Corrected as per previous follow-up inspection. On 15/05/2017: RE-opened. Not corrected. Due to retrofitting work Fire door of that pace has been removed. On 21/08/2017: Corrected. Fire door has been re-installed. On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 5 | Areas used for combustible storage are not separated by fire rated construction. Storage were located at the 1st floor. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Corrected as per recommendation | Jan 22 2016 | On 01-12-16: Corrected. On 14-02-2017: Corrected. Defined storage area has been found within limit. On 15/05/2017: Corrected as per previous follow up. On 27/11/2017: Corrected. On 12/03/2018: Refer to issue no: 27. On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 6 | Egress doors / gates with locking features are provided at most exit stairs, some stairs have sliding glass doors. | Remove locking features from all egress doors / gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected as per recommendation | Dec 22 2015 | On 15/05/2017: Corrected On 21/08/2017: Corrected. On 27/11/2017: Corrected. On 12/03/2018: Corrected. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 7 | Exit capacity is not adequate for the occupant load. 1st, 2nd and 3rd floors have an exit capacity of 400 occupants and an occupant load of 450 | Reduce occupant load to not more than available exit capacity of 400 occupants. In the future provide an additional emergency exit stair at the west side of the floors. | Corrected as per recommendation | Dec 22 2015 | On 14-02-2017: Corrected. The factory has reduced occupant load. On 15/05/2017: Corrected On 21/08/2017: Corrected. On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 8 | Exit stair door/egress door serving 50 or more occupants does not swing in the direction of egress travel. Most locations doors swings incorrectly. | Modify the egress door to swing in the direction of egress travel. | Corrected as per recommendation | Dec 22 2015 | On 14-02-2017: Corrected as per site observation. On 15/05/2017: Corrected On 21/08/2017: Corrected. On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 9 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | Already Corrected. (Installation of fire alarm system has been completed and 1st T&C varification Inspection done by Accord on 15/10/2018 and 2nd T&C varification Inspection done by Accord on 04/04/2019.There were some deficiencies observed during T&C varification Inspection, which have already been corrected. We requested to Accord again for Verification Inspection.) | Jun 24 2016 | On 15/05/2017: It is an integrated part of Fire alarm system. On 21/08/2017: Installation has been almost completed. Interfacing of Fire pump with FACP has not been completed yet. Factory shall provide proper 3rd party certification for the products used in the system during T&C. As-built drawings were not present on-site. On 27/11/2017: Installation has been completed and pending for T&C. On 12/03/2018: Factory has informed that installation of the system almost completed. Testing and commissioning of the system is pending. On 27/05/2018: Reportedly installation of the detection system is completed. Waiting for the testing and commissioning. On 04/04/2019: T&CVI found that installation certificate and record of completion are required. Verify the information used in the battery calculations and voltage drop calculations. Provide manufacturer’s product datasheets for all fire alarm equipment. Provide accurate 3rd party testing reports for fire alarm cabling. Provide control unit diagram(s) for all control equipment. Provide voltage drop calculations as required by NFPA 72. Install control unit batteries in a listed cabinet if required by the fire alarm manufacturer. Indicate the date of manufacture for all fire alarm control equipment batteries. Mount modules in back boxes if required by the fire alarm manufacturer. Provide a lock on the AC circuit breaker dedicated to the fire alarm system and provide “Fire Alarm” label on the circuit breaker. Enable piezo buzzer for the control equipment. Protect wiring entering or leaving control equipment panel(s). Provide a dedicated AC power supply from the MDB, directly to the fire alarm control equipment. Provide adequate fire alarm notification for all areas. Evacuation signal shall utilize a three-pulse temporal pattern. See detailed T&CVI Report. On 10-Dec-2020: As per Full-T&C, the system is Approved. For details, see the Full-T&C report. On 18/03/2024: Corrected. The FACP was found functional during inspection. | Design within 4 months, install within 9 months | Corrected
Initial Inspection |  | 10 | Inspection, testing, and maintenance for the fire alarm system was not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | Already Corrected. ( Installation of fire alarm system has been completed and 1st T&C varification Inspection done by Accord on 15/10/2018 and 2nd T&C varification Inspection done by Accord on 04/04/2019.There were some deficiencies observed during T&C varification Inspection, which have already been corrected. We will submit required documents to Accord very soon again for Verification Inspection.) | Jun 24 2016 | On 14-02-2017: It is an integrated part of fire alarm system. On 15/05/2017: It is an integrated part of Fire alarm system. On 21/08/2017: Integrated part of FA system. On 27/11/2017: It is an integrated part of Fire alarm system. On 12/03/2018: Factory is maintaining a checklist but not properly. On 27/05/2018: Corrected. Factory is maintaining checklist and documents have been shown. On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 11 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Replace the single-station smoke alarms. Provide automatic smoke detection throughout the building in accordance with NFPA 72. | Already Corrected. ( Installation of fire alarm system has been completed and 1st T&C varification Inspection done by Accord on 15/10/2018 and 2nd T&C varification Inspection done by Accord on 04/04/2019.There were some deficiencies observed during T&C varification Inspection, which have already been corrected. We will submit required documents to Accord very soon again for Verification Inspection.) | Jun 24 2016 | On 14-02-2017: It is an integrated part of fire alarm system. On 15/05/2017: It is an integrated part of Fire alarm system. On 21/08/2017: Integrated part of FA system. On 27/11/2017: Corrected. Removed. On 12/03/2018: Corrected as per previous follow-up. However, it is an integrated part of fire alarm system. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 12 | Inspection, testing, and maintenance records for the emergency lighting system were not available. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | Corrected as per recommendation | Dec 22 2015 | On 15/05/2017: Corrected. On 21/08/2017: Corrected. On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 13 | The exit stairs are not separated from work areas, on each floor by fire-rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. | During last follow up inspection some Doors were found open manually which is now corrected. All Exit stair and discharge is also separated from building interiors. | Jun 24 2016 | On 15/05/2017:The factory has installed most of the fire doors. Installation of magnetic door holder interfaced with FACP has not been completed yet. On 21/08/2017: Doors were found open manually. Exit stair and discharge is also not separated from building interiors. On 27/11/2017: Corrected. Fire door installation and interfacing with FACP has been done. On 12/03/2018: Corrected as per previous follow-up. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 14 | Egress doors with locking features are provided at building exits, exit stairs, along egress routes, and at exit discharge. Lockable swing or sliding doors at all exit stairs, all gates were open and unlocked during the inspection. | Remove locking features from all egress doors / gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected as per recommendation | Dec 22 2015 | On 14-02-2017: Corrected. Non-compliant locking feature has not been observed during follow-up inspection. On 15/05/2017:Corrected. Non-compliant locking feature has not been observed during follow-up inspection. On 21/08/2017: Corrected. On 27/11/2017: Corrected. On 12/03/2018: Corrected. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 15 | Exit stair door serving 50 or more occupants does not swing in the direction of egress travel. | Modify the egress door to swing in the direction of egress travel. | Corrected as per recommendation | Dec 22 2015 | On 14-02-2017: Corrected as per site observation. On 15/05/2017: Corrected. On 21/08/2017: Corrected. On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 16 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | Already Corrected. (Installation of fire alarm system has been completed and 1st T&C varification Inspection done by Accord on 15/10/2018 and 2nd T&C varification Inspection done by Accord on 04/04/2019.There were some deficiencies observed during T&C varification Inspection, which have already been corrected. We requested to Accord again for Verification Inspection.) | Jun 24 2016 | On 15/05/2017: Reviewed drawing was present during the follow-up inspection. Installation of the fire alarm system has not been completed yet. On 21/08/2017: Installation has been almost completed. Interfacing of Fire pump with FACP has not been completed yet. Factory shall provide proper 3rd party certification for the products used in the system during T&C. As-built drawings were not present on-site. On 27/11/2017: Installation has been completed and pending for T&C. On 12/03/2018: Factory has informed that installation of the system almost completed. Testing and commissioning of the system is pending. On 27/05/2018: Reportedly installation of the detection system is completed. Waiting for the testing and commissioning. On 04/04/2019: T&CVI found that installation certificate and record of completion are required. Verify the information used in the battery calculations and voltage drop calculations. Provide manufacturer’s product datasheets for all fire alarm equipment. Provide accurate 3rd party testing reports for fire alarm cabling. Provide control unit diagram(s) for all control equipment. Provide voltage drop calculations as required by NFPA 72. Install control unit batteries in a listed cabinet if required by the fire alarm manufacturer. Indicate the date of manufacture for all fire alarm control equipment batteries. Mount modules in back boxes if required by the fire alarm manufacturer. Provide a lock on the AC circuit breaker dedicated to the fire alarm system and provide “Fire Alarm” label on the circuit breaker. Enable piezo buzzer for the control equipment. Protect wiring entering or leaving control equipment panel(s). Provide a dedicated AC power supply from the MDB, directly to the fire alarm control equipment. Provide adequate fire alarm notification for all areas. Evacuation signal shall utilize a three-pulse temporal pattern. See detailed T&CVI Report. On 10-Dec-2020: As per Full-T&C, the system is Approved. For details, see the Full-T&C report. On 18/03/2024: Corrected. | Design within 4 months, install within 9 months | Corrected
Initial Inspection |  | 17 | Inspection, testing, and maintenance for the fire alarm system was not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | It is an integrated part of Fire alarm system & Corrected as per recommendation. | Jun 24 2016 | On 14-02-2017: It is an integrated part of fire alarm system. On 15/05/2017: It is an integrated part of fire alarm system. On 21/08/2017: Integrated part of FA system. On 27/11/2017: Integrated part of FA system. On 12/03/2018: Factory is maintaining a checklist but not properly. On 27/05/2018: Corrected. Factory is maintaining checklist and documents have been shown. On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 18 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Replace the single-station smoke alarms. Provide automatic smoke detection throughout the building in accordance with NFPA 72. | Corrected as per recommendation. Now the system running on test basis. | Jun 24 2016 | On 14-02-2017: It is an integrated part of fire alarm system. On 15/05/2017: It is an integrated part of fire alarm system. On 21/08/2017: Integrated part of FA system. On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. However, it is an integrated part of fire alarm system. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 19 | Inspection, testing, and maintenance records for the emergency lighting system were not available. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | Corrected as per recommendation | Dec 22 2015 | On 14-02-2017: Corrected. The factory is maintaining a checklist as per standard. On 15/05/2017: Corrected. On 21/08/2017: Corrected. On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 20 | New Finding: The building has an occupied floor greater than 10 meter (33 feet) and its not provided with standpipe system as per NFPA 14 & 20. | Provide standpipe and hose system as per NFPA 14 & 20. within 6 months | Already Corrected. (Installation of standpipe system has been completed and 1st T&C varification Inspection done by Accord on 15/10/2018 and 2nd T&C varification Inspection done by Accord on 04/04/2019.There were some deficiencies observed during T&C varification Inspection, which have already been corrected. We requested to Accord again for Verification Inspection.) | Apr 10 2016 | On 15/05/2017: In progress. Design was found in the factory. On 21/08/2017: Work in progress. Installation work is on-going. Fire pump set arrangement has been in process. On 27/11/2017: Installation has been completed and pending for T&C. On 12/03/2018: Modification work is going on. Factory has informed that modification will be completed within next month. On 27/05/2018: Installation work is in progress. On 04/04/2019: T&CVI found that, have pump acceptance testing completed for the electric fire pump. Provide adequately sized pump room detail in the as-built drawings for review. Adjust, repair or replace fire pump packing. Provide certified pressure gauge on the discharge side of the fire pumps. Provide spill containment for the diesel fuel storage tank serving the diesel fire pump (unless double walled). Remove shut-off valve on the diesel fuel return line for the diesel fire pump. Provide monitoring of all required fire pump signals. Confirm that the fuel system piping at the engine connection for the diesel fire pump is compliant. Correctly orient y-strainers vertically. Properly lubricate the operating stem of OS&Y valves. Provide eccentric tapered reducer on the suction side of each fire pump. Provide proper shut-down of the electric fire pump (run timer or manual). Provide manufacturer’s product datasheets for all system equipment. Provide waterflow monitoring (i.e. flow switch). Installation certificate and record of completion are required. See detailed T&CVI Report. On 10-Dec-2020: As per Full-T&C, the system is Approved. For details, see the Full-T&C report. On 18/03/2024: Corrected. | Within 6 months | Corrected
Follow Up Inspection |  | 21 | New Finding: Penetrations through floor/ceiling assemblies are found unsealed | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. |  | Jan 5 2016 | On 14-02-2017: Issue is reopened due to unsealed penetrations that have been found in all the floors in Building-I during follow-up inspection. On 15/05/2017:Corrected. On 21/08/2017: Corrected. On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. Note: Penetration has been found due to fire alarm and fire fighting installation work. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 22 | New finding: Hazardous materials (flammable liquid) storage area is not separated by fire rated construction. | Separate the hazardous materials /flammable gas storage room by a minimum 2-hr fire rated construction. Seal or protected all opening to maintain the required fire separation. | Corrected as per recommendation | Jun 24 2016 | On 15/05/2017:Corrected. On 21/08/2017: Corrected. On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. On 27/05/2018: Corrected as per previous follow-up. On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 23 | New Finding (4th Follow-up): Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected as per recommendation | Jul 21 2016 | On 15/05/2017:Corrected. On 21/08/2017: Corrected. On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. Note: Factory shall ensure adequate illumination at all required places. On 27/05/2018: Issued reopened. Adequate illumination has not been observed. Emergency light and exit signs were found switched off immediately after floor electrical power goes off in 3rd and 4th floor in building 1. On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 24 | New Finding: Dining room is not properly separated by fire rated construction with other Occupancies/Areas. Location: 5th floor of building 1. | Remove the dining area or if not possible then dining room shall be separated from other occupancies by a minimum 2-hr fire rated construction (wall, floor, slab etc.). Seal all penetrations and openings (door, window etc.) should be protected by 1.5-hr (90 min) fire rated materials to maintain the fire separation if required. Or Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. | Corrected as per recommendation | Mar 1 2017 | On 15/05/2017:It was found same as it was before. On 21/08/2017: Shifting works in a new location has been on-going . On 27/11/2017: Corrected. Shifted to building-2. On 12/03/2018: Corrected as per previous follow-up. On 27/05/2018: Issue reopened. Dining room was not found in 5th floor building 1 but dining room in building 2 on 1st floor is not separated from storage during Ramadan time. On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 03 months | Corrected
Follow Up Inspection |  | 25 | New Finding: The width of egress aisles is less than 36-in. Location: 1st floor of building 1. | Provide minimum aisle widths of 36-in. |  | Mar 1 2017 | On 15/05/2017: Corrected . On 21/08/2017: Corrected. On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. Note: Aisles marking shall be clear at all places. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 03 months | Corrected
Follow Up Inspection |  | 26 | New Finding (7th Follow-up): Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records on-site, in accordance with NFPA 10. |  | Mar 14 2017 | On 14-02-2017: New Finding. On 15/05/2017: Corrected . On 21/08/2017: Corrected. On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 27 | New Finding (9th FU): Heavy fire load has been observed at the production floors due to the presence of large area of unenclosed combustible storages. Location: Building-(I) , Ground Floor. | Provide defined storage areas and limit the storage arrangement as Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Corrected by defined storage areas have been provided as per recommendation in building 1 on 2nd & 3rd floor. | Sep 21 2017 | On 21/08/2017: New Finding On 27/11/2017: Corrected. On 12/03/2018: Issue reopened. Storage area has not been found as per recommendation for mentioned place. On 27/05/2018: Storage area has not been found as per recommendation in building 1 on 2nd & 3rd floor. On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 28 | New Finding (9th FU): Fire evacuation maps are not posted at the entrance of all exit stair. Location: Building-(II). | Fire evacuation maps shall be posted at the entrance to each exit stair. | Fire evacuation maps have been posted at the entrance to each exit stair. | Sep 21 2017 | On 21/08/2017: New Finding On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. Note: Factory shall provide proper evacuation plan at all required places. On 27/05/2018: Corrected. Recommendation of the last follow up applies. On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 29 | New Finding (9th FU): Emergency light has not been provided in the floor area. Location: Building-(II). | Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Emergency light has been provided in the floor area as recommended. Location: Building-(II). | Sep 21 2017 | On 21/08/2017: New Finding On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. Note: Factory shall provide emergency light at all required places. On 27/05/2018: Corrected. Recommendation of the last follow up also applies. On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 30 | New Finding (9th FU): Exit sign not provided at exit. Location: Building-(II). | Lighted exit signs shall be placed at entrance to an exit. Additional exit signs shall be placed throughout the facility anywhere the continuation of the egress is not obvious. Lighted exit signs shall be provided with either battery backup or uninterruptable power supply systems and shall be continuously illuminated. | Exit sign has been provided at all exit. Location: Building-(II). | Sep 21 2017 | On 21/08/2017: New Finding On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 31 | New Finding (9th FU): RMS room and kitchen are not separated from exit stair with fire rated construction. Location: Building-(II) , Ground Floor. | Provide mimnimum 2-hr rated fire separtion | RMS room and kitchen have been separated from exit stair with fire rated construction. Location: Building-(II) , Ground Floor. | Sep 21 2017 | On 21/08/2017: New Finding On 27/11/2017: Corrected. On 12/03/2018: Corrected as per previous follow-up. On 27/05/2018: Corrected On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 32 | New Finding (12th FU): The compressor room is not separated by fire-rated construction (openings, non-rated doors, penetrations). | Separate the compressor room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations | Already Corrected. The new compressor room has been separated by a minimum 2-hr fire-rated construction. | May 28 2018 | On 27/05/2018: New Finding On 04/04/2019: Corrected On 18/03/2024: Corrected. | Within 1 month | Corrected

## Electrical
Date
18-May-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | SPRING TRADE LTD., Konapara, Plot: 42,Zirani Bazar, B.K.S.P, Savar, Savar, Dhaka
Date of Inspection |  | 2014-05-03
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Oil cup below transformer breather is empty. | Fill the breather oil cup with transformer oil up to the required level as instructed by the manufacturer. Consult with transformer servicing company before performing the task. Establish a routine maintenance & inspection program for transformer as well as all other electrical equipment to ensure any future repetition of the occurrence. |  | Dec 20 2014 | On 22/12/2016: Corrected. | Within 1 Month | Corrected
Initial Inspection |  | 2 | Leakage current collector of the HT cable termination not connected to earth. | Connect the leakage current- collector of the HT cable to the earthing, otherwise, the insulation of the cable may get damaged due to leakage current. |  | Jul 30 2015 | On 18/12/2014: Corrected. | Within 1 Month | Corrected
Initial Inspection |  | 3 | HT service cable dropping from pole is not protected near the base of the pole, above ground level. | HT cable dropping from HT pole must be protected in steel pipe of required size at least 2m from the ground level to protect the cable from any physical damage. The cable should be supported on covered tray or ladder throughout its length up to the HT panel base-plate (except the part of the cable laid underground at a depth of at least 1 meter). |  | Sep 18 2014 | On 18/12/2014: Corrected. | Within 3 Months | Corrected
Initial Inspection |  | 4 | Barrier/separators between different phases are not installed. | Provide phase separators between poles of MCCB made of non combustible materials preferably use rubber having enough dielectric strength to insulate phases from each other. |  | Jan 9 2015 | On 22/12/2015: Corrected. | 1 Month | Corrected
Initial Inspection |  | 5 | Multiple cables connected at a terminal of the bus bar. | Remove all the multiple connections made at a single point of bus bar and connect individual branch cables to individual points on bus bar using individual lug according to the respective cable size. |  | Jan 16 2015 | On 22/12/2016: Corrected. | 3 Months | Corrected
Initial Inspection |  | 6 | Distribution panel not connected to earth. | Provide earth connection for body and doors of all metallic distribution boards using green cables preferably braid so that the metallic door remains at zero potential all the time. |  | Jul 30 2015 | On 18/12/2014: Corrected. | Within 1 Month | Corrected
Initial Inspection |  | 7 | Cables terminating to generator output terminal box are laid on floor. | Cable terminating at generator output terminal box must be supported on riser and protected. Install cable duct to protect the generator output cables and provide covers made of non-combustible material preferably metal to protect the cables’ insulation from any physical damage. |  | Sep 18 2014 | On 18/12/2014: Corrected. | Within 3 Months | Corrected
Initial Inspection |  | 8 | Generator frame connected to only one earth point. | Generator body must have two separate and distinct earth connections with minimum 35 sq.mm conductor. |  | Jul 30 2015 | On 18/12/2014: Corrected. | Within 1 Month | Corrected
Initial Inspection |  | 9 | Wires in panel are spliced and insulated with electrical tapes. | Wire joints in panels must be tightly connected using terminals or sockets crimped and insulated. Heat shrink tubes may be used for insulation. |  | Jan 16 2015 | On 22/12/2015: Corrected. | Within 1 Month | Corrected
Initial Inspection |  | 10 | Excessive lint deposit in cable duct. | Disconnect the power source of the cable laid into channel and clean dust and debris of all interior components. Establish a periodic cleaning program and maintain records of the activities. Provide cover made of non-combustible material on the channel for preventing ingress of dust and debris in future. |  | Nov 30 2015 | On 22/12/2015: Corrected. | 3 Months | Corrected
Initial Inspection |  | 11 | Transformers are guarded with wire mesh fencing. | Construct a fire rated room for the transformers. Assign a qualified engineer to design a required transformer room according to BNBC, Section-2.6.3. The transformer must be installed with barrier walls between transformer and other panels. The walls must be fire resistant and should have height up to the ceiling. The wall should have the provision for necessary ventilation and fire rated door on required side. |  | Oct 16 2015 | On 22/12/2015: Corrected. | 1 Month | Corrected
Initial Inspection |  | 12 | Panel base plates not installed. | Panel base-plate must be installed. Make circular hole at the base-plate of panels and provide cable gland according to the respective cable size for cable entry and exit so that the cables are not stressed on the sharp edges of the hole of panels. Provide covers (of non-combustible material) if any additional gap remains after installing cable glands. |  | Oct 2 2015 | On 22/12/2015: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 13 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. | Amend Electrical SLD properly. Mention all the modification there as present in the factory. |  | Apr 30 2016 | On 24/03/2016: Not corrected. New timeline is 30/04/2016. On 21/06/2016: Not corrected. On 26/09/2016: Not corrected. SLD is not matched with installation in some points. On 01/12/2016: Not corrected. On 14/02/2017: Not corrected. On 15/05/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 14 | New Finding: Lightning Protection System (LPS) drawing is unavailable. | Design LPS as built and share with Accord to get information about any necessary modification. |  | Oct 30 2015 | On 22/12/2015: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 15 | New Finding: Battery terminals are left open. | Use insulated rubber cap to cover all the battery terminals. |  | Jan 16 2015 | On 22/12/2015: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 16 | New Finding: Transformer silica gel is discolored. | Replace silica gel by a new one; or dry it under sun and reuse it, if color regains. |  | Dec 20 2014 | On 22/12/2015: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 17 | New Finding: Transformer arcing horns are not aligned. | Align all the arcing horns. |  | Dec 20 2014 | On 22/12/2015: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 18 | New Finding: Cable channels are filled with fluffs (lint/dust). | Clean all the cable channels; then seal them with metallic cover (you may use checkered/ perforated plate at the bottom). But ensure that you have used proper sized cable for all of your electrical loads. |  | Oct 2 2015 | On 24/03/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 19 | New Finding: HT cables laid on sub station room floor. | Use a cable tray to ensure adequate support. This must not be routed/supported through the equipment' working clearance area. |  | Oct 2 2015 | On 22/12/2015: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 20 | New Finding: Hotspot found at electrical panel. | Need to check the connected load, check the thermal issue. |  | Jan 16 2015 | On 24/03/2016: Corrected. No hotspot found. | 1 Month | Corrected
Follow Up Inspection |  | 21 | New Finding: Panel/distribution boxes are inaccessible or can not be opened to perform any maintenance work. | Take necessary initiative thus every panel/distribution board can be easily accessible. |  | Jul 20 2015 | On 22/12/2015: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 22 | New Finding: Electric socket outlet is near to ground level at day care center. | Install electrical socket outlet out of children reach or install GFCI. |  | Dec 20 2014 | On 22/12/2015: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 23 | New Finding: Cable laid on floor in boiler room. | Remove cable & socket near boiler and socket should not install bellow 200 mm from floor level. |  | Dec 20 2014 | On 22/12/2015: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 24 | New Finding: Distribution panel installed under stairways. | The distribution panel should not be installed under the stairways. It shall be located in a confined place with entrance control mechanism where only authorized personnel can have access. |  | Jul 20 2015 | On 22/12/2015: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 25 | New Finding: Maintenance record doesn’t reflect with house keeping (fake record). | Maintenance in charge/safety officer should check the record with housekeeping. |  | Jan 1 2015 | On 24/03/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 26 | New Finding: No/inadequate rubber (insulation) mat on the working area of distribution board/panel. | Put electrical insulation (rubber mat) on the working area of each electrical installation (transformer/LT panel/MDB/DB/SDB/other manual operated machineries). |  | Jan 16 2015 | On 22/12/2015: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding: Power cables are bent excessively. | Avoid power cable bending in electrical system; in unavoidable case bend cables without any stress but not less than 135 degree. |  | Jul 20 2015 | On 22/12/2015: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 28 | New Finding: Earth pits are not identifiable. | Identify each earth pit and mark it for periodic maintenance purpose. |  | Jan 16 2015 | On 22/12/2015: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding: MCCBs are not adjusted accordingly. | Adjust all the MCCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. |  | Jan 23 2015 | On 22/12/2015: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 30 | New Finding: Electrical terminals are left open. | Cover all the electrical terminals by graded insulator cap. |  | Jan 16 2015 | On 22/12/2015: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: Circuit is drawn from bus bar without circuit breaker or any protective means. | For distribution board, along with the main circuit breaker all outgoing circuits shall have individual outgoing circuit breaker. |  | Apr 30 2016 | On 24/03/2016: Not corrected. New timeline is 30/04/2016. On 21/06/2016: Not corrected. Factory is behind the timeline. On 26/09/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 32 | New Finding: Electric safety training program is not initiated/conducted. | Electrical safety training and awareness program for the electrical personal and workers must be initiated and recorded. |  | Feb 20 2016 | On 24/03/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: Earth pit resistance record is unavailable. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. |  | Apr 20 2016 | On 24/03/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 34 | New Finding: Lightning Protection System (LPS) has not installed yet. | Install LPS for your factory according to the proposed design. |  | Mar 20 2016 | On 24/03/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 35 | New Finding: Hot spots at terminations inside panel. | Find the cause of excessive heat-rise which may be the overloading, loose connection, unbalanced load and others and take action immediately. Thermo graphic scanning for the entire electrical system must be performed on a bi-annual basis and recorded. |  | Oct 31 2016 | On 01/12/2016: Corrected. No hot spot is found during inspection. | 1 Month | Corrected
Follow Up Inspection |  | 36 | New Finding: Light in store room/storage areas is uncovered. | Lights in store room/storage areas shall be covered. |  | Oct 31 2016 | On 01/12/2016: Corrected. In store rooms no uncovered light is found. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Multiple circuits are connected at transformer low tension end. | A single circuit must be connected at transformer low tension end. |  | Mar 30 2017 | On 14/02/2017: Not corrected. Time extension is given till 30/03/2017. On 15/05/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 38 | New Finding: Circuit breakers (CBs) are not adjusted per load demand. | All the CBs must be adjusted per connected load current; if adjustment is not possible, replacement will be the only way. |  | Sep 25 2017 | On 27/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 39 | New Finding: LPS needs modifications. Air terminals are missing at some points, mesh width is more than 50 ft at some places and no class II materials are used where class II materials are mandatory. Again, no as-built drawing is found. | Need to modify the installation of LPS and prepare an as-built drawing of all LPS installations. |  | Sep 25 2017 | On 27/11/2017: Not corrected. Need Class II materials down conductor where building height is more the 75 feet. On 12/03/2018: Corrected. As roof level is under 75 feet and other stair cases of above 75 feet are properly installed using required class type material. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: Periodicity of transformer oil test (dielectric strength test) survey is not continued. | Transformer oil test (dielectric strength test for oil) shall be done once in a year. |  | Sep 25 2017 | On 27/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: No LOTO equipment were found. No LOTO (Lock-Out-Tag-Out) policy is introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement LOTO policy with LOTO (Lock-Out-Tag-Out) equipment instead of any other means to ensure safety of the personnel during any maintenance. |  | Sep 25 2017 | On 27/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Base/top plates of generator terminal box and panel box are removed to allow cable entry. | Base plates must be installed, at all time, and cables entering panel must be firmly fixed with cable gland (and cable tray where required). |  | Sep 25 2017 | On 27/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Cable for floor to floor are hanging inside conduits. No cable ladder is used to support the power cables. | Cables must be tied with support at a certain interval when laid vertically (need to take care of floor to floor penetration issue as well). |  | Sep 25 2017 | On 27/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Hazardous lights in store room/storage areas are uncovered. | Hazardous lights in store room/storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. |  | Sep 25 2017 | On 27/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Electrical power cables are not identified properly. | Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables used in the system according to SLD. |  | Sep 25 2017 | On 27/11/2017: Not corrected. On 12/03/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Circuit is drawn from bus bar without any protective means (for PFI). | Each electrical circuit must be drawn from distribution board busbar using a proper type protection arrangement (MCCB/MCB). |  | Apr 30 2018 | On 27-05-2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Large exhaust fans are controlled directly by MCB. | Induction motor driven fans (which has high inrush current) must not be operated directly using MCB; Direct-On-Line (DoL) type control switch must be used. |  | Dec 26 2023 | On 19/02/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 48 | New Finding: Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. | We have got approval of the Single Line Diagram (SLD) finally on 08/10/2025 by RSC. We have already started the electrical remediation work as per the corrected SLD and hopefully it will be completed fully by end of February 2026. | Apr 28 2024 | On 14/07/2024: Not corrected. SLD review status was "Need modification" on 25 June 2024. Mismatch has been observed in field with SLD (ECC & CB information mismatch, individual overload protection mismatch etc). Factory shall submit SLD to RSC after correction as per review comments within 24 July 2024. On 03/08/2025: Not corrected. SLD was "Accepted" by RSC in August 2024. However, following an official meeting with the RSC engineer on 24 July 2025, the factory was advised to resubmit the SLD to RSC for further review (due to certain critical information missing in Accepted drawing compared to as built condition). Currently, the factory is working on preparing the as-built SLD for submission. RPO Comments:On 02-March-2026- Remediation needs to be completed before next follow up inspection. | 2 Months | In Progress
Follow Up Inspection |  | 49 | New Finding: Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07 m) around the transformer (and related electrical installations) must be maintained. | We have already started the electrical remediation work as per the corrected SLD and hopefully it will be completed fully by end of February 2026. | Sep 18 2024 | On 03/08/2025: Corrected. | 2 Months | Corrected

## Boiler
Date
18-May-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | SPRING TRADE LTD., Konapara, Plot: 42,Zirani Bazar, B.K.S.P, Savar, Savar, Dhaka
Date of Inspection |  | 2022-03-24
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 6293 | Necessary technical documents (Water treatment design and calculation, Electrical wiring diagram, commissioning documents) are not available to verify boiler design and operation parameters | Documentation including manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, boiler operational & maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of boiler. | We have already marked the Low Low water Level (LLWL) properly on the water level gauge glass system. | Oct 27 2025 | Comments on 28-Sep-2025: Factory given timeline is not accepted. The new timeline is 27-Nov-2025. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 6293 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed emergency stop push switch at the outside near the entrance and on the boiler control panel. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 6293 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the Low Low water Level (LLWL) properly on the water level gauge glass system. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. The gauge glass should be marked on a separate arrangement beside the gauge glass, not on the gauge glass. Besides, The lebeling should also be incorporated along with the marking. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 6293 | The boiler manufacturer's nameplate was not available on the boiler. | The boiler manufacturer's nameplate shall be available on the boiler with accurate technical information and boiler manufacturer's name in standard language. | We have already installed manufacturers nameplate on the boiler. | Sep 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 6293 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | We have already rearranged the Boiler Safety Valve outlet line. | Sep 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 6293 | Installed pressure gauge was inadequate in dial size and pressure rating according to manufacturing standard. | An appropriate pressure gauge according to Bangladesh boiler regulation (BBR)/manufacturing standard/any standard recognized by the CIoB. shall be provided. | We have already installed proper dial size steam pressure gauge and pressure rating according to manufacturing standard. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 6293 | Discharge of safety valve was not free from danger of scalding. | Safety valve outlet line shall not affect emergency discharge path or discharge of safety valve shall be free from danger of scalding. | We have already rearranged the discharge line of the boiler safety valve and now outside area is free from danger of scalding. | Sep 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 6294 | Necessary technical documents (Water treatment design and calculation, Electrical wiring diagram, commissioning documents) are not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, boiler operational & maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of boiler. | We will modify/rearrange the boilers technical documents (water treatment design and calculation, electrical wiring diagram, and commissioning document etc.) by December 31, 2025. | Oct 27 2025 | Comments on 28-Sep-2025: Factory given timeline is not accepted. The new timeline is 27-Nov-2025. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 9 | BB 6294 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed emergency stop push switch at the outside near the entrance and on the boiler control panel. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 6294 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the Low Low water Level (LLWL) properly on the water level gauge glass system. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. The gauge glass should be marked on a separate arrangement beside the gauge glass, not on the gauge glass. Besides, The lebeling should also be incorporated along with the marking. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 6294 | The boiler manufacturer's nameplate was not available on the boiler. | The boiler manufacturer's nameplate shall be available on the boiler with accurate technical information and boiler manufacturer's name in standard language. | We have already installed manufacturers nameplate on the boiler. | Sep 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 12 | BB 6294 | Boiler Safety Valve outlet line was not directed outside of the boiler room | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | We have already rearranged the Boiler Safety Valve outlet line, now the safety valve outlet line is directed outside of the boiler room. | Sep 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 13 | BB 6294 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | We have already installed proper dial size steam pressure gauge and pressure rating according to manufacturing standard. | Sep 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 14 | BB 7856 | Necessary technical documents (Water treatment design and calculation, Electrical wiring diagram, P & ID, commissioning documents) are not available to verify boiler design and operation parameters | Documentation including manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, boiler operational & maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of boiler. | We will modify/rearrange the boilers technical documents (water treatment design and calculation, electrical wiring diagram, and commissioning document etc.) by December 31, 2025. | Oct 27 2025 | Comments on 28-Sep-2025: Factory given timeline is not accepted. The new timeline is 27-Nov-2025. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 15 | BB 7856 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed emergency stop push switch at the outside near the entrance and on the boiler control panel. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 16 | BB 7856 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the Low Low water Level (LLWL) properly on the water level gauge glass system. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. The gauge glass should be marked on a separate arrangement beside the gauge glass, not on the gauge glass. Besides, The lebeling should also be incorporated along with the marking. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 17 | BB 7856 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | We have already rearranged the Boiler Safety Valve outlet line, now the safety valve outlet line is directed outside of the boiler room. | Sep 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 18 | BB 6293 | Drainage arrangement was not installed or installed in an inadequate manner for one or more safety valves. | Drainage arrangement must be installed for all safety valves as per manufacturer published guideline or at the lowest point of outlet line. | We have already rearranged the Boiler Safety Valve outlet line, now the safety valve outlet line is directed outside of the boiler room. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 19 | BB 6294 | Drainage arrangement was not installed or installed in an inadequate manner for one or more safety valves. | Drainage arrangement must be installed for all safety valves as per manufacturer published guideline or at the lowest point of outlet line. | We have already rearranged the Boiler Safety Valve outlet line, now the safety valve outlet line is directed outside of the boiler room. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 20 | BB 7856 | Drainage arrangement was not installed or installed in an inadequate manner for one or more safety valves. | Drainage arrangement must be installed for all safety valves as per manufacturer published guideline or at the lowest point of outlet line. | We have already rearranged the Boiler Safety Valve outlet line, now the safety valve outlet line is directed outside of the boiler room. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 21 | BB 6293 | Steam leakage was observed in the boiler safety valve. | The steam leakage shall be repaired to prevent burn hazard. | We have already repaired the Boiler Safety Valve to prevent the steam leakage. | Sep 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 22 | BB 6294 | Steam leakage was observed in the boiler safety valve. | The steam leakage shall be repaired to prevent burn hazard. | We have already repaired the Boiler Safety Valve to prevent the steam leakage. | Sep 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 23 | BB 6293 | The control panel cabinet does not specify the names of all boiler interlock alarm functions | Names of boiler interlock alarm functions should be specified on the cabinet. | We have rearranged the control panel cabinet, installed a device for functioning the boilers interlock alarm and now the system is fully functional. | Nov 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 3 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 24 | BB 6294 | The control panel cabinet does not specify the names of all boiler interlock alarm functions. | Names of boiler interlock alarm functions should be specified on the cabinet. | We have rearranged the control panel cabinet, installed a device for functioning the boilers interlock alarm and now the system is fully functional. | Nov 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 3 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 25 | BB 6293 | There was no visual flame monitoring system in place. | A visual flame monitoring system is required to be installed. | We have already installed a visual flame monitoring system. | Sep 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 26 | BB 6294 | There was no visual flame monitoring system in place. | A visual flame monitoring system is required to be installed. | We have already installed a visual flame monitoring system. | Sep 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 27 | BB 7856 | There was no visual flame monitoring system in place. | A visual flame monitoring system is required to be installed. | We have already installed a visual flame monitoring system. | Sep 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 28 | BB 6293 | There is no drainage available for water level gauge glass | A suitable discharge pipe shall be fitted with each water gauge drain cock or valve | We have already installed a proper drainage channel for the water level gauge glass. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 29 | BB 6294 | There is no drainage available for water level gauge glass | A suitable discharge pipe shall be fitted with each water gauge drain cock or valve | We have already installed a proper drainage channel for the water level gauge glass. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 30 | BB 7856 | There is no drainage available for water level gauge glass | A suitable discharge pipe shall be fitted with each water gauge drain cock or valve | We have already installed a proper drainage channel for the water level gauge glass. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 31 | BB 6293 | The water level gauge glass was not protected. | The water level gauge glass should be properly protected with guard rods or covered by suitable protection housing. | We have already protected the water lavel gauge glass for fafety properly. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 32 | BB 6294 | The water level gauge glass was not protected | The water level gauge glass should be properly protected with guard rods or covered by suitable protection housing. | We have already protected the water lavel gauge glass for fafety properly. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | Functional test inspection | 33 | BB 6293 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have already installed the steam pressure limiter for the boiler and now the preasure limiter is fully functional. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 34 | BB 6294 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have already installed the steam pressure limiter for the boiler and now the preasure limiter is fully functional. | Sep 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 35 | BB 7856 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have already installed the steam pressure limiter for the boiler and now the preasure limiter is fully functional. | Sep 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 36 | BB 6293 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler | The Low Low Water (LLW) level tripping mechanism should be functional. | We have already installed LLW level tripping machanism/device for functioning the boilers interlock Low Low Water (LLW) level trip of the boiler and now the system is fully functional. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 37 | BB 6294 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler | The Low Low Water (LLW) level tripping mechanism should be functional. | We have already installed LLW level tripping machanism/device for functioning the boilers interlock Low Low Water (LLW) level trip of the boiler and now the system is fully functional. | Sep 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 38 | BB 6294 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | We have already installed Air Pressure Limiter for the boiler and now the system is fully functional. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 39 | BB 7856 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | We have already installed Air Pressure Limiter for the boiler and now the system is fully functional. | Oct 27 2025 | Comments on 28-Sep-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification