## Structural
Date
17-May-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Torque Design Ltd. (Previously Torque Fashions Ltd.), Paragram, Ashulia,Ashulia Bazar,Dhaka, Bangladesh., Dhaka
Date of Inspection |  | 2014-05-12
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | ITEM - 01 : Connection details to be further investigated for capcity against uplift. | Priority : 02 - Factory Engineer to review all steel structure anchorage details on site & provide design for any corrective works required. | Corrected | Jun 25 2015 | ON 19/04/2015: Factory Engineer is working on it. ON 18/05/2016: This issue will be covered in EA. Factory has not submitted the revised EA report with necessary correction as per review mail sent on 11-May-2016. On 23/10/2016: Factory management have conducted Engineering Assessment and Engineering Assessment got acceptance from Accord based on submitted documents. During EA verification some discrepancies have observed. A discrepancy report has sent along with this report. Factory requires re-submit EA report along with necessary correction which mentioned in EA verification report within 22-Nov-2016. Issue requires to cover in EA report. On 17/04/2017: As per EA verification report, factory submitted the necessary documents to ACCORD which was accepted on 12/02/2017. On 16-11-2017: Corrected from previous follow-up report .Factory engineer reviewed all those steel structure anchorage details on site &provided design for corrective works. Factory submitted DEA to Accord which got acceptance on 12-02-2017. On 19/04/2018: Corrected in previous follow up inspection. Factory management got re-acceptance on 12/02/2017. During inspection retrofitting works were found completed. On 05-Sep-2021: Found corrected in previous follow up inspection. Factory has completed remedial works and received "Letter of recognition" from Accord. On 08-Aug-2023: Corrected Previously. EA already been accepted by Accord. On 27-Jul-2025: Corrected previously. Buildings 1 & 2 have been renamed as Shed 1 and Building 1 respectively, and from this inspection, these two structures have been covered under linked ID: 23787. Buildings 3, 4, 5, and 6 have been renamed as Shed 1, Shed 2, Shed 3, and Shed 4 respectively. This CAP item is not applicable for Shed 1 (previously Building 1), but is applicable for Shed 1 (previously Building 3) and Shed 4 (previously Building 6). | Within 6 weeks | Corrected
Initial Inspection |  | 2 | ITEM - 01 : Connection details to be further investigated for capacity against uplift. | Priority : 03 -Implement any corrective measures identified by Factory Engineer. | Corrected | Jun 25 2015 | ON 19/04/2015: As above ON 18/05/2016: This issue will be covered in EA. Factory has not submitted the revised EA report with necessary correction as per review mail sent on 11-May-2016. On 23/10/2016 : Factory management have conducted Engineering Assessment and Engineering Assessment got acceptance from Accord based on submitted documents. During EA verification some discrepancies have observed. A discrepancy report has sent along with this report. Factory requires re-submit EA report along with necessary correction which mentioned in EA verification report within 22-Nov-2016. On 17/04/2017: As per EA verification report, factory submitted the necessary documents to ACCORD which was accepted on 12/02/2017. As per accepted EA, retrofitting is required to building- 1,3,&6. During inspection, retrofitting work was found on going. This issue will be corrected after completion of retrofitting work. On 16-11-2017:Retrofiting work was found completed with some error and mismatch between field condition and retrofitting drawing accepted by Accord both for building 1&3.Factory is required to repaired the mismatched retrofitted sections as per accepted drawings. On 19/04/2018: Corrected in previous follow up inspection. Factory management got re-acceptance on 12/02/2017. During inspection retrofitting works were found completed as per accepted drawing. QC certificate was provided by consultant also. On 05-Sep-2021: Found corrected in previous follow up inspection. Factory has completed remedial works and received "Letter of recognition" from Accord. On 08-Aug-2023: Corrected Previously. Remedial works has been done by the factory and accepted by accord. On 27-Jul-2025: Corrected previously. This CAP item is not applicable for Shed 1 (previously Building 1), but is applicable for Shed 1 (previously Building 3) and Shed 4 (previously Building 6). | Within 6 month | Corrected
Initial Inspection |  | 3 | ITEM - 02 : Diaphragm action & overall stability of Building # 01 to be checked in more details by Factory Engineer. | Priority : 03 - Factory Engineer already review the lateral stability of Building # 01 after getting the DEA. | Corrected | Mar 31 2016 | ON 19/04/2015:As above ON 18/05/2016: This issue will be covered in EA. Factory has not submitted the revised EA report with necessary correction as per review mail sent on 11-May-2016. On 23/10/2016 : Factory management have conducted Engineering Assessment and Engineering Assessment got acceptance from Accord based on submitted documents. During EA verification some discrepancies have observed. A discrepancy report has sent along with this report. Factory requires re-submit EA report along with necessary correction which mentioned in EA verification report within 22-Nov-2016. On 17/04/2017: As per EA verification report, factory submitted the necessary documents to ACCORD which was accepted on 12/02/2017. On 16-11-2017:Corrected from previous report .Factory submitted EA to accord which got acceptance on 12-02-2017. On 19/04/2018: Corrected in previous follow up inspection. Factory management got re-acceptance on 12/02/2017. During inspection retrofitting works were found completed as per accepted drawing. QC certificate was provided by consultant also. On 05-Sep-2021: Found corrected in previous follow up inspection. Factory has completed remedial works and received "Letter of recognition" from Accord. On 08-Aug-2023: Corrected previously. Stability check has been covered in the accepted EA. On 27-Jul-2025: Not applicable for this ID. | Within 6 month | Corrected
Initial Inspection |  | 4 | ITEM - 02 : Diaphragm action & overall stability of Building # 01 to be checked in more detail by Factory Engineer. | Priority : 03 -Any corrective measures identified to implemented by our engineer. | Corrected | Jun 25 2015 | ON 19/04/2015:As above ON 18/05/2016: Corrective measures will be implemented after EA approval. Factory has not submitted the revised EA report with necessary correction as per review mail sent on 11-May-2016. On 23/10/2016 : Factory management have conducted Engineering Assessment and Engineering Assessment got acceptance from Accord based on submitted documents. During EA verification some discrepancies have observed. A discrepancy report has sent along with this report. Factory requires re-submit EA report along with necessary correction which mentioned in EA verification report within 22-Nov-2016. On 17/04/2017: As per EA verification report, factory submitted the necessary documents to ACCORD which was accepted on 12/02/2017. As per accepted EA, retrofitting is required to building-1. During inspection, retrofitting work was found on going. This issue will be corrected after completion of retrofitting work. On 16-11-2017: Factory submitted EA to Accord which EA includes all diaphragm action ,overall stability check and corrective action identification .EA has been accepted by Accord on 12--02- 2017.As per EA Retrofitting work was required for Factory building -1 &3 .During after retrofitting inspection, retrofitting work was found completed with major error and mismatch between field condition and retrofitting drawing accepted by Accord both for building 1&3.Factory is required to complete all retrofitting works as per drawing and design of accepted EA . On 19/04/2018: Factory management got re-acceptance on 12/02/2017. During inspection retrofitting works were found completed as per accepted drawing. QC certificate was provided by consultant also. On 05-Sep-2021: Found corrected in previous follow up inspection. Factory has completed remedial works and received "Letter of recognition" from Accord. On 08-Aug-2023: Corrected previously. Remedial works has been done. On 27-Jul-2025: Not applicable for this ID. | Within 6 month | Corrected
Follow Up Inspection |  | 5 | New Finding-1: Building # 01, Where a connection is visible at the head of the column but cover is so small that pullout resistance would be negligible. | The facility responsible person already confirmed the head of column cover and the facility already recover the DEA. | Corrected | Mar 31 2016 | ON 19/04/2015:All these issue should be covered under engineering assessment. ON 18/05/2016:This issue will be covered in EA. Factory has not submitted the revised EA report with necessary correction as per review mail sent on 11-May-2016. On 23/10/2016 :Factory management have conducted Engineering Assessment and Engineering Assessment got acceptance from Accord based on submitted documents. During EA verification some discrepancies have observed. A discrepancy report has sent along with this report. Factory requires re-submit EA report along with necessary correction which mentioned in EA verification report within 22-Nov-2016. On 17/04/2017: As per EA verification report, factory submitted the necessary documents to ACCORD which was accepted on 12/02/2017. As per accepted EA, retrofitting is required to building- 1.During inspection, retrofitting work was found on going. This issue will be corrected after completion of retrofitting work. On 16-11-2017:This column was found as a retrofitted column .Retrofitting work of that column was found satisfactory. On 19/04/2018: Corrected in previous follow up inspection. Factory management got re-acceptance on 12/02/2017. During inspection retrofitting works were found completed as per accepted drawing. QC certificate was provided by consultant also. On 05-Sep-2021: Found corrected in previous follow up inspection. Factory has completed remedial works and received "Letter of recognition" from Accord. On 08-Aug-2023: Corrected previously. This issue has been covered in the accepted EA. On 27-Jul-2025: Not applicable for this ID. | Within 6 weeks | Corrected
Follow Up Inspection |  | 6 | New Finding-2: Truss-end connection in Building # 06, An arbitrary attempt has been made to connect down, but the bricks are loose. | After getting the Details Engineering Assessment (DEA) facility appointed Engineering Firm asses &build an arbitrary column should make connection down the ground. | Corrected | Mar 31 2016 | ON 19/04/2015: As above ON 18/05/2016: This issue will be covered in EA. Factory has not submitted the revised EA report with necessary correction as per review mail sent on 11-May-2016. On 23/10/2016 : Factory management have conducted Engineering Assessment and Engineering Assessment got acceptance from Accord based on submitted documents. During EA verification some discrepancies have observed. A discrepancy report has sent along with this report. Factory requires re-submit EA report along with necessary correction which mentioned in EA verification report within 22-Nov-2016. On 17/04/2017: As per EA verification report, factory submitted the necessary documents to ACCORD which was accepted on 12/02/2017. As per accepted EA,factory is required either to complete retrofitting to building-6 or to demolish it. During inspection, retrofitting work was found on going. This issue will be corrected after completion of retrofitting work. On 16-11-2017:During inspection building #6 was found demolished. On 19/04/2018: Corrected in previous follow up inspection. On 05-Sep-2021: Found corrected in previous follow up inspection. On 08-Aug-2023: Corrected previously. building has been demolised. On 27-Jul-2025: Corrected previously. The factory has constructed a new single storied steel shed named Shed 4 (1724 sft) at that place. See item 22. | Within 6 weeks | Corrected
Follow Up Inspection |  | 7 | New Findings-3: Building # 03, where a roof truss is held down to the culumn only by a small fillet weld between T & an angle section. | After getting the Details Engineering Assessment (DEA) facility Engineering Firm asses roof truss column fillet weld between T & angle. | Corrected | Mar 31 2016 | ON 19/04/2015:As above ON 18/05/2016: This issue will be covered in EA. Factory has not submitted the revised EA report with necessary correction as per review mail sent on 11-May-2016. On 23/10/2016 : Factory management have conducted Engineering Assessment and Engineering Assessment got acceptance from Accord based on submitted documents. During EA verification some discrepancies have observed. A discrepancy report has sent along with this report. Factory requires re-submit EA report along with necessary correction which mentioned in EA verification report within 22-Nov-2016. On 17/04/2017: As per EA verification report, factory submitted the necessary documents to ACCORD which was accepted on 12/02/2017. As per accepted EA,retrofitting is required to building-03. However, Factory has submitted revised retrofitting drawing to ACCORD which is under review till inspection date. On 16-11-2017:Factory submitted EA to accord which covered this issue .As per accepted EA, retrofitting works were suggested for building 1&3 .After retrofitting completion , From retrofitting verification it was observed that retrofitting works were not matching with accepted drawing for both building 1&3 . Truss thickness ,bracing etc. were not matched with drawing for building 3 .Factory is required to complete all retrofitting work as per accepted drawing . On 19/04/2018: Factory management got re-acceptance on 12/02/2017. During inspection retrofitting works were found completed as per accepted drawing. QC certificate was provided by consultant also. On 05-Sep-2021: Found corrected in previous follow up inspection. Factory has completed remedial works and received "Letter of recognition" from Accord. On 08-Aug-2023: Corrected Previously. Remidial works has been done by the factory. On 27-Jul-2025: Corrected previously. | Within 6 weeks | Corrected
Follow Up Inspection |  | 8 | New Findings-4: Building # 01, Steel rebar visible, bent over the truss end. Its unclear whether such details are present at other location accross the side. | As per facility visit (Building # 01) Steel rebar visible, bent over the truss end. Its unclear whether such details are present at other location across the side. | Corrected | Jun 25 2015 | ON 19/04/2015:As above ON 18/05/2016:This issue will be covered in EA. Factory has not submitted the revised EA report with necessary correction as per review mail sent on 11-May- 2016. On 23/10/2016: Factory management have conducted Engineering Assessment and Engineering Assessment got acceptance from Accord based on submitted documents. During EA verification some discrepancies have observed. A discrepancy report has sent along with this report. Factory requires re-submit EA report along with necessary correction which mentioned in EA verification report within 22-Nov-2016. On 17/04/2017: As per EA verification report, factory submitted the necessary documents to ACCORD which was accepted on 12/02/2017. As per accepted EA,retrofitting is required to building-01.During inspection, retrofitting work was found on going. This issue will be corrected after completion of retrofitting work. On 16-11-2017:Retrofitting was done in building 1 .Those steel rebar were not found as bent over truss end , .Those trusses were repaired by factory . On 19/04/2018: Corrected in previous follow up inspection. Factory management got re-acceptance on 12/02/2017. During inspection retrofitting works were found completed as per accepted drawing. QC certificate was provided by consultant also. On 05-Sep-2021: Found corrected in previous follow up inspection. Factory has completed remedial works as per Accord acceptance drawings and received "Letter of recognition" from Accord. On 08-Aug-2023: Correected previously. On 27-Jul-2025: Not applicable for this ID. | Within 6 weeks | Corrected
Follow Up Inspection |  | 9 | New Finding-5: Building # 01, First pitch of the building where no bracing is present & the connections between parlins & roof sheeting may not be sufficient for diaphragm action. | After getting the Details Engineering Assesment (DEA) facility Engineering Firm asses & first pitch of the building use the bracing the roof sheeting & parlin as sufficient for diaphram action. | Corrected | Mar 31 2016 | ON 19/04/2015:As above ON 18/05/2016:This issue will be covered in EA. Factory has not submitted the revised EA report with necessary correction as per review mail sent on 11-May-2016. On 23/10/2016: Factory management have conducted Engineering Assessment and Engineering Assessment got acceptance from Accord based on submitted documents. During EA verification some discrepancies have observed. A discrepancy report has sent along with this report. Factory requires re-submit EA report along with necessary correction which mentioned in EA verification report within 22-Nov-2016. On 17/04/2017: As per EA verification report, factory submitted the necessary documents to ACCORD which was accepted on 12/02/2017. As per accepted EA,retrofitting is required to building-01.During inspection, retrofitting work was found on going. This issue will be corrected after completion of retrofitting work. On 16-11-2017:Retrofiting work was found completed with major error and mismatch between field condition and retrofitting drawing accepted by Accord both for building 1&3. On 19/04/2018: Factory management got re-acceptance on 12/02/2017. During inspection retrofitting works were found completed as per accepted drawing. Bracings were also installed as per recommendation. QC certificate was provided by consultant also. On 05-Sep-2021: Found corrected in previous follow up inspection. Factory has completed remedial works as per Accord acceptance drawings and received "Letter of recognition" from Accord. On 08-Aug-2023: Correected previously. Remedial works has been completed as per accepted EA. On 27-Jul-2025: Not applicable for this ID. | Within 6 months | Corrected
Follow Up Inspection |  | 10 | New Finding-6: Building # 01, Extarnal view showing the lightweight roofing which may provide insufficient lateral stiffness againest wind actions. | After getting the details engineering assesment (DEA) facility already done this issue. | Corrected | Mar 31 2016 | ON 19/04/2015:As above ON 18/05/2016:This issue will be covered in EA. Factory has not submitted the revised EA report with necessary correction as per review mail sent on 11 May-2016. On 23/10/2016: Factory management have conducted Engineering Assessment and Engineering Assessment got acceptance from Accord based on submitted documents. During EA verification some discrepancies have observed. A discrepancy report has sent along with this report. Factory requires re-submit EA report along with necessary correction which mentioned in EA verification report within 22-Nov-2016. On 17/04/2017: As per EA verification report, factory submitted necessary documents to ACCORD. On 17/04/2017: As per EA verification report, factory submitted the necessary documents to ACCORD which was accepted on 12/02/2017. As per accepted EA,retrofitting is required to building-01. During inspection, retrofitting work was found on going. This issue will be corrected after completion of retrofitting work. On 16-11-2017: Factory submitted DEA to Accord which DEA includes all lateral stiffness against wind action ,diaphragm action ,overall stability check and corrective action identification .DEA has been accepted by Accord on 12--02-2017.As per DEA Retrofitting work was required for Factory building -1 &2 .During after retrofitting visit retrofitting work was found completed with major error and mismatch between field condition and retrofitting drawing accepted by Accord both for building 1&3.Factory is required to finish all retrofitting works as per drawing and design of accepted DEA . On 19/04/2018: Factory management got re-acceptance on 12/02/2017. During inspection retrofitting works were found completed as per accepted drawing. QC certificate was provided by consultant also. On 05-Sep-2021: Found corrected in previous follow up inspection. Factory has completed remedial works as per Accord acceptance drawings and received "Letter of recognition" from Accord. On 08-Aug-2023: Correected previously. On 27-Jul-2025: Not applicable for this ID. | Within 6 months | Corrected
Follow Up Inspection |  | 11 | New Finding-7: Building # 02, No water proofing was observed on the roof of the concrete building, although no ponding or sign of the water ingress were on site, the facility owner may wish to consider applying a water proofing embrace. | The facility responsible person agree to make & confirm the water proofing membrane applying. | Corrected | Jun 25 2015 | ON 19/04/2015: As above ON 18/05/2016: This issue will be covered in EA. Factory has not submitted the revised EA report with necessary correction as per review mail sent on 11-May-2016. On 23/10/2016: No water proofing material is installed yet. On 17/04/2017: A water proofing layer was observed on roof of building-2. . On 16-11-2017: Corrected from previous follow-up report .During inspection waterproofing was observed on rooftop of building 2 . On 19/04/2018: Corrected in previous follow up inspection. Waterproofing observed on roof top. On 05-Sep-2021: Found corrected in previous follow up inspection. On 08-Aug-2023: Corrected previously. Water proofing has been applied by the factory. On 27-Jul-2025: Not applicable for this ID. | Within 6 months | Corrected
Follow Up Inspection |  | 12 | New Finding-8: Horizontal extension in front of Building#01 at south side | The building Engineer is required to carry out Engineering Assesment (EA) for the horizontal extension following BNBC; suggest necessery remedial measures and submit the EA documents to the RSC for review. | The horizontal extension was demolished | Sep 22 2023 | On 08-Aug-2023: During inspection extended shed is observed in front of Building# 01. The building Engineer is required to carry out Engineering Assesment (EA) for the horizontal extension following BNBC; suggest necessery remedial measures and submit the EA documents to the RSC for review. On 27-Jul-2025: Not applicable for this ID. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 13 | New Finding-9: Horizontal extension in front of Building#01 at south side | The factory is required to collect building permit for the extension part and carry out remedial works if required as per EA | The horizontal extension was demolished | Feb 24 2024 | On 08-Aug-2023: During inspection extended shed is observed in front of Building# 01. The factory is required to collect building permit for the extension part and carry out remedial works if required as per EA. On 27-Jul-2025: Not applicable for this ID. | (within 6 months) | Corrected
Follow Up Inspection |  | 14 | New finding 10 (Added from CAP item 1 of linked factory ID 23787): Item 1: Mismatch in as-built drawing [Shed 6 (previously Shed 12)] | Priority 2 - The building engineer to check the structure, collect information and produce accurate and complete as-built architectural and structural documentations. |  | Dec 29 2019 | On 01-Feb-2021: This issue is covered in EA. The factory prepared as built drawings for shed-7, 10, 11 & 12 and submitted to ACCORD which has been accepted from RSC on 22-Dec-2020. During inspection, as built drawings was found matched with on-site condition. On 05-Sep-2021: Found corrected from previous follow up inspection. Factory got acceptance of the EA documents from RSC on 22-Dec-2020. On 08-Aug-2023: Corrected previously. The as built drawings along with EA has been prepared by the factory and accepted by the RSC on 22-Dec-2020. On 27-Jul-2025: Corrected previously. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 15 | New finding 11 (Added from CAP item 2 of linked factory ID 23787): Item 2: Incomplete retrofitting works. [Shed 6 (previously Shed 12)] | Priority 2- Revise the DEA report and complete the review with ACCORD. |  | Dec 29 2019 | On 01-Feb-2021: This issue is covered in EA. The factory prepared EA for shed-7, 9, 10, 11, 12 & 13 and submitted to ACCORD which has been accepted from RSC on 22-Dec-2020. As per accepted EA, remediation works was required for shed-7, 9, 10, 11, 12 & 13. On 05-Sep-2021: Found corrected from previous follow up inspection. During inspection, all the remedial works were found completed. On 08-Aug-2023: Corrected previously. DEA has been revised which already been accepted by the RSC. On 27-Jul-2025: Corrected previously. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 16 | New finding 12 (Added from CAP item 3 of linked factory ID 23787): Item 2: Incomplete retrofitting works. [Shed 6 (previously Shed 12)] | Priority 3- Complete remedial works arising from DEA report after being reviewed by ACCORD. |  | May 3 2020 | 9, 10, 11, 12 & 13 and submitted to ACCORD which has been accepted from RSC on 22-Dec-2020. As per accepted EA, remediation works was required for shed-7, 9, 10, 11, 12 & 13. As per initial report factory had started remediation works before the initial inspection. During inspection, remediation works was found ongoing for all sheds. On 05-Sep-2021: Factory has completed all the remedial works for all sheds as per RSC accepted documents. During inspection the Office building was found demolished. However, during inspection some minor discrepancies were observed in between the accepted drawing and site condition. The factory is required to update the drawing and keep on site. On 08-Aug-2023: Corrected previously. All remedial works has been completed by the factory as per accepted DEA. On 27-Jul-2025: Corrected previously. | (within 6 months) | Corrected
Follow Up Inspection |  | 17 | New finding 13 (Added from CAP item 4 of linked factory ID 23787): Item 3: Lack of lateral Stability. [Shed 6 (previously Shed 12) Shed 7 (previously Shed 13)] | Priority 2- Factory engineer is required to check stability system against lateral loading. |  | Dec 29 2019 | On 01-Feb-2021: This issue is covered in EA. The factory prepared EA for shed-7, 9, 10, 11, 12 & 13 and submitted to ACCORD which has been accepted from RSC on 22-Dec-2020. As per accepted EA, remediation works was required for shed-7, 9, 10, 11, 12 & 13. On 05-Sep-2021: Found corrected from previous follow up inspection. Factory got acceptance of the EA documents from RSC on 22-Dec-2020. On 08-Aug-2023: Corrected Previously. Lateral stability check has been incorporated in the EA which already been accepted by the RSC. On 27-Jul-2025: Corrected previously. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 18 | New finding 14 (Added from CAP item 5 of linked factory ID 23787): Item 3: Lack of lateral Stability. [Shed 6 (previously Shed 12) Shed 7 (previously Shed 13)] | Priority 3- Carry out remedial works as per recommendation of engineering assessment report. |  | May 16 2020 | On 01-Feb-2021: This issue is covered in EA. The factory prepared EA for shed-7, 9, 10, 11, 12 & 13 and submitted to ACCORD which has been accepted from RSC on 22-Dec-2020. As per accepted EA, remediation works was required for shed-7, 9, 10, 11, 12 & 13. As per initial report factory started remediation works before the initial inspection. During inspection, remediation works was found ongoing for all those sheds. On 05-Sep-2021: Factory has completed all the remedial works for all sheds as per RSC accepted documents. During inspection the Office building was found demolished. However, during inspection some minor discrepancies were observed in between the accepted drawing and site condition. The factory is required to update the drawing and keep on site. On 08-Aug-2023: Corrected Previously. All the remedial works have been completed by the factory. On 27-Jul-2025: Corrected previously. | (within 6 months) | Corrected
Follow Up Inspection |  | 19 | New finding 15 (Added from CAP item 6 of linked factory ID 23787): Item 4: Corrosion in steel member. [Shed 6 (previously Shed 12) Shed 7 (previously Shed 13)] | Priority 2- The building engineer to investigate the reason & extent of corrosion and suggest proper remedial measure accordingly. |  | Dec 29 2019 | On 01-Feb-2021: The factory has investigated the reason of corrosion. During inspection, corrosion on steel members was found repaired. Investigation report was found on-site. On 05-Sep-2021: During inspection no corrosions was found. However, this issue was found corrected from previous follow up inspections. On 08-Aug-2023: Corrected Previously. As per investigation report factory repaired the corroded steel member. No further corrosion was observed. On 27-Jul-2025: Corrected previously. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 20 | New finding 16 (Added from CAP item 7 of linked factory ID 23787): Item 4: Corrosion in steel member. [Shed 6 (previously Shed 12) Shed 7 (previously Shed 13)] | Priority 3- Take necessary measures to prevent further corrosion and repair the corroded steel members as per engineer’s suggestion. |  | May 3 2020 | On 01-Feb-2021: The factory has investigated the reason of corrosion. During inspection, corrosion on steel members was found repaired. Investigation report was found available on-site. On 05-Sep-2021: During inspection no corrosions was found. However, this issue was found corrected from previous follow up inspections. On 08-Aug-2023: Corrected Previously. Factory has repaired the corroded member and no further corrosion was observed. On 27-Jul-2025: Corrected previously. | (within 6 months) | Corrected
Follow Up Inspection |  | 21 | New finding 17 (Added from CAP item 8 of linked factory ID 23787): Item 5: Significant gap in the beam-column joint. [Shed 6 (previously Shed 12) Shed 7 (previously Shed 13)] | Priority 2-Factory Engineer is required to investigate the connections and take necessary remedial measures where required |  | Dec 29 2019 | On 01-Feb-2021: The factory management was required to investigate the connection gap and take necessary remedial actions. During inspection, gap in beam column connection was found repaired. Investigation report was found on- site. On 05-Sep-2021: During inspection no corrosions was found. However, this issue was found corrected from previous follow up inspections. On 08-Aug-2023: Corrected Previously. Factory has repaired the connections as per investigation. On 27-Jul-2025: Corrected previously. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 22 | New finding 18: Mismatches in as-built drawing [Shed 4 (1724 sft), Shed 5 (2010 sft)] Lack of as-built drawing [Shed 2 (previously Building 4); Shed 3 (previously Building 5); Shed 5 (2010 sft); Shed 8 (517 sft); Toilet Block (270 sft)] | The building engineer is required to survey the whole structures anfd update/produce as-built drawing and keep the hard copy onsite for verification | work completed | Oct 9 2025 | On 27-Jul-2025: During the inspection, four new single storied steel structures (shed 4, Shed 5, Shed 8, Toilet Block) were found. Mismatches (Shed 4- mismatches in column size & bracing locations; Shed 5 – connection details & sub beam details missing, mismatches in grid & storey height details etc.) were found between as-built drawing and onsite condition. As-built drawing was not available for two new structures (Shed 8, Toilet Block) and two existing structures [Shed 2 (previously Building 4), Shed 3 (previously Building 5)]. The building engineer is required to survey the whole structures and update/produce as-built drawing and keep the hard copy onsite for verification during the next inspection.RPO Comments: On 10-Nov-25: the factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 weeks) | Pending Verification
Follow Up Inspection |  | 23 | New finding 19: Corrosin on steel member (Shed 5) | Remove rust and apply anti-corrosive paint on the steel member | work completed | Oct 9 2025 | On 27-Jul-2025: During the inspection, corrosion was found on several steel members. The building engineer is required to remove rust and apply anti-corrosive paint on the steel member.RPO Comments: On 10-Nov-25: the factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 weeks) | Pending Verification

## Fire
Date
17-May-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Torque Design Ltd. (Previously Torque Fashions Ltd.), Paragram, Ashulia,Ashulia Bazar,Dhaka, Bangladesh., Dhaka
Date of Inspection |  | 2014-06-15
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Areas used for combustible storage are not separated by fire rated construction. Location: Ground floor on factory floor. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: Maximum height of 2.4m and maximum area of 23m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Corrected | Feb 4 2016 | On 17/01/2017: No action has been taken yet for store room areas. Bonded ware house has been found with Cutting Section without proper separation. Accessories Store has been found without any fire rated separation. On 17/04/2017: Few works needs to complete to separate the store rooms. On 01/08/2017: Corrected. On 30/01/2018: Corrected On 26/09/2018: Corrected. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Within 3 months | Corrected
Initial Inspection |  | 2 | The boiler and generator rooms is not separated by fire-rated construction (openings, non-rated doors, penetrations). Location: Ground floor separate buildings | Separate the boiler and generator rooms by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations | Corrected | Apr 30 2015 | On 13/11/2016: Corrected. On 17/01/2017: Corrected. On 17/04/2017: Completed On 01/08/2017: Corrected. On 30/01/2018: Corrected. Diesel storage room is not properly separated from the generator area. On 26/09/2018: Corrected. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Within 3 months | Corrected
Initial Inspection |  | 3 | Egress doors / gates with locking features are provided at building exits, exit stairs, along egress routes, exit discharge. Ground floor at exit discharges all gates/doors were open and unlocked during the inspection. | Remove locking features from all egress doors / gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Feb 23 2016 | On 13/11/2016: Corrected. On 17/01/2017: Corrected. On 17/04/2017: Removed On 01/08/2017: Corrected. On 30/01/2018: Corrected as per previous follow up. Issue reopened at no. 19. On 26/09/2018: Corrected. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Immediately | Corrected
Initial Inspection |  | 4 | Storage was located in the exit stair. Location: Under stairs from first floor to ground from storage room. | Remove all storage from exit stairs and egress paths. | Corrected | Aug 31 2014 | On 24.07.2016: Corrected. No storage was found underneath the stair during inspection. On 13/11/2016: Corrected. On 17/01/2017: Corrected. On 17/04/2017: Removed On 01/08/2017: Corrected. On 30/01/2018: Corrected On 26/09/2018: On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Immediately | Corrected
Initial Inspection |  | 5 | Sliding Door & Gates, Location: Ground floor. | Replace all gates / sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Feb 23 2016 | On 13/11/2016: Corrected. On 17/01/2017: Corrected. On 17/04/2017: Replaced On 01/08/2017: On 30/01/2018: Corrected On 26/09/2018: Corrected. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Within 1 month | Corrected
Initial Inspection |  | 6 | The width of egress aisles is less than 36-in. Location: Ground floor north side of factory floor aisles reduced to 26.5 -in. | Provide minimum aisle widths of 36-in. | Corrected | Jan 9 2016 | On 13/11/2016: Corrected. On 17/01/2017: Corrected. On 17/04/2017: Provided On 01/08/2017: Corrected. On 30/01/2018: Corrected On 26/09/2018: Corrected. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Within 3 months | Corrected
Initial Inspection |  | 7 | Exit stairs discharge inside the building. Location: The first floor stairs from storage room discharges into interior of the factory. | Modify stair to discharge directly outside. Provide 2-hr fire-rated exit passageway leading directly outside (vestibules to separate any storage areas). | Corrected | May 3 2015 | On 13/11/2016: Corrected. On 17/01/2017: Corrected. Factory has provided an additional exit stair leading directly outside. On 17/04/2017: Modified On 01/08/2017: Corrected. On 30/01/2018: Corrected On 26/09/2018: Corrected. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Within 6 months | Corrected
Initial Inspection |  | 8 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | Corrected | Feb 8 2016 | On 30/01/2018: T&Cx pending On 26/09/2018: Factory shall apply to ACCORD for witnessing T&Cx. On 07/04/2019: Installation is completed as per standard and functionality comply with standard during T&C inspection. Note: Future alteration or modification or extension shall be done as per standard. On 08/08/2023: Refer to issue no. 21. On 19/12/2023: Refer to issue no. 21. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Refer to issue no. 21. | Within 9 months | Corrected
Initial Inspection |  | 9 | Inspection, testing, and maintenance of the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | Corrected | Feb 8 2016 | On 17/01/2017: Corrected. On 17/04/2017: It is an integrated part of fire alarm system. On 01/08/2017: It is an integrated part of fire alarm system. On 30/01/2018: Corrected. It is an integrated part of FAS On 26/09/2018: Corrected on previous follow-up. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Within 3 months | Corrected
Initial Inspection |  | 10 | Inspection, testing, and maintenance for the emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | Corrected | Feb 8 2016 | On 17/01/2017: Corrected. On 17/04/2017: Maintaining On 01/08/2017: Corrected. On 30/01/2018: Corrected On 26/09/2018: Corrected. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Within 3 months | Corrected
Initial Inspection |  | 11 | Areas used for combustible storage are not separated by fire rated construction. Location: On the factory floor. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: Maximum height of 2.4m and maximum area of 23m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Corrected | Feb 8 2016 | On 17/01/2017: Finished Carton area (Shed 5) has been found without any separation with the finishing section (Shed 4) & pump room (Shed 6). On 17/04/2017: Still few works needs to be done to complete this issue On 01/08/2017: In progress. On 30/01/2018: Corrected On 26/09/2018: Corrected. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Within 3 months | Corrected
Initial Inspection |  | 12 | Egress doors with locking features are provided at building exits, exit stairs, along egress routes, exit discharge. Location: Ground floor and exits all doors were open and unlocked during the inspection. | Remove locking features from all egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Feb 8 2016 | On 13/11/2016: Corrected. On 17/01/2017: Corrected. On 17/04/2017: Completed On 01/08/2017: Corrected. On 30/01/2018: Reopened at issue 19 On 26/09/2018: Corrected. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Immediately | Corrected
Initial Inspection |  | 13 | Sliding doors are provided at building exits, exit stairs, along egress routes, exit discharge. Location: Ground floor and all exits. | Replace all sliding doors along the means of egress with side hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Feb 8 2016 | On 13/11/2016: Corrected. On 17/01/2017: Corrected. On 17/04/2017: Completed On 01/08/2017: Corrected. On 30/01/2018: Corrected On 26/09/2018: Corrected. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Within 1 month | Corrected
Initial Inspection |  | 14 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | Corrected | Feb 4 2016 | On 30/01/2018: It is an integrated part of FAS On 26/09/2018: It is an integrated part of FA system. On 07/04/2019: Installation is completed as per standard and functionality comply with standard during T&C inspection. Note: Future alteration or modification or extension shall be done as per standard. On 08/08/2023: Refer to issue no. 21. On 19/12/2023: Refer to issue no. 21. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Refer to issue no. 21. | Within 9 months | Corrected
Initial Inspection |  | 15 | Inspection, testing, and maintenance of the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | Corrected | Feb 4 2016 | On 17/01/2017: Corrected. On 17/04/2017: It is an integrated part of fire alarm system. On 01/08/2017: Corrected. On 30/01/2018: Corrected. On 26/09/2018: Corrected on previous follow-ups. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Within 3 months | Corrected
Initial Inspection |  | 16 | Inspection, testing, and maintenance for the emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | Corrected | Feb 4 2016 | On 13/11/2016: Corrected. On 17/01/2017: Corrected. On 17/04/2017: Completed On 01/08/2017: Corrected. On 30/01/2018: Corrected On 26/09/2018: Corrected. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Within 3 months | Corrected
Follow Up Inspection |  | 17 | New Finding in 3rd Follow-up: Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected | Jun 18 2016 | On 17/01/2017: Corrected. On 17/04/2017: Completed On 01/08/2017: Corrected. On 30/01/2018: Corrected On 26/09/2018: Corrected. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Within 1 month | Corrected
Follow Up Inspection |  | 18 | New Finding in 3rd Follow-up: Storage located in the dining area. | Remove storage from the dining area. | Corrected | May 25 2016 | On 17/01/2017: No fire separation work has been started yet between the store room and dinning area. On 17/04/2017: Removed On 01/08/2017: Not found. On 30/01/2018: Corrected. Production floor is open to the dinning area. On 26/09/2018: Corrected. Production floor has been found in place of dinning. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Immediately | Corrected
Follow Up Inspection |  | 19 | New Finding from 9th Follow Up: Egress doors/gates with locking features have been observed at more than 30 locations throughout the factory along the egress routes. | Remove non-compliant locking features from all gates. | Corrected | Feb 5 2018 | On 30/01/2018: New Finding On 26/09/2018: Corrected. On 08/08/2023: Corrected. On 19/12/2023: Corrected. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: Corrected | Immediately | Corrected
Follow Up Inspection |  | 20 | New Finding (10th FU): Rooms used for storage of combustible materials are not separated from the surrounding occupancy/areas. (Non-rated structures above false ceiling) | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour construction. | Corrected | Oct 27 2018 | On 26/09/2018: New Finding On 07/04/2019: Fire door provided. Full height partition wall is required. Note: Newly constructed sheds (not inspected by Accord) used for storage room/area should be separated as per standard (suggested only). On 08/08/2023: Store room is not separated from production and sample section due to non rated openings. RPO Comments On 19-Nov-2023: the factory management reported the remediation completion. This item will be verified in the next inspection. On 19/12/2023: No significant progress is observed since the previous follow up. Fire rated door is required to be installed. On 28/01/2024 (Special Escalation Inspection): Corrected. Store room has been separated from other occupancies. Fire door has been installed and found functional properly during inspection. On 28-Apr-26: Issue re-opened. Stationary store is not separated in Shed-10 (newly constructed) and bonded warehouse is not separated in Shed-7 (Previously shed-13) due to unprotected openings. | Within 1 month | In Progress
Follow Up Inspection |  | 21 | New Finding (12th FUI): During inspection FACP was found at abnormal condition. Reportedly, some major modification work is on going on FACP. | Factory shall modify and maintain the system as per NFPA-72 and RSC Technical Guidelines Standard V1.0 and apply for Full T&CVI. | corrected | Nov 8 2023 | On 08/08/2023: New Finding On 19/12/2023: Fire alarm control panel has many troubles. The factory reported that they will replace the fire alarm control unit for troubles and limitations. The factory shall submit the design and documentation hard copy to the RSC for review for modification. On 28/01/2024 (Special Escalation Inspection): Not checked. On 28-Apr-26: The factory submitted the design & documents to RSC for review on January 2024 and get the rejected comments on April 2024. After that the factory submitted the design softcopy to RSC on 7 Apr 2026 for review. Reportedly due to the factory name and license changes issue, the factory delayed the last submission. | Within 3 months | In Progress
Follow Up Inspection |  | 22 | New Finding (14th FUI): Pump room is not separated in Shed-4 due to unprotected openings with other occupancies. | Provide fire pump room with 2 hr. rated fire separation when building is not fully sprinklered and 1 hr. rated fire separation when the building is provided with automatic sprinklers in accordance with NFPA 13. Or, Physically separate the pump room from the protected building by a minimum of 50 ft. (15.3 m) in accordance with NFPA 20. Provide direct access from the outside or provide a 2-hr enclosed passageway from an enclosed stairway or exterior exit. | In Progress | Jul 28 2026 | On 28-Apr-26: New Finding. | Within 3 months | In Progress
Follow Up Inspection |  | 23 | New Finding (14th FUI): Catwalk has been constructed on high pile rack storage and the area of the intermediate deck creates a full floor where the size of the deck is more than 33% of the total floor area and requires fire rated separation. Location: Shed-07 (Previously shed-13). Area of intermediate deck: Approx.. 3400 sft. Total Floor Area: Approx.. 5400 sft. | Remove all catwalk and stair from the multistoried storage (combustible materials) rack facilities area. or Separate each floors by fire rated construction as per BNBC Part-3, chapter-3 and Table 3.3.1. | In Progress | Oct 28 2026 | On 28-Apr-26: New Finding. | Within 6 months | In Progress
Follow Up Inspection |  | 24 | New Finding (14th FUI): The main structural element of the new building (Shed-10, DIFE machine layout approval on 10/03/2026 and construction year 2025, height-5.6 meter approx.. , shed-10 is connected with Shed-1 (Finishing) (previous shed-03), Shed-2 (Sewing) (previous shed-04), Shed-3 (Packing) (previous shed-05), Shed-4 (Store, Pump) (previous shed-06), Shed-06 (Sewing, Dining) (previously shed-12), Shed-7 (Fabric & Finished Goods Store; previous shed-13, Shed-08 (Medical, Childcare) and thus considered as single fire event) is constructed by steel which is non-rated and were found in exposed condition without any fire protection. Among the single fire event sheds, Shed-07 has the greatest height (measuring approximately 6.7 meters) and two stories. | The construction type shall confirm to be in accordance with BNBC 2020 Part-3, Table 3.1.7. Ensure fire resistive rated construction following Table 3.3.1 (a) Part 3 Section-3, Table 3.2.2 and Table 3.2.3 Part 3 Section 2 and Table 4.1.1 from BNBC 2020 Part 4 Section 1. Provide design philosophy to determine the construction type as per BNBC 2020. If any construction rating requires, Consult a qualified fire protection engineer to achieve the require fire rating. Submit the design philosophy along with the required documents to RSC for review the required construction type. Once the design philosophy is reviewed, provide fire ratings of structural members. | In Progress | Oct 28 2026 | On 28-Apr-26: New Finding. | Within 6 months | In Progress
Follow Up Inspection |  | 25 | New Finding (14th FUI): The egress court is less than 10 ft wide and is not separated from the building interior/adjacent building exterior which is not in accordance with section 6.17.2 of RSC Technical Guidelines (Standard). Location: Exits of Shed-1 (Finishing) (previous shed-03), Shed-2 (Sewing) (previous shed-04), Shed-3 (Packing) (previous shed-05), Shed-06 (Sewing, Dining) (previously shed-12), Shed-7 (Fabric & Finished Goods Store) (previous shed-13, Shed-10 (cutting, stationary store). | Egress courts less than 3050 mm (10 ft) in width (as measured from the building and the adjacent property line) shall be provided with walls having a 1-hr fire resistance rated construction for a distance of 3050 mm (10 ft) above the floor of the court. Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft. to provide a minimum 1-hr fire separation. Alternatively, provide a second remote discharge path to the public way (only include this if feasible). | In Progress | Jul 28 2026 | On 28-Apr-26: New Finding. | Within 3 months | In Progress
Follow Up Inspection |  | 26 | New Finding (14th FUI): Areas used for in-process storage of combustible materials are open to the surrounding occupancy. Location: Shed-10. | Provide defined storage areas and limit the storage arrangement as follows: Maximum height of 2.45 m and maximum area of 23 m² and is separated by a minimum 3.0 m (10ft) from other storage areas and they do not exceed 10 percent of the building area of the story in which they occur. or, If sprinkler protected, Maximum height 12 ft (3.66 m) and maximum area of 1000 ft² (93 m²) and separated by a at least 25 ft (7.62 m) and does not constitute more than 10 percent of the building area or 4000 ft² (372 m²) of the sprinklered area, whichever is greater. or, Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | In Progress | Jun 28 2026 | On 28-Apr-26: New Finding. | Within 2 months | In Progress

## Electrical
Date
17-May-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Torque Design Ltd. (Previously Torque Fashions Ltd.), Paragram, Ashulia,Ashulia Bazar,Dhaka, Bangladesh., Dhaka
Date of Inspection |  | 2014-06-15
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Service cable not supported. | Install cable tray or ladder or conduit to support the service cables throughout the whole length. | Corrected | Dec 31 2014 | Already corrected on previous follow up inspection. | 3 months | Corrected
Initial Inspection |  | 2 | LT cable trench is not protected. | Install the concrete slab or checkered plates on cable trench to ensure the required mechanical protection. | Corrected | Sep 30 2014 | Already corrected on previous follow up inspection. | 1 month | Corrected
Initial Inspection |  | 3 | Panel doors are not connected with earth bond. | Provide earth connection for body and doors of metallic distribution boards using green cables preferably braid so that the metallic door remains at zero potential all the time. | Corrected | Sep 30 2014 | Already corrected on previous follow up inspection. | 1 month | Corrected
Initial Inspection |  | 4 | Phase barrier/ separators between different phases are not installed and sharp bend cables. | Phase barriers between different phases supplied by the breaker manufacturer must be installed to avoid arc flashing. Rearrange excessive cables and sharp bent cables shall be avoided such that no stress is imposed on the termination of the cable or insulation of the cable. | Corrected | Sep 30 2014 | Already corrected on previous follow up inspection. | 1 month | Corrected
Follow Up Inspection |  | 5 | New Finding: MCCBs are not adjusted accordingly. | Adjust all the MCCB's according to cable ampacity (Connected Load). Avoid using different sized cable at the terminals. | Corrected | Jun 2 2015 | Already corrected on previous follow up inspection. | 2 months | Corrected
Follow Up Inspection |  | 6 | New Finding: Cable duct / channels are not covered. | Clean All the cable, channels / duct , than seal them for permanent (you may use checkered / performed plate at the bottom). But ensure that you have used proper sized cable for all of your electric loads. | Corrected | Feb 28 2016 | Already corrected on previous follow up inspection. | 2 months | Corrected
Follow Up Inspection |  | 7 | New Finding: Generator body has been earth by inadequate / improper size type cable. | Ensure minimum two earthling connection for generator body (consult with your generator supplier). | Corrected | Feb 28 2016 | Already corrected on previous follow up inspection. | 2 months | Corrected
Follow Up Inspection |  | 8 | New Finding: Earth Continuity Conductor (ECC) in the distribution box is undersized/ improper. | Increase ECC size for whole factory according to BNBC 2006 Part 8 Chapter 2 section 2.8 (Usually ECC should be equal to the half of the respective phase cable). | Corrected | May 27 2015 | Already corrected on previous follow up inspection. | 2 months | Corrected
Follow Up Inspection |  | 9 | New Finding: Battery cases are kept in wooden base. | Use non-flammable case/shelf to store battery. | Corrected | Apr 27 2015 | Already corrected on previous follow up inspection. | 1 month | Corrected
Follow Up Inspection |  | 10 | New Finding: Wiring has done using flexible PVC cable around vertical boiler surface. | Wires close/attached to boiler must be protected from external heat. In unavoidable case use metal type flexible pipe. Again Power cable should keep 0.9m apart from hot area. | Corrected | Apr 27 2015 | Already corrected on previous follow up inspection. | 1 month | Corrected
Follow Up Inspection |  | 11 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. | Amend Electrical SLD properly. Mention all the modification there as present in the factory. | Corrected | Feb 28 2016 | On 04/01/2016: Not Corrected. New committed timeline is given till 28/02/2016. On 18/05/2016: Not Corrected. SLD is not as built. This issue is behind the timeline. On 24/07/2016: Not Corrected. Still some information of SLD are mismatch with actual system. On 13/11/2016: Not Corrected. SLD is not as built. On 17/01/2017: Not Corrected. On 17/04/2017: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 12 | New Finding: Insulation resistance test of electrical equipment is not performed. | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off). | Corrected | May 24 2015 | Already corrected on previous follow up inspection. | 1 month | Corrected
Follow Up Inspection |  | 13 | New Finding: Earth Pit resistance record is unavailable. | Record earth pit resistance for all the earth pit and do once in a year. | Corrected | Feb 28 2016 | On 04/01/2016: Earth pit resistance should be less than 1ohm. New committed timeline is given till 28/02/2016. On 18/05/2016: Not Corrected. Include all earth pit resistance test record. On 24/07/2016: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 14 | New Finding: Thermal inspection record is unavailable. | Thermal inspection is needed to be conducted and recorded bi-annually. Record/Ask for the calibration certificate of the scanner. | Corrected | Feb 28 2016 | On 04/01/2016: The issue is not corrected yet. New committed timeline is given till 28/02/2016. On 18/05/2016: Not Corrected. On 24/07/2016: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 15 | New Finding: Lightning Protection System(LPS) has not installed yet. | Design and Install LPS for your factory; Factory have to submit LPS design to Accord before starting installation. | Corrected | Feb 28 2016 | On 04/01/2016: The issue is not corrected yet. New committed timeline is given till 28/02/2016. On 18/05/2016: Not Corrected. LPS drawing is not visible enough to verify. On 24/07/2016: Not Corrected. LPS drawing needs some modification. On 13/11/2016: Not Corrected. LPS installation is running. LPS drawing is not as per standard and contains wrong information. Need many modifications in the existing LPS. On 17/01/2017: Not Corrected. On 17/04/2017: Corrected. | 3 months | Corrected
Follow Up Inspection |  | 16 | New Finding: Cables are hanging without support. Cable terminals may be in tension. | Use cable tray/ladder to support cables at any where to keep cable out of tension. | Corrected | Jan 31 2016 | Already corrected on previous follow up inspection. | 2 months | Corrected
Follow Up Inspection |  | 17 | New Finding : Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | Hang this instruction near all electrical equipment (LT panel, MDB, FDB, DB, SDB) on a visible location | Corrected | Jan 15 2016 | Already corrected on previous follow up inspection. | 1 month | Corrected
Follow Up Inspection |  | 18 | New Finding: Personal Protective Equipment (PPE) for Electrical Work is not available. | Personal Protective Equipment (PPE) must be arranged by the factory management team for the safety of their employee and worker. | Corrected | Jun 30 2016 | On 24/07/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 19 | New Finding: Power cables are bent excessively. | Avoid power cable bending in electrical system; in unavoidable case bend cables without any stress but not less than 135 degree. | Corrected | Jun 30 2016 | On 24/07/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 20 | New Finding: Light in store room / storage areas is uncovered. | Lights in store room / storage areas shall be covered. | Corrected | Aug 30 2016 | On 24/07/2016: Not Corrected. Factory committed timeline is 30-08-2016. On 13/11/2016: Corrected. LED lights have been used. | 1 Month | Corrected
Follow Up Inspection |  | 21 | New Finding: Cable Channel terminals are left open. | Cable Channel terminals must be covered/capped. | Corrected | Feb 28 2017 | On 17/04/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 22 | New Finding: Cable duct are filled with fluffs (Lint/dust). | Cable ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Corrected | Feb 28 2017 | On 17/04/2017: Not Corrected. Generator output panel bottom cover left open. On 01/08/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 23 | New Finding: Earth electrode for LPS is inadequate. | The size of earth electrode must meet the standard (At least 12.7mm dia solid bare copper conductor). | Corrected | Mar 10 2018 | On 26/09/2018: Not Corrected. #Air terminals are missing at several places. #Earth pit resistance report is not prepared properly. On 27/03/2019: Not Corrected. Inadequate earth pit test report. On 12-08-2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 24 | New Finding: Panel/Distribution boxes are inaccessible or cannot be opened to perform any maintenance work. | Each electrical distribution board/panel must be easily accessible. In case of height its top shall not be higher than 2m from base; and door opening shall be at least 90 degree. | Corrected | Nov 10 2018 | On 27/03/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 25 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected | Nov 10 2018 | On 27/03/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 26 | New Finding: MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per cable current ampacity/load current; if adjustment is not possible, replacement will be the only way. | Corrected | Nov 10 2018 | On 27/03/2019: Not Corrected. On 12/08/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding: Panel/distribution board is not firmly fixed with the foundation. | Panel base must be securely fixed to the foundation. With appropriate fastening devices. | Corrected | Nov 10 2018 | On 27/03/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding: *Power Cables are hanging without proper support. *Wiring using flexible/rigid PVC pipe- this arrangement does not have any support for cables. *Cables running along the ladder are not securely fastened. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. Cables along the cable tray/s must be fastened properly with an interval. | Corrected | Nov 10 2018 | On 27/03/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding: *Panel doors are not connected with earth. *Exhaust fan body and fan blade enclosure has no earth connection *Motor/Pumps are not earthed properly. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. Exhaust fan frame and its enclosure in the production area/s shall be connected to earth. Ensure earthing connection for all motor/pumps coil and body. | Corrected | Nov 10 2018 | On 27/03/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 30 | New Finding: Compressed airline run through the enclosed cable raceway. Cable duct/channels are filled with fluffs (Lint/dust). Cable channel/duct terminals are left open for ingression of lint, dust or fluffs. | Raceways or cable trays containing electrical conductors shall not have a foreign system (e.g. steam, water, air, gas, drainage) other than electrical. Segregate the airline and power line and use different support for each. Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Corrected | Nov 10 2018 | On 27/03/2019: Not Corrected. On 12/08/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: Hazardous lights in store room / storage areas are uncovered. | Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. | Corrected | Nov 10 2018 | On 27/03/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 32 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Corrected | Nov 10 2018 | On 27/03/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible location. Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) must be ensured. | Corrected | Nov 10 2018 | On 27/03/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 34 | New Finding: Combustible materials are tied with cable ducts. | Combustible materials shall be removed from electrical system. | Corrected | Nov 10 2018 | On 27/03/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 35 | New Finding: No policies for PPE & LOTO (Lock-Out-Tag-Out) are introduced for safety of the personnel during any kind of maintenance work. Electric safety training program document is not enriched enough. | Need to introduce and implement PPE & LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all records of using LOTO. It is a periodic task which factory has to continue to improve overall electrical safety situation for the staffs.(Factory may follow NFPA 70E). | Corrected | Nov 10 2018 | On 27/03/2019: Not Corrected. On 12-08-2021: Not Corrected. LOTO policies not found . Training Program documents shall be enriched. On 8-Aug-2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 36 | New Finding: Field information has no/less reflection in existing SLD. Electrical power cables are not identified properly. | Electrical SLD must be amended properly; all the required information must be mentioned there; and it shall be updated when you do significant amount of changes of your electrical system. Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables used in the system according to SLD. | Corrected | Nov 10 2018 | On 27/03/2019: Not Corrected. Reviewed Acknowledged SLD is not available in the factory, If not found please resubmit SLD for review. On 12-08-2021: Not Corrected. Cables are not identified properly. On 8-Aug-2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Lightning Protection System (LPS) is not maintained properly. (Air terminal missing/AT lower height, missing on Generator Shed etc.) | Factory shall redesign Lightning Protection System (LPS) as per standard and install accordingly. Periodic maintenance shall be done to maintain LPS. | Corrected | May 16 2024 | On 12/11/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: Multiple electric motor circuits are controlled by single mcb. | Every electric motor having a rating exceeding 0.376 kW shall be provided with individual control equipment incorporating means of protection against overcurrent. | Corrected | May 16 2024 | On 12/11/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 39 | New Finding: Equipment's/ Loads are not identified properly. | Identify every equipment to distinguish from others (Add point reference, L1-4, PS-1, PS-2, SM 1-10...etc. | Corrected | May 16 2024 | On 12/11/2025: Corrected. | 1 Month | Corrected

## Boiler
Date
17-May-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Torque Fashions Ltd, Paragram, Ashulia,Ashulia Bazar,Dhaka, Bangladesh., Dhaka
Date of Inspection |  | 2022-03-24
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 10337 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | This boiler has already sold. | Mar 5 2025 | Comments on 07-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 14511 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | corrected | Mar 5 2025 | Comments on 07-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 10337 | Direct groundwater was used as feed water for the boiler. | Boiler feed water shall be treated. The feedwater and boiler water quality should meet the manufacturer's specifications. When unavailable, should meet manufacturer's standard or BS EN 12953-10. | This boiler has already sold. | Mar 5 2025 | Comments on 07-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 10337 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | This boiler has already sold. | Mar 5 2025 | Comments on 07-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 14511 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | corrected | Mar 5 2025 | Comments on 07-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 10337 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | This boiler has already sold. | Feb 5 2025 | Comments on 07-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 14511 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | corrected | Feb 5 2025 | Comments on 07-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 10337 | Necessary technical documents (manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | This boiler has already sold. | Mar 5 2025 | Comments on 07-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 14511 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | We have already quotation arranged from the vendor. Which will be done by on 31-Mar-25 | Feb 5 2025 | Comments on 07-May-2025: Factory given timeline is over and not updated. The new timeline is 15-May-2025. The remediation work shall be done following guidelines provided and applicable standard within the given timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 10 | BB 14511 | Salt and scale formation was observed on the waterside of the boiler uniformly. Average size 1mm. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | corrected | Feb 5 2025 | Comments on 07-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 11 | BB 14511 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have already quotation arranged from the vendor. Which will be done by on 31-Mar-25 | Feb 5 2025 | Comments on 07-May-2025: Factory given timeline is over and not updated. The new timeline is 15-May-2025. The remediation work shall be done following guidelines provided and applicable standard within the given timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 12 | BB 14511 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | We have already quotation arranged from the vendor. Which will be done by on 31-Mar-25 | Feb 5 2025 | Comments on 07-May-2025: Factory given timeline is over and not updated. The new timeline is 15-May-2025. The remediation work shall be done following guidelines provided and applicable standard within the given timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 13 | BB 14511 | There was no Low Low Water (LLWL) level trip with an interlock for the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We have already quotation arranged from the vendor. Which will be done by on 31-Mar-25 | Jan 14 2025 | Comments on 07-May-2025: Factory given timeline is over and not updated. The new timeline is 15-May-2025. The remediation work shall be done following guidelines provided and applicable standard within the given timeline. | 1 WEEKS | In Progress